## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_228-1_0_9_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_228-1_0_9_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_228-1_0_9_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_228-1_0_9_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_228-1_0_9_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_228-1_0_9_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_228-1_0_9_node_119 | 0.4 | n |  | TRUE
7 | bus_LV_228-1_0_9_node_49 | 0.4 | n |  | TRUE
8 | bus_LV_228-1_0_9_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_228-1_0_9_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_228-1_0_9_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_228-1_0_9_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_228-1_0_9_node_60 | 0.4 | n |  | TRUE
13 | bus_LV_228-1_0_9_node_64 | 0.4 | n |  | TRUE
14 | bus_LV_228-1_0_9_node_65 | 0.4 | n |  | TRUE
15 | bus_LV_228-1_0_9_node_43 | 0.4 | n |  | TRUE
16 | bus_LV_228-1_0_9_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_228-1_0_9_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_228-1_0_9_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_228-1_0_9_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_228-1_0_9_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_228-1_0_9_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_228-1_0_9_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_228-1_0_9_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_228-1_0_9_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_228-1_0_9_node_110 | 0.4 | n |  | TRUE
26 | bus_LV_228-1_0_9_node_112 | 0.4 | n |  | TRUE
27 | bus_LV_228-1_0_9_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_228-1_0_9_node_109 | 0.4 | n |  | TRUE
29 | bus_LV_228-1_0_9_node_80 | 0.4 | n |  | TRUE
30 | bus_LV_228-1_0_9_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_228-1_0_9_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_228-1_0_9_node_81 | 0.4 | n |  | TRUE
33 | bus_LV_228-1_0_9_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_228-1_0_9_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_228-1_0_9_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_228-1_0_9_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_228-1_0_9_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_228-1_0_9_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_228-1_0_9_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_228-1_0_9_node_92 | 0.4 | n |  | TRUE
41 | bus_LV_228-1_0_9_node_115 | 0.4 | n |  | TRUE
42 | bus_LV_228-1_0_9_node_85 | 0.4 | n |  | TRUE
43 | bus_LV_228-1_0_9_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_228-1_0_9_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_228-1_0_9_node_91 | 0.4 | n |  | TRUE
46 | bus_LV_228-1_0_9_node_116 | 0.4 | n |  | TRUE
47 | bus_LV_228-1_0_9_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_228-1_0_9_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_228-1_0_9_node_121 | 0.4 | n |  | TRUE
50 | bus_LV_228-1_0_9_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_228-1_0_9_node_82 | 0.4 | n |  | TRUE
52 | bus_LV_228-1_0_9_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_228-1_0_9_node_120 | 0.4 | n |  | TRUE
54 | bus_LV_228-1_0_9_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_228-1_0_9_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_228-1_0_9_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_228-1_0_9_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_228-1_0_9_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_228-1_0_9_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_228-1_0_9_node_30 | 0.4 | n |  | TRUE
61 | bus_LV_228-1_0_9_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_228-1_0_9_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_228-1_0_9_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_228-1_0_9_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_228-1_0_9_node_45 | 0.4 | n |  | TRUE
66 | bus_LV_228-1_0_9_node_99 | 0.4 | n |  | TRUE
67 | bus_LV_228-1_0_9_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_228-1_0_9_node_83 | 0.4 | n |  | TRUE
69 | bus_LV_228-1_0_9_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_228-1_0_9_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_228-1_0_9_node_36 | 0.4 | n |  | TRUE
72 | bus_LV_228-1_0_9_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_228-1_0_9_node_37 | 0.4 | n |  | TRUE
74 | bus_LV_228-1_0_9_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_228-1_0_9_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_228-1_0_9_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_228-1_0_9_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_228-1_0_9_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_228-1_0_9_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_228-1_0_9_node_93 | 0.4 | n |  | TRUE
81 | bus_LV_228-1_0_9_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_228-1_0_9_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_228-1_0_9_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_228-1_0_9_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_228-1_0_9_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_228-1_0_9_node_66 | 0.4 | n |  | TRUE
87 | bus_LV_228-1_0_9_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_228-1_0_9_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_228-1_0_9_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_228-1_0_9_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_228-1_0_9_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_228-1_0_9_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_228-1_0_9_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_228-1_0_9_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_228-1_0_9_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_228-1_0_9_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_228-1_0_9_node_106 | 0.4 | n |  | TRUE
98 | bus_LV_228-1_0_9_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_228-1_0_9_node_103 | 0.4 | n |  | TRUE
100 | bus_LV_228-1_0_9_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_228-1_0_9_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_228-1_0_9_node_78 | 0.4 | n |  | TRUE
103 | bus_LV_228-1_0_9_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_228-1_0_9_node_124 | 0.4 | n |  | TRUE
105 | bus_LV_228-1_0_9_node_104 | 0.4 | n |  | TRUE
106 | bus_LV_228-1_0_9_node_122 | 0.4 | n |  | TRUE
107 | bus_LV_228-1_0_9_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_228-1_0_9_node_88 | 0.4 | n |  | TRUE
109 | bus_LV_228-1_0_9_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_228-1_0_9_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_228-1_0_9_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_228-1_0_9_node_96 | 0.4 | n |  | TRUE
113 | bus_LV_228-1_0_9_node_97 | 0.4 | n |  | TRUE
114 | bus_LV_228-1_0_9_node_98 | 0.4 | n |  | TRUE
115 | bus_LV_228-1_0_9_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_228-1_0_9_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_228-1_0_9_node_126 | 0.4 | n |  | TRUE
118 | bus_LV_228-1_0_9_node_117 | 0.4 | n |  | TRUE
119 | bus_LV_228-1_0_9_node_118 | 0.4 | n |  | TRUE
120 | bus_LV_228-1_0_9_node_123 | 0.4 | n |  | TRUE
121 | bus_MV_26_0_node_162 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_228-1_0_9_load_0 | 0 | 0.035536 | 0.0089061 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_228-1_0_9_load_6 | 5 | 0.041152 | 0.010314 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_228-1_0_9_load_119 | 6 | 0.0074225 | 0.0018603 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_228-1_0_9_load_44 | 8 | 0.0078749 | 0.0019736 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_228-1_0_9_load_60 | 12 | 0.0081276 | 0.002037 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_228-1_0_9_load_64 | 13 | 0.002497 | 0.0006258 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_228-1_0_9_load_65 | 14 | 0.0031776 | 0.00079639 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_228-1_0_9_load_43 | 15 | 0.002095 | 0.00052505 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_228-1_0_9_load_21 | 17 | 0.004469 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_228-1_0_9_load_8 | 20 | 0.015014 | 0.0037628 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_228-1_0_9_load_13 | 23 | 0.011786 | 0.0029539 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_228-1_0_9_load_14 | 24 | 0.01728 | 0.0043309 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_228-1_0_9_load_110 | 25 | 0.00084784 | 0.00021249 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_228-1_0_9_load_112 | 26 | 0.0008992 | 0.00022536 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_228-1_0_9_load_109 | 28 | 0.00087281 | 0.00021875 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_228-1_0_9_load_48 | 30 | 0.0044283 | 0.0011098 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_228-1_0_9_load_15 | 33 | 0.0044606 | 0.0011179 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_228-1_0_9_load_19 | 37 | 0.0026633 | 0.00066749 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_228-1_0_9_load_20 | 38 | 0.0033703 | 0.00084467 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_228-1_0_9_load_84 | 39 | 0.0013312 | 0.00033362 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_228-1_0_9_load_115 | 41 | 0.0057901 | 0.0014511 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_228-1_0_9_load_85 | 42 | 0.0013093 | 0.00032815 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_228-1_0_9_load_86 | 43 | 0.0011443 | 0.00028678 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_228-1_0_9_load_91 | 45 | 0.0094066 | 0.0023575 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_228-1_0_9_load_121 | 49 | 0.015267 | 0.0038262 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_228-1_0_9_load_82 | 51 | 0.0010006 | 0.00025077 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_228-1_0_9_load_42 | 52 | 0.01222 | 0.0030625 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_228-1_0_9_load_120 | 53 | 0.014948 | 0.0037464 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_228-1_0_9_load_55 | 54 | 0.0059083 | 0.0014808 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_228-1_0_9_load_51 | 55 | 0.0062805 | 0.0015741 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_228-1_0_9_load_108 | 56 | 0.010712 | 0.0026847 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_228-1_0_9_load_41 | 57 | 0.080737 | 0.020235 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_228-1_0_9_load_28 | 58 | 0.00090792 | 0.00022755 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_228-1_0_9_load_31 | 61 | 0.0090891 | 0.0022779 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_228-1_0_9_load_32 | 62 | 0.021543 | 0.0053991 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_228-1_0_9_load_33 | 63 | 0.0013671 | 0.00034264 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_228-1_0_9_load_34 | 64 | 0.0033344 | 0.00083567 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_228-1_0_9_load_45 | 65 | 0.0038071 | 0.00095414 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_228-1_0_9_load_99 | 66 | 0.0085973 | 0.0021547 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_228-1_0_9_load_38 | 67 | 0.0038054 | 0.00095373 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_228-1_0_9_load_83 | 68 | 0.0017056 | 0.00042747 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_228-1_0_9_load_46 | 69 | 0.00079367 | 0.00019891 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_228-1_0_9_load_36 | 71 | 0.0015605 | 0.00039109 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_228-1_0_9_load_35 | 72 | 0.0021459 | 0.00053781 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_228-1_0_9_load_39 | 74 | 0.0060687 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_228-1_0_9_load_40 | 75 | 0.0086179 | 0.0021599 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_228-1_0_9_load_47 | 76 | 0.0038626 | 0.00096806 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_228-1_0_9_load_63 | 77 | 0.0024318 | 0.00060946 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_228-1_0_9_load_50 | 78 | 0.0093403 | 0.0023409 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_228-1_0_9_load_52 | 79 | 0.027393 | 0.0068652 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_228-1_0_9_load_93 | 80 | 0.0093707 | 0.0023485 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_228-1_0_9_load_113 | 81 | 0.0042726 | 0.0010708 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_228-1_0_9_load_56 | 82 | 0.011506 | 0.0028837 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_228-1_0_9_load_74 | 83 | 0.0051059 | 0.0012797 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_228-1_0_9_load_72 | 84 | 0.0044488 | 0.001115 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_228-1_0_9_load_62 | 85 | 0.0038061 | 0.00095389 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_228-1_0_9_load_66 | 86 | 0.0017778 | 0.00044555 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_228-1_0_9_load_67 | 87 | 0.001006 | 0.00025213 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_228-1_0_9_load_68 | 88 | 0.0089233 | 0.0022364 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_228-1_0_9_load_69 | 89 | 0.0065384 | 0.0016387 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_228-1_0_9_load_70 | 90 | 0.0014761 | 0.00036993 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_228-1_0_9_load_102 | 91 | 0.0011034 | 0.00027655 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_228-1_0_9_load_101 | 92 | 0.001037 | 0.00025988 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_228-1_0_9_load_71 | 93 | 0.00094502 | 0.00023684 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_228-1_0_9_load_73 | 94 | 0.0039701 | 0.00099499 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_228-1_0_9_load_106 | 97 | 0.0054833 | 0.0013742 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_228-1_0_9_load_87 | 98 | 0.0053304 | 0.0013359 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_228-1_0_9_load_76 | 100 | 0.00093697 | 0.00023483 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_228-1_0_9_load_77 | 101 | 0.0014581 | 0.00036543 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_228-1_0_9_load_124 | 104 | 0.00019204 | 4.8129e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_228-1_0_9_load_104 | 105 | 0.0034425 | 0.00086278 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_228-1_0_9_load_122 | 106 | 0.0015423 | 0.00038654 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_228-1_0_9_load_105 | 107 | 0.0037847 | 0.00094853 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_228-1_0_9_load_88 | 108 | 0.0025211 | 0.00063186 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_228-1_0_9_load_90 | 109 | 0.0020541 | 0.00051481 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_228-1_0_9_load_114 | 110 | 0.009366 | 0.0023473 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_228-1_0_9_load_95 | 111 | 0.0013379 | 0.00033531 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_228-1_0_9_load_96 | 112 | 0.0019027 | 0.00047686 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_228-1_0_9_load_97 | 113 | 0.0013771 | 0.00034513 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_228-1_0_9_load_100 | 115 | 0.00083337 | 0.00020886 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_228-1_0_9_load_107 | 116 | 0.0034302 | 0.00085969 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_228-1_0_9_load_126 | 117 | 0.0034668 | 0.00086885 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_228-1_0_9_load_117 | 118 | 0.003372 | 0.00084511 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_228-1_0_9_load_118 | 119 | 0.0018825 | 0.00047181 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_228-1_0_9_load_123 | 120 | 0.00039119 | 9.8041e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_228-1_0_9_line_0 |  | 0 | 1 | 0.04235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_228-1_0_9_line_1 |  | 1 | 5 | 0.032648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_228-1_0_9_line_2 |  | 2 | 3 | 0.009413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_228-1_0_9_line_3 |  | 2 | 4 | 0.07718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_228-1_0_9_line_4 |  | 3 | 6 | 0.018444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_228-1_0_9_line_5 |  | 4 | 7 | 0.028264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_228-1_0_9_line_6 |  | 4 | 8 | 0.020682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_228-1_0_9_line_7 |  | 5 | 9 | 0.005114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_228-1_0_9_line_8 |  | 7 | 13 | 0.01304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_228-1_0_9_line_9 |  | 8 | 15 | 0.0048241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_228-1_0_9_line_10 |  | 9 | 16 | 0.022501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_228-1_0_9_line_11 |  | 9 | 17 | 0.0069239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_228-1_0_9_line_12 |  | 10 | 11 | 0.003909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_228-1_0_9_line_13 |  | 10 | 12 | 0.025985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_228-1_0_9_line_14 |  | 11 | 18 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_228-1_0_9_line_15 |  | 11 | 14 | 0.010577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_228-1_0_9_line_16 |  | 12 | 19 | 0.017628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_228-1_0_9_line_17 |  | 13 | 77 | 0.010147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_228-1_0_9_line_18 |  | 15 | 74 | 0.024824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_228-1_0_9_line_19 |  | 16 | 19 | 0.0128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_228-1_0_9_line_20 |  | 16 | 53 | 0.008293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_228-1_0_9_line_21 |  | 18 | 76 | 0.015825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_228-1_0_9_line_22 |  | 20 | 21 | 0.010722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_228-1_0_9_line_23 |  | 21 | 22 | 0.023296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_228-1_0_9_line_24 |  | 21 | 23 | 0.0093405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_228-1_0_9_line_25 |  | 21 | 24 | 0.016117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_228-1_0_9_line_26 |  | 22 | 25 | 0.020252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_228-1_0_9_line_27 |  | 22 | 26 | 0.028813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_228-1_0_9_line_28 |  | 23 | 27 | 0.012343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_228-1_0_9_line_29 |  | 25 | 28 | 0.010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_228-1_0_9_line_30 |  | 26 | 29 | 0.0053559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_228-1_0_9_line_31 |  | 27 | 30 | 0.021952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_228-1_0_9_line_32 |  | 27 | 31 | 0.05504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_228-1_0_9_line_33 |  | 29 | 32 | 0.045477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_228-1_0_9_line_34 |  | 30 | 56 | 0.0020965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_228-1_0_9_line_35 |  | 31 | 47 | 0.023498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_228-1_0_9_line_36 |  | 32 | 105 | 0.023847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_228-1_0_9_line_37 |  | 32 | 51 | 0.053618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_228-1_0_9_line_38 |  | 32 | 102 | 0.030219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_228-1_0_9_line_39 |  | 33 | 34 | 0.052099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_228-1_0_9_line_40 |  | 33 | 35 | 0.02154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_228-1_0_9_line_41 |  | 34 | 36 | 0.090244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_228-1_0_9_line_42 |  | 35 | 37 | 0.0070875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_228-1_0_9_line_43 |  | 35 | 38 | 0.013832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_228-1_0_9_line_44 |  | 36 | 39 | 0.089417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_228-1_0_9_line_45 |  | 37 | 40 | 0.033222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_228-1_0_9_line_46 |  | 38 | 41 | 0.012328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_228-1_0_9_line_47 |  | 39 | 42 | 0.0031129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_228-1_0_9_line_48 |  | 40 | 44 | 0.014413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_228-1_0_9_line_49 |  | 40 | 45 | 0.010751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_228-1_0_9_line_50 |  | 41 | 46 | 0.011469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_228-1_0_9_line_51 |  | 42 | 43 | 0.0057903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_228-1_0_9_line_52 |  | 44 | 80 | 0.018984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_228-1_0_9_line_53 |  | 44 | 79 | 0.026027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_228-1_0_9_line_54 |  | 45 | 109 | 0.0048682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_228-1_0_9_line_55 |  | 46 | 118 | 0.029663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_228-1_0_9_line_56 |  | 46 | 119 | 0.013792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_228-1_0_9_line_57 |  | 47 | 48 | 0.023276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_228-1_0_9_line_58 |  | 47 | 49 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_228-1_0_9_line_59 |  | 48 | 54 | 0.013117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_228-1_0_9_line_60 |  | 48 | 55 | 0.013663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_228-1_0_9_line_61 |  | 49 | 53 | 0.012937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_228-1_0_9_line_62 |  | 50 | 51 | 0.024661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_228-1_0_9_line_63 |  | 50 | 52 | 0.034901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_228-1_0_9_line_64 |  | 52 | 57 | 0.0094797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_228-1_0_9_line_65 |  | 55 | 78 | 0.0053271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_228-1_0_9_line_66 |  | 58 | 59 | 0.01556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_228-1_0_9_line_67 |  | 58 | 60 | 0.015284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_228-1_0_9_line_68 |  | 59 | 61 | 0.041157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_228-1_0_9_line_69 |  | 59 | 62 | 0.019987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_228-1_0_9_line_70 |  | 60 | 63 | 0.0041741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_228-1_0_9_line_71 |  | 60 | 64 | 0.019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_228-1_0_9_line_72 |  | 61 | 65 | 0.0094956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_228-1_0_9_line_73 |  | 62 | 66 | 0.040888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_228-1_0_9_line_74 |  | 63 | 67 | 0.0035454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_228-1_0_9_line_75 |  | 64 | 68 | 0.016415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_228-1_0_9_line_76 |  | 65 | 69 | 0.033753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_228-1_0_9_line_77 |  | 66 | 70 | 0.0089673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_228-1_0_9_line_78 |  | 67 | 71 | 0.014615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_228-1_0_9_line_79 |  | 69 | 76 | 0.015586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_228-1_0_9_line_80 |  | 70 | 83 | 0.013432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_228-1_0_9_line_81 |  | 70 | 82 | 0.042777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_228-1_0_9_line_82 |  | 71 | 72 | 0.021683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_228-1_0_9_line_83 |  | 72 | 73 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_228-1_0_9_line_84 |  | 73 | 74 | 0.040373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_228-1_0_9_line_85 |  | 73 | 75 | 0.0058967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_228-1_0_9_line_86 |  | 77 | 85 | 0.00012942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_228-1_0_9_line_87 |  | 78 | 79 | 0.032485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_228-1_0_9_line_88 |  | 80 | 81 | 6.9716e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_228-1_0_9_line_89 |  | 81 | 110 | 0.040226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_228-1_0_9_line_90 |  | 83 | 84 | 0.0077718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_228-1_0_9_line_91 |  | 84 | 93 | 0.0093459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_228-1_0_9_line_92 |  | 86 | 87 | 0.020636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_228-1_0_9_line_93 |  | 86 | 88 | 0.0026917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_228-1_0_9_line_94 |  | 87 | 89 | 0.018939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_228-1_0_9_line_95 |  | 88 | 90 | 0.019288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_228-1_0_9_line_96 |  | 89 | 91 | 0.001548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_228-1_0_9_line_97 |  | 91 | 92 | 0.022684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_228-1_0_9_line_98 |  | 92 | 115 | 0.012144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_228-1_0_9_line_99 |  | 93 | 94 | 0.046571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_228-1_0_9_line_100 |  | 95 | 96 | 0.007603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_228-1_0_9_line_101 |  | 95 | 97 | 0.072538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_228-1_0_9_line_102 |  | 96 | 98 | 0.034807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_228-1_0_9_line_103 |  | 97 | 99 | 0.042277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_228-1_0_9_line_104 |  | 98 | 108 | 0.044228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_228-1_0_9_line_105 |  | 99 | 116 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_228-1_0_9_line_106 |  | 99 | 114 | 0.004779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_228-1_0_9_line_107 |  | 100 | 101 | 0.0047114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_228-1_0_9_line_108 |  | 100 | 102 | 0.038399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_228-1_0_9_line_109 |  | 102 | 103 | 0.052247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_228-1_0_9_line_110 |  | 103 | 104 | 0.030957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_228-1_0_9_line_111 |  | 104 | 106 | 0.021235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_228-1_0_9_line_112 |  | 105 | 107 | 0.037731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_228-1_0_9_line_113 |  | 106 | 120 | 0.0080783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_228-1_0_9_line_114 |  | 108 | 109 | 0.025214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_228-1_0_9_line_115 |  | 111 | 112 | 0.027386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_228-1_0_9_line_116 |  | 111 | 113 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_228-1_0_9_line_117 |  | 112 | 114 | 0.049749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_228-1_0_9_line_118 |  | 114 | 115 | 0.012212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_228-1_0_9_line_119 |  | 116 | 117 | 0.062101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_228-1_0_9_trafo_53 | 0.63 MVA 20/0.4 kV | 121 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2706058.4919 | 1255114.9017 | 2706042.4203 | 1255106.5515 | 2706032.5115 | 1255121.8533 | 2706028.7868 | 1255126.5682
1 | 2706058.4919 | 1255114.9017 | 2706064.0256 | 1255103.3469 | 2706072.3095 | 1255085.3235
2 | 2705978.6302 | 1255198.7741 | 2705987.9596 | 1255200.22
3 | 2705987.9596 | 1255200.22 | 2705999.0774 | 1255203.7552 | 2706023.3774 | 1255213.0867 | 2706038.6545 | 1255219.4432 | 2706043.2128 | 1255212.2078 | 2706055.9021 | 1255218.985
4 | 2705978.6302 | 1255198.7741 | 2705985.0244 | 1255181.4737
5 | 2706055.9021 | 1255218.985 | 2706070.4229 | 1255194.7141
6 | 2706055.9021 | 1255218.985 | 2706074.5266 | 1255227.9777
7 | 2706074.5037 | 1255080.7049 | 2706073.6979 | 1255082.3028 | 2706072.3095 | 1255085.3235
8 | 2706070.4229 | 1255194.7141 | 2706074.1323 | 1255195.281 | 2706076.5764 | 1255194.4574 | 2706080.3927 | 1255188.9404
9 | 2706074.5266 | 1255227.9777 | 2706078.8708 | 1255230.0752
10 | 2706074.5037 | 1255080.7049 | 2706087.4687 | 1255086.8421 | 2706095.6855 | 1255086.8115
11 | 2706074.5037 | 1255080.7049 | 2706077.4404 | 1255074.4346
12 | 2706087.2276 | 1255132.275 | 2706090.5788 | 1255134.3034
13 | 2706087.2276 | 1255132.275 | 2706098.6051 | 1255108.9135
14 | 2706090.5788 | 1255134.3034 | 2706100.626 | 1255118.0256
15 | 2706090.5788 | 1255134.3034 | 2706085.0842 | 1255143.3416
16 | 2706106.7505 | 1255093.3039 | 2706104.4134 | 1255096.9873 | 2706098.6051 | 1255108.9135
17 | 2706080.3927 | 1255188.9404 | 2706086.1652 | 1255180.5951
18 | 2706101.2256 | 1255240.869 | 2706078.8708 | 1255230.0752
19 | 2706095.6855 | 1255086.8115 | 2706106.7505 | 1255093.3039
20 | 2706095.6855 | 1255086.8115 | 2706099.5488 | 1255079.4733
21 | 2706100.626 | 1255118.0256 | 2706114.1295 | 1255126.2761
22 | 2706021.0286 | 1255014.8823 | 2706013.3257 | 1255022.3409
23 | 2706021.0286 | 1255014.8823 | 2706023.2171 | 1254991.6914
24 | 2706021.0286 | 1255014.8823 | 2706030.0391 | 1255017.343
25 | 2706021.0286 | 1255014.8823 | 2706015.7246 | 1254999.6627
26 | 2706023.2171 | 1254991.6914 | 2706034.8663 | 1254989.1756 | 2706041.5505 | 1254984.1968
27 | 2706023.2171 | 1254991.6914 | 2706024.6888 | 1254983.6667 | 2706028.4103 | 1254963.35
28 | 2706041.9462 | 1255020.5948 | 2706030.0391 | 1255017.343
29 | 2706041.5505 | 1254984.1968 | 2706042.345 | 1254983.605 | 2706049.4576 | 1254977.1669
30 | 2706026.1965 | 1254958.4731 | 2706028.4103 | 1254963.35
31 | 2706041.9462 | 1255020.5948 | 2706051.6317 | 1255000.8946
32 | 2706041.9462 | 1255020.5948 | 2706059.9255 | 1255027.3334 | 2706065.1542 | 1255029.8513 | 2706070.6011 | 1255032.4065 | 2706092.3434 | 1255042.6154
33 | 2706040.1971 | 1254921.9939 | 2706030.5314 | 1254924.1337 | 2706023.7629 | 1254951.5461 | 2706026.1965 | 1254958.4731
34 | 2706052.5567 | 1254999.0132 | 2706051.6317 | 1255000.8946
35 | 2706112.9162 | 1255054.0823 | 2706103.3768 | 1255048.7626 | 2706092.3434 | 1255042.6154
36 | 2706040.1971 | 1254921.9939 | 2706063.9919 | 1254920.4219
37 | 2706040.1971 | 1254921.9939 | 2706048.3505 | 1254943.2017 | 2706052.435 | 1254945.9993 | 2706060.1812 | 1254965.4984 | 2706061.8364 | 1254970.1795
38 | 2706040.1971 | 1254921.9939 | 2706030.5314 | 1254924.1337 | 2706035.0281 | 1254908.9796 | 2706036.3128 | 1254904.6546
39 | 2706252.6462 | 1254898.182 | 2706250.0304 | 1254904.7738 | 2706233.9945 | 1254937.2905 | 2706229.498 | 1254944.7982
40 | 2706218.4306 | 1254963.2771 | 2706229.498 | 1254944.7982
41 | 2706264.5187 | 1254815.1714 | 2706264.0938 | 1254818.6667 | 2706269.3105 | 1254818.916 | 2706268.8042 | 1254824.8451 | 2706267.0941 | 1254844.8642 | 2706264.789 | 1254860.6246 | 2706258.6046 | 1254883.1766 | 2706252.6462 | 1254898.182
42 | 2706218.4306 | 1254963.2771 | 2706214.7889 | 1254969.3574
43 | 2706218.4306 | 1254963.2771 | 2706230.9807 | 1254969.0915
44 | 2706264.5187 | 1254815.1714 | 2706177.7555 | 1254836.7921
45 | 2706194.3496 | 1254995.5161 | 2706201.3621 | 1254987.3463 | 2706214.0749 | 1254970.5494 | 2706214.7889 | 1254969.3574
46 | 2706230.9807 | 1254969.0915 | 2706234.2864 | 1254970.6231 | 2706242.429 | 1254973.6446
47 | 2706177.7555 | 1254836.7921 | 2706175.5221 | 1254834.6237
48 | 2706194.3496 | 1254995.5161 | 2706184.7701 | 1255006.3088
49 | 2706194.3496 | 1254995.5161 | 2706197.6113 | 1254997.4873 | 2706203.9946 | 1255000.2103
50 | 2706253.1813 | 1254977.6344 | 2706242.429 | 1254973.6446
51 | 2706171.3677 | 1254830.5902 | 2706175.5221 | 1254834.6237
52 | 2706184.7701 | 1255006.3088 | 2706170.5752 | 1254993.7033
53 | 2706184.7701 | 1255006.3088 | 2706167.489 | 1255025.7707
54 | 2706203.9946 | 1255000.2103 | 2706205.5032 | 1255000.8538 | 2706208.6217 | 1255001.6878
55 | 2706253.1813 | 1254977.6344 | 2706258.8627 | 1254976.3687 | 2706282.0559 | 1254982.2452
56 | 2706253.1813 | 1254977.6344 | 2706249.4786 | 1254990.9206
57 | 2706112.9162 | 1255054.0823 | 2706126.7582 | 1255061.8033 | 2706133.6577 | 1255064.5514
58 | 2706112.9162 | 1255054.0823 | 2706105.5754 | 1255068.0258
59 | 2706133.6577 | 1255064.5514 | 2706138.9192 | 1255065.6577 | 2706145.4808 | 1255069.7642
60 | 2706133.6577 | 1255064.5514 | 2706138.4675 | 1255058.4548 | 2706142.383 | 1255054.0452
61 | 2706099.5488 | 1255079.4733 | 2706105.5754 | 1255068.0258
62 | 2706072.6209 | 1254991.6982 | 2706068.0084 | 1254987.6345 | 2706061.8364 | 1254970.1795
63 | 2706072.6209 | 1254991.6982 | 2706076.6004 | 1254988.9895 | 2706084.2822 | 1254985.9802 | 2706093.6585 | 1254988.617 | 2706103.6888 | 1254995.3795
64 | 2706103.6888 | 1254995.3795 | 2706111.5489 | 1255000.6789
65 | 2706145.92 | 1255050.0618 | 2706142.383 | 1255054.0452
66 | 2706186.7315 | 1255185.8577 | 2706178.0275 | 1255198.756
67 | 2706169.4784 | 1255211.4249 | 2706178.0275 | 1255198.756
68 | 2706186.7315 | 1255185.8577 | 2706166.8125 | 1255173.724 | 2706166.6717 | 1255163.0683 | 2706161.6725 | 1255159.965 | 2706161.1885 | 1255158.7665
69 | 2706186.7315 | 1255185.8577 | 2706197.9127 | 1255169.291
70 | 2706169.4784 | 1255211.4249 | 2706167.1433 | 1255214.8848
71 | 2706169.4784 | 1255211.4249 | 2706185.7213 | 1255221.9929
72 | 2706161.1885 | 1255158.7665 | 2706161.1885 | 1255158.7665 | 2706153.1491 | 1255153.7131
73 | 2706220.7867 | 1255135.3993 | 2706197.9127 | 1255169.291
74 | 2706167.1433 | 1255214.8848 | 2706165.16 | 1255217.8236
75 | 2706183.8519 | 1255235.8543 | 2706187.7972 | 1255229.0567 | 2706188.775 | 1255225.4379 | 2706187.8985 | 1255223.4095 | 2706185.7213 | 1255221.9929
76 | 2706128.1858 | 1255132.1551 | 2706134.3125 | 1255136.1551 | 2706139.9184 | 1255145.3965 | 2706153.1491 | 1255153.7131
77 | 2706225.8033 | 1255127.9665 | 2706220.7867 | 1255135.3993
78 | 2706156.9841 | 1255229.9381 | 2706165.16 | 1255217.8236
79 | 2706128.1858 | 1255132.1551 | 2706125.8185 | 1255130.6095 | 2706120.1267 | 1255129.9403 | 2706114.1295 | 1255126.2761
80 | 2706225.8033 | 1255127.9665 | 2706234.3553 | 1255117.6091
81 | 2706225.8033 | 1255127.9665 | 2706191.5991 | 1255102.2774
82 | 2706156.9841 | 1255229.9381 | 2706144.8542 | 1255247.9111
83 | 2706136.7553 | 1255259.9115 | 2706144.8542 | 1255247.9111
84 | 2706136.7553 | 1255259.9115 | 2706133.6186 | 1255257.709 | 2706123.1383 | 1255251.4494 | 2706101.2256 | 1255240.869
85 | 2706136.7553 | 1255259.9115 | 2706133.6602 | 1255264.9306
86 | 2706086.2389 | 1255180.4886 | 2706086.1652 | 1255180.5951
87 | 2706145.92 | 1255050.0618 | 2706167.489 | 1255025.7707
88 | 2706170.523 | 1254993.657 | 2706170.5752 | 1254993.7033
89 | 2706170.523 | 1254993.657 | 2706164.4362 | 1254988.2517 | 2706158.7177 | 1254986.5366 | 2706153.8466 | 1254988.0617 | 2706139.8785 | 1255003.7569
90 | 2706234.3553 | 1255117.6091 | 2706239.3036 | 1255111.6161
91 | 2706245.2541 | 1255104.4094 | 2706239.3036 | 1255111.6161
92 | 2706287.451 | 1255195.8018 | 2706289.6799 | 1255193.7443 | 2706303.5196 | 1255182.8668
93 | 2706287.451 | 1255195.8018 | 2706285.4732 | 1255197.6276
94 | 2706318.3553 | 1255171.0943 | 2706305.4904 | 1255181.3179 | 2706303.5196 | 1255182.8668
95 | 2706276.1681 | 1255213.8739 | 2706278.2073 | 1255212.9097 | 2706281.3843 | 1255204.8935 | 2706284.5398 | 1255198.4893 | 2706285.4732 | 1255197.6276
96 | 2706318.3553 | 1255171.0943 | 2706319.5672 | 1255170.1312
97 | 2706319.5672 | 1255170.1312 | 2706326.8372 | 1255164.3539 | 2706337.2853 | 1255155.9671
98 | 2706346.7558 | 1255148.3651 | 2706337.2853 | 1255155.9671
99 | 2706245.2541 | 1255104.4094 | 2706274.9056 | 1255068.4983
100 | 2706313.9328 | 1255032.2361 | 2706308.8437 | 1255026.5734
101 | 2706313.9328 | 1255032.2361 | 2706319.2165 | 1255043.0287 | 2706325.0602 | 1255059.6027 | 2706334.6974 | 1255101.4545
102 | 2706308.8437 | 1255026.5734 | 2706305.046 | 1255024.2033 | 2706293.4301 | 1255018.1454 | 2706276.2959 | 1255016.3336
103 | 2706354.7893 | 1255138.3789 | 2706339.965 | 1255115.6496 | 2706334.6974 | 1255101.4545
104 | 2706276.2959 | 1255016.3336 | 2706274.935 | 1255016.1897 | 2706256.5407 | 1255014.5027 | 2706232.9802 | 1255008.2019
105 | 2706354.7893 | 1255138.3789 | 2706372.2062 | 1255136.0787 | 2706376.0203 | 1255135.0608
106 | 2706357.4033 | 1255142.3847 | 2706354.7893 | 1255138.3789
107 | 2706064.8001 | 1254896.137 | 2706065.6841 | 1254891.5093
108 | 2706036.3128 | 1254904.6546 | 2706061.0413 | 1254908.6673 | 2706062.8316 | 1254906.442 | 2706064.8001 | 1254896.137
109 | 2706051.2862 | 1254854.7485 | 2706047.4859 | 1254862.6091 | 2706042.6246 | 1254883.3724 | 2706036.3128 | 1254904.6546
110 | 2706051.2862 | 1254854.7485 | 2706048.7661 | 1254852.2235 | 2706045.2322 | 1254849.0132 | 2706034.8743 | 1254839.6645 | 2706035.1252 | 1254831.0058
111 | 2706035.7403 | 1254809.7798 | 2706035.1252 | 1254831.0058
112 | 2706063.9919 | 1254920.4219 | 2706085.0826 | 1254919.0286 | 2706101.2965 | 1254922.5617
113 | 2706035.7403 | 1254809.7798 | 2706035.9417 | 1254802.8313 | 2706036.1101 | 1254801.7171
114 | 2706232.9802 | 1255008.2019 | 2706208.6217 | 1255001.6878
115 | 2706332.8245 | 1255209.357 | 2706345.9572 | 1255200.7826 | 2706350.4979 | 1255189.9978
116 | 2706307.2366 | 1255226.0637 | 2706332.8245 | 1255209.357
117 | 2706357.4033 | 1255142.3847 | 2706360.4824 | 1255154.5055 | 2706358.6614 | 1255170.6082 | 2706350.4979 | 1255189.9978
118 | 2706357.4033 | 1255142.3847 | 2706346.7558 | 1255148.3651 | 2706346.7558 | 1255148.3651
119 | 2706376.0203 | 1255135.0608 | 2706414.0599 | 1255184.1478

## bus_geodata
| x | y | coords
0 | 2706028.7868 | 1255126.5682
1 | 2706058.4919 | 1255114.9017
2 | 2705987.9596 | 1255200.22
3 | 2705978.6302 | 1255198.7741
4 | 2706055.9021 | 1255218.985
5 | 2706072.3095 | 1255085.3235
6 | 2705985.0244 | 1255181.4737
7 | 2706070.4229 | 1255194.7141
8 | 2706074.5266 | 1255227.9777
9 | 2706074.5037 | 1255080.7049
10 | 2706087.2276 | 1255132.275
11 | 2706090.5788 | 1255134.3034
12 | 2706098.6051 | 1255108.9135
13 | 2706080.3927 | 1255188.9404
14 | 2706085.0842 | 1255143.3416
15 | 2706078.8708 | 1255230.0752
16 | 2706095.6855 | 1255086.8115
17 | 2706077.4404 | 1255074.4346
18 | 2706100.626 | 1255118.0256
19 | 2706106.7505 | 1255093.3039
20 | 2706013.3257 | 1255022.3409
21 | 2706021.0286 | 1255014.8823
22 | 2706023.2171 | 1254991.6914
23 | 2706030.0391 | 1255017.343
24 | 2706015.7246 | 1254999.6627
25 | 2706041.5505 | 1254984.1968
26 | 2706028.4103 | 1254963.35
27 | 2706041.9462 | 1255020.5948
28 | 2706049.4576 | 1254977.1669
29 | 2706026.1965 | 1254958.4731
30 | 2706051.6317 | 1255000.8946
31 | 2706092.3434 | 1255042.6154
32 | 2706040.1971 | 1254921.9939
33 | 2706229.498 | 1254944.7982
34 | 2706252.6462 | 1254898.182
35 | 2706218.4306 | 1254963.2771
36 | 2706264.5187 | 1254815.1714
37 | 2706214.7889 | 1254969.3574
38 | 2706230.9807 | 1254969.0915
39 | 2706177.7555 | 1254836.7921
40 | 2706194.3496 | 1254995.5161
41 | 2706242.429 | 1254973.6446
42 | 2706175.5221 | 1254834.6237
43 | 2706171.3677 | 1254830.5902
44 | 2706184.7701 | 1255006.3088
45 | 2706203.9946 | 1255000.2103
46 | 2706253.1813 | 1254977.6344
47 | 2706112.9162 | 1255054.0823
48 | 2706133.6577 | 1255064.5514
49 | 2706105.5754 | 1255068.0258
50 | 2706072.6209 | 1254991.6982
51 | 2706061.8364 | 1254970.1795
52 | 2706103.6888 | 1254995.3795
53 | 2706099.5488 | 1255079.4733
54 | 2706145.4808 | 1255069.7642
55 | 2706142.383 | 1255054.0452
56 | 2706052.5567 | 1254999.0132
57 | 2706111.5489 | 1255000.6789
58 | 2706178.0275 | 1255198.756
59 | 2706186.7315 | 1255185.8577
60 | 2706169.4784 | 1255211.4249
61 | 2706161.1885 | 1255158.7665
62 | 2706197.9127 | 1255169.291
63 | 2706167.1433 | 1255214.8848
64 | 2706185.7213 | 1255221.9929
65 | 2706153.1492 | 1255153.7131
66 | 2706220.7867 | 1255135.3993
67 | 2706165.16 | 1255217.8236
68 | 2706183.8519 | 1255235.8543
69 | 2706128.1858 | 1255132.1551
70 | 2706225.8033 | 1255127.9665
71 | 2706156.9841 | 1255229.9381
72 | 2706144.8542 | 1255247.9111
73 | 2706136.7553 | 1255259.9115
74 | 2706101.2256 | 1255240.869
75 | 2706133.6602 | 1255264.9306
76 | 2706114.1295 | 1255126.2761
77 | 2706086.1652 | 1255180.5951
78 | 2706145.92 | 1255050.0618
79 | 2706167.489 | 1255025.7707
80 | 2706170.5752 | 1254993.7033
81 | 2706170.523 | 1254993.657
82 | 2706191.5991 | 1255102.2775
83 | 2706234.3553 | 1255117.6091
84 | 2706239.3036 | 1255111.6161
85 | 2706086.2389 | 1255180.4886
86 | 2706287.451 | 1255195.8018
87 | 2706303.5196 | 1255182.8668
88 | 2706285.4732 | 1255197.6276
89 | 2706318.3553 | 1255171.0943
90 | 2706276.1681 | 1255213.8739
91 | 2706319.5672 | 1255170.1312
92 | 2706337.2853 | 1255155.9671
93 | 2706245.2541 | 1255104.4094
94 | 2706274.9056 | 1255068.4983
95 | 2706313.9328 | 1255032.2361
96 | 2706308.8437 | 1255026.5734
97 | 2706334.6974 | 1255101.4545
98 | 2706276.2959 | 1255016.3336
99 | 2706354.7893 | 1255138.3789
100 | 2706064.8001 | 1254896.137
101 | 2706065.6841 | 1254891.5093
102 | 2706036.3128 | 1254904.6546
103 | 2706051.2862 | 1254854.7485
104 | 2706035.1252 | 1254831.0058
105 | 2706063.9919 | 1254920.4219
106 | 2706035.7403 | 1254809.7798
107 | 2706101.2965 | 1254922.5617
108 | 2706232.9802 | 1255008.2019
109 | 2706208.6217 | 1255001.6878
110 | 2706139.8785 | 1255003.7569
111 | 2706332.8245 | 1255209.357
112 | 2706350.4979 | 1255189.9978
113 | 2706307.2366 | 1255226.0637
114 | 2706357.4033 | 1255142.3847
115 | 2706346.7558 | 1255148.3651
116 | 2706376.0203 | 1255135.0608
117 | 2706414.0599 | 1255184.1478
118 | 2706282.0559 | 1254982.2452
119 | 2706249.4786 | 1254990.9206
120 | 2706036.1101 | 1254801.7171
121 | 2706126.7582 | 1255061.8033

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99123 | -0.16782 | 0.035536 | 0.0089061
1 | 0.99261 | -0.14116 | 0 | 0
2 | 0.97082 | -0.56314 | 0 | 0
3 | 0.97076 | -0.56443 | 0 | 0
4 | 0.97136 | -0.55254 | 0 | 0
5 | 0.99367 | -0.12065 | 0.041152 | 0.010314
6 | 0.97063 | -0.56696 | 0.0074225 | 0.0018603
7 | 0.97113 | -0.55711 | 0 | 0
8 | 0.97167 | -0.54637 | 0.0078749 | 0.0019736
9 | 0.99403 | -0.11373 | 0 | 0
10 | 0.9931 | -0.13078 | 0 | 0
11 | 0.99286 | -0.13536 | 0 | 0
12 | 0.9947 | -0.1004 | 0.0081276 | 0.002037
13 | 0.97102 | -0.55921 | 0.002497 | 0.0006258
14 | 0.99283 | -0.13595 | 0.0031776 | 0.00079639
15 | 0.97178 | -0.54423 | 0.002095 | 0.00052505
16 | 0.9957 | -0.081574 | 0 | 0
17 | 0.994 | -0.11428 | 0.004469 | 0.00112
18 | 0.99056 | -0.17917 | 0 | 0
19 | 0.99528 | -0.08949 | 0 | 0
20 | 0.99351 | -0.12315 | 0.015014 | 0.0037628
21 | 0.99366 | -0.12031 | 0 | 0
22 | 0.9913 | -0.16497 | 0 | 0
23 | 0.99426 | -0.10872 | 0.011786 | 0.0029539
24 | 0.9934 | -0.12523 | 0.01728 | 0.0043309
25 | 0.99127 | -0.16559 | 0.00084784 | 0.00021249
26 | 0.98844 | -0.21962 | 0.0008992 | 0.00022536
27 | 0.9947 | -0.10044 | 0 | 0
28 | 0.99126 | -0.16575 | 0.00087281 | 0.00021875
29 | 0.98791 | -0.22972 | 0 | 0
30 | 0.9944 | -0.10629 | 0.0044283 | 0.0011098
31 | 0.99683 | -0.059905 | 0 | 0
32 | 0.98343 | -0.31597 | 0 | 0
33 | 0.9904 | -0.18418 | 0.0044606 | 0.0011179
34 | 0.99022 | -0.1877 | 0 | 0
35 | 0.99056 | -0.18103 | 0 | 0
36 | 0.9899 | -0.19378 | 0 | 0
37 | 0.99071 | -0.17817 | 0.0026633 | 0.00066749
38 | 0.99038 | -0.18457 | 0.0033703 | 0.00084467
39 | 0.98959 | -0.1998 | 0.0013312 | 0.00033362
40 | 0.99148 | -0.16324 | 0 | 0
41 | 0.99025 | -0.18699 | 0.0057901 | 0.0014511
42 | 0.98959 | -0.19994 | 0.0013093 | 0.00032815
43 | 0.98958 | -0.20005 | 0.0011443 | 0.00028678
44 | 0.99259 | -0.1417 | 0 | 0
45 | 0.99089 | -0.17449 | 0.0094066 | 0.0023575
46 | 0.9902 | -0.18806 | 0 | 0
47 | 0.99774 | -0.042654 | 0 | 0
48 | 1 | 0 | -0.58545 | -0.14939
49 | 0.99683 | -0.060052 | 0.015267 | 0.0038262
50 | 0.9766 | -0.449 | 0 | 0
51 | 0.97874 | -0.4072 | 0.0010006 | 0.00025077
52 | 0.97357 | -0.50848 | 0.01222 | 0.0030625
53 | 0.99612 | -0.073493 | 0.014948 | 0.0037464
54 | 0.99993 | -0.0013509 | 0.0059083 | 0.0014808
55 | 0.99953 | -0.0089572 | 0.0062805 | 0.0015741
56 | 0.99438 | -0.10669 | 0.010712 | 0.0026847
57 | 0.97286 | -0.52256 | 0.080737 | 0.020235
58 | 0.97676 | -0.44621 | 0.00090792 | 0.00022755
59 | 0.97757 | -0.43041 | 0 | 0
60 | 0.97598 | -0.46151 | 0 | 0
61 | 0.98185 | -0.34687 | 0.0090891 | 0.0022779
62 | 0.97652 | -0.45089 | 0.021543 | 0.0053991
63 | 0.97578 | -0.46531 | 0.0013671 | 0.00034264
64 | 0.97589 | -0.4633 | 0.0033344 | 0.00083567
65 | 0.98292 | -0.32614 | 0.0038071 | 0.00095414
66 | 0.97521 | -0.47676 | 0.0085973 | 0.0021547
67 | 0.97563 | -0.46845 | 0.0038054 | 0.00095373
68 | 0.97586 | -0.46381 | 0.0017056 | 0.00042747
69 | 0.98683 | -0.25053 | 0.00079367 | 0.00019891
70 | 0.97499 | -0.48103 | 0 | 0
71 | 0.97502 | -0.48037 | 0.0015605 | 0.00039109
72 | 0.97415 | -0.49747 | 0.0021459 | 0.00053781
73 | 0.9736 | -0.50833 | 0 | 0
74 | 0.97238 | -0.53227 | 0.0060687 | 0.001521
75 | 0.97355 | -0.50926 | 0.0086179 | 0.0021599
76 | 0.98865 | -0.21559 | 0.0038626 | 0.00096806
77 | 0.97096 | -0.56038 | 0.0024318 | 0.00060946
78 | 0.99918 | -0.015656 | 0.0093403 | 0.0023409
79 | 0.99516 | -0.092394 | 0.027393 | 0.0068652
80 | 0.9922 | -0.14943 | 0.0093707 | 0.0023485
81 | 0.99219 | -0.14945 | 0.0042726 | 0.0010708
82 | 0.97453 | -0.49006 | 0.011506 | 0.0028837
83 | 0.97481 | -0.4846 | 0.0051059 | 0.0012797
84 | 0.97474 | -0.48593 | 0.0044488 | 0.001115
85 | 0.97096 | -0.56039 | 0.0038061 | 0.00095389
86 | 0.98062 | -0.37397 | 0.0017778 | 0.00044555
87 | 0.98085 | -0.36942 | 0.001006 | 0.00025213
88 | 0.98059 | -0.37448 | 0.0089233 | 0.0022364
89 | 0.98108 | -0.3649 | 0.0065384 | 0.0016387
90 | 0.98057 | -0.375 | 0.0014761 | 0.00036993
91 | 0.98111 | -0.36434 | 0.0011034 | 0.00027655
92 | 0.98155 | -0.35579 | 0.001037 | 0.00025988
93 | 0.9747 | -0.48678 | 0.00094502 | 0.00023684
94 | 0.97453 | -0.49017 | 0.0039701 | 0.00099499
95 | 0.98617 | -0.26576 | 0 | 0
96 | 0.98645 | -0.26035 | 0 | 0
97 | 0.98351 | -0.31752 | 0.0054833 | 0.0013742
98 | 0.98772 | -0.23563 | 0.0053304 | 0.0013359
99 | 0.98217 | -0.34362 | 0 | 0
100 | 0.98322 | -0.3201 | 0.00093697 | 0.00023483
101 | 0.98322 | -0.32022 | 0.0014581 | 0.00036543
102 | 0.98331 | -0.31844 | 0 | 0
103 | 0.9832 | -0.32044 | 0 | 0
104 | 0.98314 | -0.32163 | 0.00019204 | 4.8129e-05
105 | 0.98327 | -0.31908 | 0.0034425 | 0.00086278
106 | 0.98311 | -0.32237 | 0.0015423 | 0.00038654
107 | 0.98314 | -0.32166 | 0.0037847 | 0.00094853
108 | 0.98956 | -0.2001 | 0.0025211 | 0.00063186
109 | 0.99067 | -0.17878 | 0.0020541 | 0.00051481
110 | 0.99185 | -0.15612 | 0.009366 | 0.0023473
111 | 0.98177 | -0.35148 | 0.0013379 | 0.00033531
112 | 0.98184 | -0.35014 | 0.0019027 | 0.00047686
113 | 0.98173 | -0.35224 | 0.0013771 | 0.00034513
114 | 0.98205 | -0.34598 | 0 | 0
115 | 0.98179 | -0.35099 | 0.00083337 | 0.00020886
116 | 0.98203 | -0.3463 | 0.0034302 | 0.00085969
117 | 0.98183 | -0.3502 | 0.0034668 | 0.00086885
118 | 0.99011 | -0.18984 | 0.003372 | 0.00084511
119 | 0.99017 | -0.18852 | 0.0018825 | 0.00047181
120 | 0.9831 | -0.32243 | 0.00039119 | 9.8041e-05
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.035536 | -0.0089061 | 0.035581 | 0.0089345 | 4.5194e-05 | 2.8378e-05 | 0.053346 | 0.053346 | 0.053346 | 0.99123 | -0.16782 | 0.99261 | -0.14116 | 14.6554
1 | -0.035581 | -0.0089345 | 0.035616 | 0.0089564 | 3.484e-05 | 2.1875e-05 | 0.053346 | 0.053345 | 0.053346 | 0.99261 | -0.14116 | 0.99367 | -0.12065 | 14.6554
2 | 0.0074239 | 0.0018608 | -0.0074234 | -0.0018606 | 4.5705e-07 | 1.7613e-07 | 0.011379 | 0.011379 | 0.011379 | 0.97082 | -0.56314 | 0.97076 | -0.56443 | 3.1261
3 | -0.0074239 | -0.0018608 | 0.0074276 | 0.0018622 | 3.7474e-06 | 1.4435e-06 | 0.011379 | 0.011379 | 0.011379 | 0.97082 | -0.56314 | 0.97136 | -0.55254 | 3.1261
4 | 0.0074234 | 0.0018606 | -0.0074225 | -0.0018603 | 8.9557e-07 | 3.4516e-07 | 0.011379 | 0.011379 | 0.011379 | 0.97076 | -0.56443 | 0.97063 | -0.56696 | 3.1261
5 | 0.0087379 | 0.0021905 | -0.008736 | -0.0021896 | 1.8991e-06 | 8.6566e-07 | 0.013386 | 0.013386 | 0.013386 | 0.97136 | -0.55254 | 0.97113 | -0.55711 | 3.6774
6 | -0.016166 | -0.0040527 | 0.01617 | 0.0040555 | 4.7563e-06 | 2.788e-06 | 0.024764 | 0.024764 | 0.024764 | 0.97136 | -0.55254 | 0.97167 | -0.54637 | 6.8034
7 | -0.076768 | -0.01927 | 0.076793 | 0.019286 | 2.5349e-05 | 1.6157e-05 | 0.11497 | 0.11497 | 0.11497 | 0.99367 | -0.12065 | 0.99403 | -0.11373 | 31.5853
8 | 0.008736 | 0.0021896 | -0.0087351 | -0.0021892 | 8.762e-07 | 3.9944e-07 | 0.013386 | 0.013386 | 0.013386 | 0.97113 | -0.55711 | 0.97102 | -0.55921 | 3.6775
9 | -0.024045 | -0.0060292 | 0.024048 | 0.0060307 | 2.453e-06 | 1.5102e-06 | 0.036824 | 0.036824 | 0.036824 | 0.97167 | -0.54637 | 0.97178 | -0.54423 | 10.1164
10 | -0.081263 | -0.020406 | 0.081387 | 0.020486 | 0.00012489 | 7.9638e-05 | 0.12166 | 0.12166 | 0.12166 | 0.99403 | -0.11373 | 0.9957 | -0.081574 | 33.4232
11 | 0.0044691 | 0.00112 | -0.004469 | -0.00112 | 1.1621e-07 | -1.5379e-08 | 0.00669 | 0.00669 | 0.00669 | 0.99403 | -0.11373 | 0.994 | -0.11428 | 1.8379
12 | 0.13463 | 0.034567 | -0.1346 | -0.034548 | 2.9912e-05 | 1.9043e-05 | 0.20202 | 0.20202 | 0.20202 | 0.9931 | -0.13078 | 0.99286 | -0.13536 | 27.7498
13 | -0.13463 | -0.034567 | 0.13483 | 0.034694 | 0.00019884 | 0.00012658 | 0.20202 | 0.20202 | 0.20202 | 0.9931 | -0.13078 | 0.9947 | -0.1004 | 27.7498
14 | 0.13142 | 0.033752 | -0.13114 | -0.033573 | 0.00027891 | 0.00017826 | 0.19726 | 0.19726 | 0.19726 | 0.99286 | -0.13536 | 0.99056 | -0.17917 | 54.1913
15 | 0.0031777 | 0.00079631 | -0.0031776 | -0.00079639 | 8.9966e-08 | -7.9211e-08 | 0.0047625 | 0.0047625 | 0.0047625 | 0.99286 | -0.13536 | 0.99283 | -0.13595 | 1.3084
16 | -0.14296 | -0.036731 | 0.14303 | 0.036778 | 7.5807e-05 | 4.7601e-05 | 0.21418 | 0.21418 | 0.21418 | 0.9947 | -0.1004 | 0.99528 | -0.08949 | 14.7099
17 | 0.0062382 | 0.0015634 | -0.0062378 | -0.0015633 | 3.4774e-07 | 9.704e-08 | 0.0095595 | 0.0095596 | 0.0095596 | 0.97102 | -0.55921 | 0.97096 | -0.56038 | 2.6263
18 | -0.026143 | -0.0065557 | 0.026158 | 0.0065649 | 1.4918e-05 | 9.2398e-06 | 0.040032 | 0.040032 | 0.040032 | 0.97178 | -0.54423 | 0.97238 | -0.53227 | 10.9977
19 | 0.14309 | 0.036813 | -0.14303 | -0.036778 | 5.5046e-05 | 3.4564e-05 | 0.21418 | 0.21418 | 0.21418 | 0.9957 | -0.081574 | 0.99528 | -0.08949 | 14.7099
20 | -0.22447 | -0.057299 | 0.22456 | 0.057354 | 8.7687e-05 | 5.5688e-05 | 0.33584 | 0.33584 | 0.33584 | 0.9957 | -0.081574 | 0.99612 | -0.073493 | 23.0656
21 | 0.13114 | 0.033573 | -0.13091 | -0.033426 | 0.0002309 | 0.00014757 | 0.19726 | 0.19726 | 0.19726 | 0.99056 | -0.17917 | 0.98865 | -0.21559 | 54.1913
22 | -0.015014 | -0.0037628 | 0.015016 | 0.003764 | 2.0332e-06 | 1.1624e-06 | 0.022487 | 0.022487 | 0.022487 | 0.99351 | -0.12315 | 0.99366 | -0.12031 | 6.1777
23 | 0.11027 | 0.028388 | -0.11003 | -0.028235 | 0.00023899 | 0.00015266 | 0.1654 | 0.1654 | 0.1654 | 0.99366 | -0.12031 | 0.9913 | -0.16497 | 45.4398
24 | -0.14257 | -0.036485 | 0.14265 | 0.036536 | 8.0033e-05 | 5.0979e-05 | 0.21377 | 0.21377 | 0.21377 | 0.99366 | -0.12031 | 0.99426 | -0.10872 | 29.3642
25 | 0.017284 | 0.0043333 | -0.01728 | -0.0043309 | 4.0494e-06 | 2.3829e-06 | 0.025884 | 0.025884 | 0.025884 | 0.99366 | -0.12031 | 0.9934 | -0.12523 | 7.1111
26 | 0.0017207 | 0.00043087 | -0.0017206 | -0.0004311 | 5.0663e-08 | -2.2866e-07 | 0.0025828 | 0.0025829 | 0.0025829 | 0.9913 | -0.16497 | 0.99127 | -0.16559 | 0.70957
27 | 0.10831 | 0.027804 | -0.10802 | -0.027621 | 0.00028644 | 0.00018295 | 0.16282 | 0.16282 | 0.16282 | 0.9913 | -0.16497 | 0.98844 | -0.21962 | 44.7303
28 | -0.15444 | -0.03949 | 0.1545 | 0.039529 | 6.1967e-05 | 3.9018e-05 | 0.23141 | 0.23141 | 0.23141 | 0.99426 | -0.10872 | 0.9947 | -0.10044 | 15.8935
29 | 0.00087281 | 0.00021861 | -0.00087281 | -0.00021875 | 6.8132e-09 | -1.3208e-07 | 0.0013101 | 0.0013102 | 0.0013102 | 0.99127 | -0.16559 | 0.99126 | -0.16575 | 0.35994
30 | 0.10713 | 0.027396 | -0.10707 | -0.027362 | 5.2362e-05 | 3.3443e-05 | 0.16146 | 0.16146 | 0.16146 | 0.98844 | -0.21962 | 0.98791 | -0.22972 | 44.3584
31 | 0.015145 | 0.003797 | -0.015141 | -0.0037946 | 4.2256e-06 | 2.4195e-06 | 0.022656 | 0.022656 | 0.022656 | 0.9947 | -0.10044 | 0.9944 | -0.10629 | 6.2243
32 | -0.16964 | -0.043326 | 0.16998 | 0.043536 | 0.00033307 | 0.0002103 | 0.25407 | 0.25406 | 0.25407 | 0.9947 | -0.10044 | 0.99683 | -0.059905 | 17.4496
33 | 0.10707 | 0.027362 | -0.10663 | -0.027078 | 0.00044461 | 0.00028397 | 0.16146 | 0.16146 | 0.16146 | 0.98791 | -0.22972 | 0.98343 | -0.31597 | 44.3585
34 | 0.010712 | 0.0026848 | -0.010712 | -0.0026847 | 2.0201e-07 | 1.0209e-07 | 0.01603 | 0.01603 | 0.01603 | 0.9944 | -0.10629 | 0.99438 | -0.10669 | 4.4038
35 | -0.16998 | -0.043536 | 0.17012 | 0.043626 | 0.0001422 | 8.9779e-05 | 0.25406 | 0.25406 | 0.25406 | 0.99683 | -0.059905 | 0.99774 | -0.042654 | 17.4495
36 | 0.0072287 | 0.0018115 | -0.0072277 | -0.0018111 | 1.0698e-06 | 3.8216e-07 | 0.010938 | 0.010938 | 0.010938 | 0.98343 | -0.31597 | 0.98327 | -0.31908 | 3.0049
37 | 0.094878 | 0.024136 | -0.094463 | -0.023871 | 0.00041512 | 0.000265 | 0.14369 | 0.14369 | 0.14369 | 0.98343 | -0.31597 | 0.97874 | -0.4072 | 39.4743
38 | 0.0045217 | 0.0011313 | -0.0045211 | -0.0011314 | 5.3034e-07 | -4.3955e-08 | 0.006841 | 0.0068411 | 0.0068411 | 0.98343 | -0.31597 | 0.98331 | -0.31844 | 1.8794
39 | 0.0037876 | 0.00094727 | -0.003787 | -0.00094754 | 6.3255e-07 | -2.6548e-07 | 0.0056899 | 0.0056902 | 0.0056902 | 0.9904 | -0.18418 | 0.99022 | -0.1877 | 1.5632
40 | -0.0082482 | -0.0020652 | 0.0082494 | 0.0020657 | 1.2403e-06 | 5.1656e-07 | 0.012392 | 0.012392 | 0.012392 | 0.9904 | -0.18418 | 0.99056 | -0.18103 | 3.4043
41 | 0.003787 | 0.00094754 | -0.0037859 | -0.00094799 | 1.0958e-06 | -4.592e-07 | 0.0056902 | 0.0056906 | 0.0056906 | 0.99022 | -0.1877 | 0.9899 | -0.19378 | 1.5633
42 | -0.022669 | -0.0056801 | 0.022672 | 0.005682 | 3.0819e-06 | 1.8812e-06 | 0.034052 | 0.034052 | 0.034052 | 0.99056 | -0.18103 | 0.99071 | -0.17817 | 9.355
43 | 0.014419 | 0.0036144 | -0.014417 | -0.003613 | 2.4336e-06 | 1.3795e-06 | 0.021661 | 0.021661 | 0.021661 | 0.99056 | -0.18103 | 0.99038 | -0.18457 | 5.9508
44 | 0.0037859 | 0.00094799 | -0.0037848 | -0.00094845 | 1.0859e-06 | -4.5417e-07 | 0.0056906 | 0.005691 | 0.005691 | 0.9899 | -0.19378 | 0.98959 | -0.1998 | 1.5635
45 | -0.025335 | -0.0063495 | 0.025353 | 0.0063606 | 1.8039e-05 | 1.1117e-05 | 0.038053 | 0.038052 | 0.038053 | 0.99071 | -0.17817 | 0.99148 | -0.16324 | 10.454
46 | 0.011047 | 0.0027684 | -0.011045 | -0.0027677 | 1.2735e-06 | 6.5643e-07 | 0.016597 | 0.016597 | 0.016597 | 0.99038 | -0.18457 | 0.99025 | -0.18699 | 4.5596
47 | 0.0024536 | 0.00061483 | -0.0024536 | -0.00061486 | 1.5889e-08 | -2.9824e-08 | 0.0036894 | 0.0036894 | 0.0036894 | 0.98959 | -0.1998 | 0.98959 | -0.19994 | 1.0136
48 | -0.084757 | -0.021397 | 0.084844 | 0.021453 | 8.7531e-05 | 5.5834e-05 | 0.12726 | 0.12726 | 0.12726 | 0.99148 | -0.16324 | 0.99259 | -0.1417 | 34.9612
49 | 0.059404 | 0.015036 | -0.059372 | -0.015016 | 3.2082e-05 | 2.0394e-05 | 0.089206 | 0.089206 | 0.089206 | 0.99148 | -0.16324 | 0.99089 | -0.17449 | 24.5073
50 | 0.0052552 | 0.0013166 | -0.0052549 | -0.0013166 | 2.6818e-07 | 2.4102e-08 | 0.0078966 | 0.0078966 | 0.0078966 | 0.99025 | -0.18699 | 0.9902 | -0.18806 | 2.1694
51 | 0.0011443 | 0.00028671 | -0.0011443 | -0.00028678 | 6.4283e-09 | -7.0277e-08 | 0.0017206 | 0.0017206 | 0.0017206 | 0.98959 | -0.19994 | 0.98958 | -0.20005 | 0.4727
52 | 0.023021 | 0.0057732 | -0.023012 | -0.0057681 | 8.4794e-06 | 5.1815e-06 | 0.034512 | 0.034512 | 0.034512 | 0.99259 | -0.1417 | 0.9922 | -0.14943 | 9.4814
53 | -0.10787 | -0.027226 | 0.10812 | 0.027389 | 0.00025542 | 0.00016313 | 0.16177 | 0.16177 | 0.16177 | 0.99259 | -0.1417 | 0.99516 | -0.092394 | 44.4425
54 | 0.049965 | 0.012658 | -0.049955 | -0.012652 | 1.0291e-05 | 6.5236e-06 | 0.075081 | 0.075081 | 0.075081 | 0.99089 | -0.17449 | 0.99067 | -0.17878 | 20.6266
55 | 0.0033723 | 0.00084491 | -0.003372 | -0.00084511 | 2.8567e-07 | -1.987e-07 | 0.0050677 | 0.0050678 | 0.0050678 | 0.9902 | -0.18806 | 0.99011 | -0.18984 | 1.3922
56 | 0.0018826 | 0.00047166 | -0.0018825 | -0.00047181 | 4.1395e-08 | -1.5092e-07 | 0.002829 | 0.0028291 | 0.0028291 | 0.9902 | -0.18806 | 0.99017 | -0.18852 | 0.77721
57 | -0.42527 | -0.10879 | 0.42615 | 0.10935 | 0.00087995 | 0.00056195 | 0.63502 | 0.63502 | 0.63502 | 0.99774 | -0.042654 | 1 | 0 | 43.6138
58 | 0.25515 | 0.065162 | -0.25493 | -0.065026 | 0.00021439 | 0.00013639 | 0.38095 | 0.38095 | 0.38095 | 0.99774 | -0.042654 | 0.99683 | -0.060052 | 26.1644
59 | 0.0059087 | 0.0014808 | -0.0059083 | -0.0014808 | 3.8025e-07 | 7.1287e-08 | 0.0087922 | 0.0087923 | 0.0087923 | 1 | 0 | 0.99993 | -0.0013509 | 2.4155
60 | 0.15175 | 0.03856 | -0.15168 | -0.038519 | 6.5415e-05 | 4.1149e-05 | 0.22599 | 0.22599 | 0.22599 | 1 | 0 | 0.99953 | -0.0089572 | 15.5212
61 | 0.23967 | 0.0612 | -0.23951 | -0.061101 | 0.00015559 | 9.8901e-05 | 0.35816 | 0.35816 | 0.35816 | 0.99683 | -0.060052 | 0.99612 | -0.073493 | 24.5992
62 | -0.093275 | -0.023501 | 0.093462 | 0.02362 | 0.00018691 | 0.00011931 | 0.14217 | 0.14217 | 0.14217 | 0.9766 | -0.449 | 0.97874 | -0.4072 | 39.0564
63 | 0.093275 | 0.023501 | -0.093011 | -0.023332 | 0.00026452 | 0.00016886 | 0.14217 | 0.14217 | 0.14217 | 0.9766 | -0.449 | 0.97357 | -0.50848 | 39.0565
64 | 0.080791 | 0.020269 | -0.080737 | -0.020235 | 5.4211e-05 | 3.4577e-05 | 0.12349 | 0.12349 | 0.12349 | 0.97357 | -0.50848 | 0.97286 | -0.52256 | 33.9256
65 | 0.1454 | 0.036945 | -0.14535 | -0.036915 | 4.6878e-05 | 2.9862e-05 | 0.21664 | 0.21664 | 0.21664 | 0.99953 | -0.0089572 | 0.99918 | -0.015656 | 29.7581
66 | -0.055847 | -0.014072 | 0.055889 | 0.014099 | 4.2264e-05 | 2.6854e-05 | 0.085106 | 0.085106 | 0.085106 | 0.97676 | -0.44621 | 0.97757 | -0.43041 | 23.3808
67 | 0.054939 | 0.013845 | -0.054899 | -0.013819 | 4.0174e-05 | 2.552e-05 | 0.083723 | 0.083723 | 0.083723 | 0.97676 | -0.44621 | 0.97598 | -0.46151 | 23.0008
68 | -0.11212 | -0.028232 | 0.11257 | 0.02852 | 0.00044976 | 0.00028733 | 0.17071 | 0.17071 | 0.17071 | 0.97757 | -0.43041 | 0.98185 | -0.34687 | 46.8979
69 | 0.056228 | 0.014133 | -0.056173 | -0.014098 | 5.4923e-05 | 3.49e-05 | 0.085603 | 0.085603 | 0.085603 | 0.97757 | -0.43041 | 0.97652 | -0.45089 | 23.5172
70 | 0.049858 | 0.012556 | -0.049849 | -0.012551 | 9.0502e-06 | 5.74e-06 | 0.076038 | 0.076038 | 0.076038 | 0.97598 | -0.46151 | 0.97578 | -0.46531 | 20.8896
71 | 0.0050405 | 0.001263 | -0.00504 | -0.001263 | 4.2916e-07 | 3.2522e-08 | 0.0076848 | 0.0076849 | 0.0076849 | 0.97598 | -0.46151 | 0.97589 | -0.4633 | 2.1112
72 | -0.12166 | -0.030798 | 0.12178 | 0.030875 | 0.00012119 | 7.7442e-05 | 0.18448 | 0.18448 | 0.18448 | 0.98185 | -0.34687 | 0.98292 | -0.32614 | 50.6822
73 | 0.03463 | 0.0086991 | -0.034587 | -0.0086723 | 4.2708e-05 | 2.6822e-05 | 0.052776 | 0.052776 | 0.052776 | 0.97652 | -0.45089 | 0.97521 | -0.47676 | 14.499
74 | 0.048482 | 0.012208 | -0.048475 | -0.012203 | 7.2713e-06 | 4.6093e-06 | 0.073953 | 0.073953 | 0.073953 | 0.97578 | -0.46531 | 0.97563 | -0.46845 | 20.3169
75 | 0.0017057 | 0.00042729 | -0.0017056 | -0.00042747 | 4.1637e-08 | -1.7844e-07 | 0.0026007 | 0.0026008 | 0.0026008 | 0.97589 | -0.4633 | 0.97586 | -0.46381 | 0.7145
76 | -0.12558 | -0.031829 | 0.12604 | 0.032122 | 0.00045812 | 0.00029277 | 0.19025 | 0.19025 | 0.19025 | 0.98292 | -0.32614 | 0.98683 | -0.25053 | 52.2655
77 | 0.02599 | 0.0065176 | -0.025985 | -0.0065144 | 5.2888e-06 | 3.273e-06 | 0.039658 | 0.039658 | 0.039658 | 0.97521 | -0.47676 | 0.97499 | -0.48103 | 10.8951
78 | 0.04467 | 0.01125 | -0.044644 | -0.011234 | 2.5454e-05 | 1.6108e-05 | 0.068149 | 0.068149 | 0.068149 | 0.97563 | -0.46845 | 0.97502 | -0.48037 | 18.7224
79 | -0.12684 | -0.032321 | 0.12705 | 0.032458 | 0.00021421 | 0.0001369 | 0.19144 | 0.19144 | 0.19144 | 0.98683 | -0.25053 | 0.98865 | -0.21559 | 52.5942
80 | 0.014474 | 0.003628 | -0.014471 | -0.0036266 | 2.4578e-06 | 1.4055e-06 | 0.02209 | 0.02209 | 0.02209 | 0.97499 | -0.48103 | 0.97481 | -0.4846 | 6.0686
81 | 0.011511 | 0.0028863 | -0.011506 | -0.0028837 | 4.9512e-06 | 2.6356e-06 | 0.017569 | 0.017569 | 0.017569 | 0.97499 | -0.48103 | 0.97453 | -0.49006 | 4.8266
82 | 0.043084 | 0.010842 | -0.043049 | -0.01082 | 3.5171e-05 | 2.2239e-05 | 0.065768 | 0.065768 | 0.065768 | 0.97502 | -0.48037 | 0.97415 | -0.49747 | 18.0681
83 | 0.040903 | 0.010282 | -0.040881 | -0.010269 | 2.1201e-05 | 1.3388e-05 | 0.06249 | 0.06249 | 0.06249 | 0.97415 | -0.49747 | 0.9736 | -0.50833 | 17.1676
84 | 0.032263 | 0.008109 | -0.032226 | -0.0080859 | 3.6825e-05 | 2.3067e-05 | 0.049318 | 0.049318 | 0.049318 | 0.9736 | -0.50833 | 0.97238 | -0.53227 | 13.549
85 | 0.0086183 | 0.00216 | -0.0086179 | -0.0021599 | 3.8366e-07 | 1.7222e-07 | 0.013172 | 0.013172 | 0.013172 | 0.9736 | -0.50833 | 0.97355 | -0.50926 | 3.6187
86 | 0.0038061 | 0.00095389 | -0.0038061 | -0.00095389 | 1.6514e-09 | -5.4351e-10 | 0.0058328 | 0.0058328 | 0.0058328 | 0.97096 | -0.56038 | 0.97096 | -0.56039 | 1.6024
87 | 0.13601 | 0.034574 | -0.13551 | -0.034254 | 0.00050067 | 0.00032 | 0.20273 | 0.20273 | 0.20273 | 0.99918 | -0.015656 | 0.99516 | -0.092394 | 55.6949
88 | 0.013642 | 0.0034195 | -0.013642 | -0.0034195 | 1.0942e-08 | 6.1045e-09 | 0.020459 | 0.020459 | 0.020459 | 0.9922 | -0.14943 | 0.99219 | -0.14945 | 5.6205
89 | 0.009369 | 0.0023487 | -0.009366 | -0.0023473 | 2.9782e-06 | 1.3867e-06 | 0.014051 | 0.014051 | 0.014051 | 0.99219 | -0.14945 | 0.99185 | -0.15612 | 3.8602
90 | 0.0093654 | 0.0023469 | -0.0093648 | -0.0023467 | 5.9562e-07 | 2.8432e-07 | 0.014296 | 0.014296 | 0.014296 | 0.97481 | -0.4846 | 0.97474 | -0.48593 | 3.9274
91 | 0.0049159 | 0.0012317 | -0.0049157 | -0.0012317 | 1.9737e-07 | 9.827e-09 | 0.0075044 | 0.0075044 | 0.0075044 | 0.97474 | -0.48593 | 0.9747 | -0.48678 | 2.0617
92 | -0.012177 | -0.0030518 | 0.01218 | 0.0030532 | 2.6423e-06 | 1.4307e-06 | 0.018478 | 0.018478 | 0.018478 | 0.98062 | -0.37397 | 0.98085 | -0.36942 | 5.0764
93 | 0.0104 | 0.0026062 | -0.010399 | -0.0026061 | 2.5136e-07 | 1.2692e-07 | 0.015781 | 0.015781 | 0.015781 | 0.98062 | -0.37397 | 0.98059 | -0.37448 | 4.3353
94 | -0.013186 | -0.0033053 | 0.013189 | 0.0033069 | 2.8421e-06 | 1.5798e-06 | 0.020004 | 0.020004 | 0.020004 | 0.98085 | -0.36942 | 0.98108 | -0.3649 | 5.4957
95 | 0.0014761 | 0.00036971 | -0.0014761 | -0.00036993 | 3.6289e-08 | -2.2009e-07 | 0.0022398 | 0.0022399 | 0.0022399 | 0.98059 | -0.37448 | 0.98057 | -0.375 | 0.61536
96 | -0.019727 | -0.0049456 | 0.019728 | 0.0049459 | 5.197e-07 | 3.1306e-07 | 0.029921 | 0.029921 | 0.029921 | 0.98108 | -0.3649 | 0.98111 | -0.36434 | 8.2201
97 | -0.020831 | -0.0052225 | 0.02084 | 0.0052276 | 8.4913e-06 | 5.1478e-06 | 0.031595 | 0.031595 | 0.031595 | 0.98111 | -0.36434 | 0.98155 | -0.35579 | 8.6799
98 | -0.021877 | -0.0054875 | 0.021882 | 0.0054906 | 5.0096e-06 | 3.0526e-06 | 0.033167 | 0.033167 | 0.033167 | 0.98155 | -0.35579 | 0.98179 | -0.35099 | 9.1117
99 | 0.0039707 | 0.00099482 | -0.0039701 | -0.00099499 | 6.4173e-07 | -1.6964e-07 | 0.0060617 | 0.0060619 | 0.0060619 | 0.9747 | -0.48678 | 0.97453 | -0.49017 | 1.6654
100 | -0.039865 | -0.010053 | 0.039876 | 0.010059 | 1.0324e-05 | 6.5102e-06 | 0.060174 | 0.060174 | 0.060174 | 0.98617 | -0.26576 | 0.98645 | -0.26035 | 16.5314
101 | 0.039865 | 0.010053 | -0.039767 | -0.0099908 | 9.8497e-05 | 6.2115e-05 | 0.060174 | 0.060175 | 0.060175 | 0.98617 | -0.26576 | 0.98351 | -0.31752 | 16.5315
102 | -0.039876 | -0.010059 | 0.039923 | 0.010089 | 4.7263e-05 | 2.9803e-05 | 0.060174 | 0.060174 | 0.060174 | 0.98645 | -0.26035 | 0.98772 | -0.23563 | 16.5314
103 | 0.034284 | 0.0086165 | -0.034241 | -0.0085898 | 4.267e-05 | 2.6773e-05 | 0.051879 | 0.051879 | 0.051879 | 0.98351 | -0.31752 | 0.98217 | -0.34362 | 14.2524
104 | -0.045253 | -0.011425 | 0.045331 | 0.011474 | 7.7154e-05 | 4.8811e-05 | 0.068205 | 0.068204 | 0.068205 | 0.98772 | -0.23563 | 0.98956 | -0.2001 | 18.7375
105 | 0.0068985 | 0.0017285 | -0.0068976 | -0.0017282 | 8.813e-07 | 2.9177e-07 | 0.010451 | 0.010451 | 0.010451 | 0.98217 | -0.34362 | 0.98203 | -0.3463 | 2.8712
106 | 0.027342 | 0.0068613 | -0.027339 | -0.0068594 | 3.0757e-06 | 1.908e-06 | 0.041428 | 0.041428 | 0.041428 | 0.98217 | -0.34362 | 0.98205 | -0.34598 | 11.3812
107 | 0.0014581 | 0.00036537 | -0.0014581 | -0.00036543 | 8.603e-09 | -5.4247e-08 | 0.0022067 | 0.0022067 | 0.0022067 | 0.98322 | -0.3201 | 0.98322 | -0.32022 | 0.60623
108 | -0.002395 | -0.0006002 | 0.0023952 | 0.00059983 | 1.8918e-07 | -3.6598e-07 | 0.0036247 | 0.0036245 | 0.0036247 | 0.98322 | -0.3201 | 0.98331 | -0.31844 | 0.99579
109 | 0.0021259 | 0.00053153 | -0.0021257 | -0.00053206 | 2.0274e-07 | -5.3293e-07 | 0.0032166 | 0.0032169 | 0.0032169 | 0.98331 | -0.31844 | 0.9832 | -0.32044 | 0.88376
110 | 0.0021257 | 0.00053206 | -0.0021256 | -0.00053238 | 1.2014e-07 | -3.1569e-07 | 0.0032169 | 0.003217 | 0.003217 | 0.9832 | -0.32044 | 0.98314 | -0.32163 | 0.8838
111 | 0.0019336 | 0.00048425 | -0.0019335 | -0.00048447 | 6.8195e-08 | -2.2562e-07 | 0.0029264 | 0.0029265 | 0.0029265 | 0.98314 | -0.32163 | 0.98311 | -0.32237 | 0.80397
112 | 0.0037851 | 0.00094835 | -0.0037847 | -0.00094853 | 4.6425e-07 | -1.814e-07 | 0.005728 | 0.0057282 | 0.0057282 | 0.98327 | -0.31908 | 0.98314 | -0.32166 | 1.5737
113 | 0.00039119 | 9.7939e-05 | -0.00039119 | -9.8041e-05 | 1.062e-09 | -1.0175e-07 | 0.00059206 | 0.0005921 | 0.0005921 | 0.98311 | -0.32237 | 0.9831 | -0.32243 | 0.16266
114 | -0.047852 | -0.012106 | 0.047901 | 0.012137 | 4.9011e-05 | 3.1042e-05 | 0.071995 | 0.071995 | 0.071995 | 0.98956 | -0.2001 | 0.99067 | -0.17878 | 19.779
115 | -0.0027151 | -0.00068009 | 0.0027152 | 0.00067986 | 1.7389e-07 | -2.3504e-07 | 0.0041149 | 0.0041148 | 0.0041149 | 0.98177 | -0.35148 | 0.98184 | -0.35014 | 1.1305
116 | 0.0013771 | 0.00034478 | -0.0013771 | -0.00034513 | 4.9923e-08 | -3.5446e-07 | 0.0020871 | 0.0020873 | 0.0020873 | 0.98177 | -0.35148 | 0.98173 | -0.35224 | 0.57342
117 | -0.0046179 | -0.0011567 | 0.0046188 | 0.0011567 | 9.137e-07 | -4.4548e-08 | 0.0069984 | 0.0069982 | 0.0069984 | 0.98184 | -0.35014 | 0.98205 | -0.34598 | 1.9226
118 | 0.022721 | 0.0057027 | -0.022715 | -0.0056994 | 5.4285e-06 | 3.3198e-06 | 0.03443 | 0.03443 | 0.03443 | 0.98205 | -0.34598 | 0.98179 | -0.35099 | 9.4587
119 | 0.0034674 | 0.00086848 | -0.0034668 | -0.00086885 | 6.4282e-07 | -3.7414e-07 | 0.0052537 | 0.005254 | 0.005254 | 0.98203 | -0.3463 | 0.98183 | -0.3502 | 1.4434

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58545 | 0.14939

## res_load
| p_mw | q_mvar
0 | 0.035536 | 0.0089061
1 | 0.041152 | 0.010314
2 | 0.0074225 | 0.0018603
3 | 0.0078749 | 0.0019736
4 | 0.0081276 | 0.002037
5 | 0.002497 | 0.0006258
6 | 0.0031776 | 0.00079639
7 | 0.002095 | 0.00052505
8 | 0.004469 | 0.00112
9 | 0.015014 | 0.0037628
10 | 0.011786 | 0.0029539
11 | 0.01728 | 0.0043309
12 | 0.00084784 | 0.00021249
13 | 0.0008992 | 0.00022536
14 | 0.00087281 | 0.00021875
15 | 0.0044283 | 0.0011098
16 | 0.0044606 | 0.0011179
17 | 0.0026633 | 0.00066749
18 | 0.0033703 | 0.00084467
19 | 0.0013312 | 0.00033362
20 | 0.0057901 | 0.0014511
21 | 0.0013093 | 0.00032815
22 | 0.0011443 | 0.00028678
23 | 0.0094066 | 0.0023575
24 | 0.015267 | 0.0038262
25 | 0.0010006 | 0.00025077
26 | 0.01222 | 0.0030625
27 | 0.014948 | 0.0037464
28 | 0.0059083 | 0.0014808
29 | 0.0062805 | 0.0015741
30 | 0.010712 | 0.0026847
31 | 0.080737 | 0.020235
32 | 0.00090792 | 0.00022755
33 | 0.0090891 | 0.0022779
34 | 0.021543 | 0.0053991
35 | 0.0013671 | 0.00034264
36 | 0.0033344 | 0.00083567
37 | 0.0038071 | 0.00095414
38 | 0.0085973 | 0.0021547
39 | 0.0038054 | 0.00095373
40 | 0.0017056 | 0.00042747
41 | 0.00079367 | 0.00019891
42 | 0.0015605 | 0.00039109
43 | 0.0021459 | 0.00053781
44 | 0.0060687 | 0.001521
45 | 0.0086179 | 0.0021599
46 | 0.0038626 | 0.00096806
47 | 0.0024318 | 0.00060946
48 | 0.0093403 | 0.0023409
49 | 0.027393 | 0.0068652
50 | 0.0093707 | 0.0023485
51 | 0.0042726 | 0.0010708
52 | 0.011506 | 0.0028837
53 | 0.0051059 | 0.0012797
54 | 0.0044488 | 0.001115
55 | 0.0038061 | 0.00095389
56 | 0.0017778 | 0.00044555
57 | 0.001006 | 0.00025213
58 | 0.0089233 | 0.0022364
59 | 0.0065384 | 0.0016387
60 | 0.0014761 | 0.00036993
61 | 0.0011034 | 0.00027655
62 | 0.001037 | 0.00025988
63 | 0.00094502 | 0.00023684
64 | 0.0039701 | 0.00099499
65 | 0.0054833 | 0.0013742
66 | 0.0053304 | 0.0013359
67 | 0.00093697 | 0.00023483
68 | 0.0014581 | 0.00036543
69 | 0.00019204 | 4.8129e-05
70 | 0.0034425 | 0.00086278
71 | 0.0015423 | 0.00038654
72 | 0.0037847 | 0.00094853
73 | 0.0025211 | 0.00063186
74 | 0.0020541 | 0.00051481
75 | 0.009366 | 0.0023473
76 | 0.0013379 | 0.00033531
77 | 0.0019027 | 0.00047686
78 | 0.0013771 | 0.00034513
79 | 0.00083337 | 0.00020886
80 | 0.0034302 | 0.00085969
81 | 0.0034668 | 0.00086885
82 | 0.003372 | 0.00084511
83 | 0.0018825 | 0.00047181
84 | 0.00039119 | 9.8041e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1