## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-11_0_4_node_43 | 0.4 | n |  | TRUE
3 | bus_LV_2325-11_0_4_node_179 | 0.4 | n |  | TRUE
4 | bus_LV_2325-11_0_4_node_76 | 0.4 | n |  | TRUE
5 | bus_LV_2325-11_0_4_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_2325-11_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2325-11_0_4_node_176 | 0.4 | n |  | TRUE
8 | bus_LV_2325-11_0_4_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_2325-11_0_4_node_2 | 0.4 | n |  | TRUE
10 | bus_LV_2325-11_0_4_node_3 | 0.4 | n |  | TRUE
11 | bus_LV_2325-11_0_4_node_108 | 0.4 | n |  | TRUE
12 | bus_LV_2325-11_0_4_node_200 | 0.4 | n |  | TRUE
13 | bus_LV_2325-11_0_4_node_109 | 0.4 | n |  | TRUE
14 | bus_LV_2325-11_0_4_node_199 | 0.4 | n |  | TRUE
15 | bus_LV_2325-11_0_4_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_2325-11_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_2325-11_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2325-11_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2325-11_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2325-11_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2325-11_0_4_node_274 | 0.4 | n |  | TRUE
22 | bus_LV_2325-11_0_4_node_189 | 0.4 | n |  | TRUE
23 | bus_LV_2325-11_0_4_node_273 | 0.4 | n |  | TRUE
24 | bus_LV_2325-11_0_4_node_190 | 0.4 | n |  | TRUE
25 | bus_LV_2325-11_0_4_node_188 | 0.4 | n |  | TRUE
26 | bus_LV_2325-11_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2325-11_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2325-11_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2325-11_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2325-11_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2325-11_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2325-11_0_4_node_222 | 0.4 | n |  | TRUE
33 | bus_LV_2325-11_0_4_node_285 | 0.4 | n |  | TRUE
34 | bus_LV_2325-11_0_4_node_220 | 0.4 | n |  | TRUE
35 | bus_LV_2325-11_0_4_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_2325-11_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_2325-11_0_4_node_249 | 0.4 | n |  | TRUE
38 | bus_LV_2325-11_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2325-11_0_4_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_2325-11_0_4_node_224 | 0.4 | n |  | TRUE
41 | bus_LV_2325-11_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_2325-11_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_2325-11_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2325-11_0_4_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_2325-11_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_2325-11_0_4_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_2325-11_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_2325-11_0_4_node_174 | 0.4 | n |  | TRUE
49 | bus_LV_2325-11_0_4_node_96 | 0.4 | n |  | TRUE
50 | bus_LV_2325-11_0_4_node_97 | 0.4 | n |  | TRUE
51 | bus_LV_2325-11_0_4_node_283 | 0.4 | n |  | TRUE
52 | bus_LV_2325-11_0_4_node_98 | 0.4 | n |  | TRUE
53 | bus_LV_2325-11_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_2325-11_0_4_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2325-11_0_4_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_2325-11_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_2325-11_0_4_node_30 | 0.4 | n |  | TRUE
58 | bus_LV_2325-11_0_4_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_2325-11_0_4_node_34 | 0.4 | n |  | TRUE
60 | bus_LV_2325-11_0_4_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_2325-11_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_2325-11_0_4_node_119 | 0.4 | n |  | TRUE
63 | bus_LV_2325-11_0_4_node_120 | 0.4 | n |  | TRUE
64 | bus_LV_2325-11_0_4_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_2325-11_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_2325-11_0_4_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_2325-11_0_4_node_192 | 0.4 | n |  | TRUE
68 | bus_LV_2325-11_0_4_node_236 | 0.4 | n |  | TRUE
69 | bus_LV_2325-11_0_4_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_2325-11_0_4_node_45 | 0.4 | n |  | TRUE
71 | bus_LV_2325-11_0_4_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_2325-11_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_2325-11_0_4_node_207 | 0.4 | n |  | TRUE
74 | bus_LV_2325-11_0_4_node_208 | 0.4 | n |  | TRUE
75 | bus_LV_2325-11_0_4_node_251 | 0.4 | n |  | TRUE
76 | bus_LV_2325-11_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_2325-11_0_4_node_160 | 0.4 | n |  | TRUE
78 | bus_LV_2325-11_0_4_node_233 | 0.4 | n |  | TRUE
79 | bus_LV_2325-11_0_4_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_2325-11_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2325-11_0_4_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_2325-11_0_4_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_2325-11_0_4_node_126 | 0.4 | n |  | TRUE
84 | bus_LV_2325-11_0_4_node_178 | 0.4 | n |  | TRUE
85 | bus_LV_2325-11_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_2325-11_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_2325-11_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_2325-11_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_2325-11_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_2325-11_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_2325-11_0_4_node_94 | 0.4 | n |  | TRUE
92 | bus_LV_2325-11_0_4_node_172 | 0.4 | n |  | TRUE
93 | bus_LV_2325-11_0_4_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_2325-11_0_4_node_169 | 0.4 | n |  | TRUE
95 | bus_LV_2325-11_0_4_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_2325-11_0_4_node_88 | 0.4 | n |  | TRUE
97 | bus_LV_2325-11_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_2325-11_0_4_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_2325-11_0_4_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_2325-11_0_4_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_2325-11_0_4_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_2325-11_0_4_node_113 | 0.4 | n |  | TRUE
103 | bus_LV_2325-11_0_4_node_111 | 0.4 | n |  | TRUE
104 | bus_LV_2325-11_0_4_node_181 | 0.4 | n |  | TRUE
105 | bus_LV_2325-11_0_4_node_245 | 0.4 | n |  | TRUE
106 | bus_LV_2325-11_0_4_node_112 | 0.4 | n |  | TRUE
107 | bus_LV_2325-11_0_4_node_209 | 0.4 | n |  | TRUE
108 | bus_LV_2325-11_0_4_node_244 | 0.4 | n |  | TRUE
109 | bus_LV_2325-11_0_4_node_246 | 0.4 | n |  | TRUE
110 | bus_LV_2325-11_0_4_node_247 | 0.4 | n |  | TRUE
111 | bus_LV_2325-11_0_4_node_171 | 0.4 | n |  | TRUE
112 | bus_LV_2325-11_0_4_node_235 | 0.4 | n |  | TRUE
113 | bus_LV_2325-11_0_4_node_175 | 0.4 | n |  | TRUE
114 | bus_LV_2325-11_0_4_node_237 | 0.4 | n |  | TRUE
115 | bus_LV_2325-11_0_4_node_167 | 0.4 | n |  | TRUE
116 | bus_LV_2325-11_0_4_node_168 | 0.4 | n |  | TRUE
117 | bus_LV_2325-11_0_4_node_170 | 0.4 | n |  | TRUE
118 | bus_LV_2325-11_0_4_node_173 | 0.4 | n |  | TRUE
119 | bus_LV_2325-11_0_4_node_291 | 0.4 | n |  | TRUE
120 | bus_LV_2325-11_0_4_node_290 | 0.4 | n |  | TRUE
121 | bus_LV_2325-11_0_4_node_284 | 0.4 | n |  | TRUE
122 | bus_LV_2325-11_0_4_node_177 | 0.4 | n |  | TRUE
123 | bus_LV_2325-11_0_4_node_180 | 0.4 | n |  | TRUE
124 | bus_LV_2325-11_0_4_node_201 | 0.4 | n |  | TRUE
125 | bus_LV_2325-11_0_4_node_202 | 0.4 | n |  | TRUE
126 | bus_LV_2325-11_0_4_node_206 | 0.4 | n |  | TRUE
127 | bus_LV_2325-11_0_4_node_203 | 0.4 | n |  | TRUE
128 | bus_LV_2325-11_0_4_node_204 | 0.4 | n |  | TRUE
129 | bus_LV_2325-11_0_4_node_205 | 0.4 | n |  | TRUE
130 | bus_LV_2325-11_0_4_node_191 | 0.4 | n |  | TRUE
131 | bus_LV_2325-11_0_4_node_239 | 0.4 | n |  | TRUE
132 | bus_LV_2325-11_0_4_node_248 | 0.4 | n |  | TRUE
133 | bus_LV_2325-11_0_4_node_289 | 0.4 | n |  | TRUE
134 | bus_LV_2325-11_0_4_node_287 | 0.4 | n |  | TRUE
135 | bus_LV_2325-11_0_4_node_288 | 0.4 | n |  | TRUE
136 | bus_LV_2325-11_0_4_node_238 | 0.4 | n |  | TRUE
137 | bus_LV_2325-11_0_4_node_217 | 0.4 | n |  | TRUE
138 | bus_LV_2325-11_0_4_node_219 | 0.4 | n |  | TRUE
139 | bus_LV_2325-11_0_4_node_286 | 0.4 | n |  | TRUE
140 | bus_LV_2325-11_0_4_node_223 | 0.4 | n |  | TRUE
141 | bus_LV_2325-11_0_4_node_268 | 0.4 | n |  | TRUE
142 | bus_LV_2325-11_0_4_node_267 | 0.4 | n |  | TRUE
143 | bus_LV_2325-11_0_4_node_240 | 0.4 | n |  | TRUE
144 | bus_LV_2325-11_0_4_node_241 | 0.4 | n |  | TRUE
145 | bus_LV_2325-11_0_4_node_242 | 0.4 | n |  | TRUE
146 | bus_LV_2325-11_0_4_node_266 | 0.4 | n |  | TRUE
147 | bus_LV_2325-11_0_4_node_271 | 0.4 | n |  | TRUE
148 | bus_LV_2325-11_0_4_node_272 | 0.4 | n |  | TRUE
149 | bus_LV_2325-11_0_4_node_275 | 0.4 | n |  | TRUE
150 | bus_LV_2325-11_0_4_node_292 | 0.4 | n |  | TRUE
151 | bus_LV_2325-11_0_4_node_293 | 0.4 | n |  | TRUE
152 | bus_MV_37_0_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-11_0_4_load_0 | 0 | 0.0007254 | 0.0001818 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-11_0_4_load_1 | 1 | 0.0014877 | 0.00037286 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-11_0_4_load_179 | 3 | 0.0016937 | 0.00042447 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-11_0_4_load_76 | 4 | 0.00076472 | 0.00019166 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-11_0_4_load_42 | 5 | 0.0013212 | 0.00033112 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-11_0_4_load_41 | 8 | 0.00081812 | 0.00020504 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-11_0_4_load_3 | 10 | 0.00069665 | 0.0001746 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-11_0_4_load_108 | 11 | 0.00068867 | 0.0001726 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-11_0_4_load_200 | 12 | 0.0011297 | 0.00028312 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-11_0_4_load_109 | 13 | 0.0015968 | 0.0004002 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-11_0_4_load_199 | 14 | 0.0018058 | 0.00045259 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-11_0_4_load_5 | 15 | 0.010657 | 0.0026709 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-11_0_4_load_9 | 17 | 0.0016463 | 0.00041261 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-11_0_4_load_10 | 18 | 0.0027162 | 0.00068074 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-11_0_4_load_12 | 20 | 0.0018711 | 0.00046895 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-11_0_4_load_274 | 21 | 0.0054654 | 0.0013698 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-11_0_4_load_190 | 24 | 0.0012132 | 0.00030407 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-11_0_4_load_188 | 25 | 0.0013184 | 0.00033043 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-11_0_4_load_13 | 26 | 0.0031677 | 0.00079389 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-11_0_4_load_15 | 28 | 0.0026364 | 0.00066074 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-11_0_4_load_16 | 29 | 0.0018051 | 0.00045241 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-11_0_4_load_17 | 30 | 0.0013909 | 0.00034858 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-11_0_4_load_18 | 31 | 0.0039419 | 0.00098792 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-11_0_4_load_222 | 32 | 0.0030802 | 0.00077198 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-11_0_4_load_285 | 33 | 0.0026447 | 0.00066282 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-11_0_4_load_19 | 35 | 0.0009796 | 0.00024551 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-11_0_4_load_20 | 36 | 0.0026147 | 0.00065532 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-11_0_4_load_249 | 37 | 0.0025917 | 0.00064953 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-11_0_4_load_40 | 39 | 0.0010721 | 0.00026869 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-11_0_4_load_224 | 40 | 0.0015429 | 0.0003867 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-11_0_4_load_25 | 41 | 0.0020838 | 0.00052225 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-11_0_4_load_21 | 42 | 0.0011911 | 0.00029852 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-11_0_4_load_39 | 43 | 0.0011442 | 0.00028676 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-11_0_4_load_22 | 44 | 0.0013389 | 0.00033557 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-11_0_4_load_24 | 45 | 0.0012404 | 0.00031088 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-11_0_4_load_26 | 46 | 0.0022607 | 0.00056659 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-11_0_4_load_174 | 48 | 0.0010198 | 0.00025559 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-11_0_4_load_96 | 49 | 0.00054994 | 0.00013783 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-11_0_4_load_97 | 50 | 0.0015235 | 0.00038181 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-11_0_4_load_283 | 51 | 0.0025663 | 0.00064317 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-11_0_4_load_98 | 52 | 0.0012183 | 0.00030533 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-11_0_4_load_28 | 53 | 0.00056543 | 0.00014171 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-11_0_4_load_30 | 57 | 0.0012932 | 0.0003241 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-11_0_4_load_34 | 59 | 0.0015692 | 0.00039327 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-11_0_4_load_35 | 60 | 0.00080681 | 0.00020221 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-11_0_4_load_36 | 61 | 0.00066539 | 0.00016676 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-11_0_4_load_119 | 62 | 0.0011483 | 0.00028779 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-11_0_4_load_120 | 63 | 0.0039096 | 0.00097984 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-11_0_4_load_37 | 64 | 0.0010748 | 0.00026937 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-11_0_4_load_44 | 65 | 0.00050987 | 0.00012779 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-11_0_4_load_192 | 67 | 0.0014548 | 0.0003646 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2325-11_0_4_load_236 | 68 | 0.0015384 | 0.00038556 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2325-11_0_4_load_38 | 69 | 0.0009886 | 0.00024777 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2325-11_0_4_load_45 | 70 | 0.00096712 | 0.00024238 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2325-11_0_4_load_67 | 71 | 0.0012608 | 0.00031598 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2325-11_0_4_load_63 | 72 | 0.00057233 | 0.00014344 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2325-11_0_4_load_207 | 73 | 0.0014166 | 0.00035504 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2325-11_0_4_load_208 | 74 | 0.00070522 | 0.00017674 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2325-11_0_4_load_251 | 75 | 0.0014945 | 0.00037455 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2325-11_0_4_load_46 | 76 | 0.0016555 | 0.0004149 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2325-11_0_4_load_160 | 77 | 0.0013822 | 0.00034641 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2325-11_0_4_load_233 | 78 | 0.0026485 | 0.00066377 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2325-11_0_4_load_62 | 79 | 0.00086736 | 0.00021738 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2325-11_0_4_load_64 | 80 | 0.0022919 | 0.0005744 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2325-11_0_4_load_66 | 81 | 0.0017627 | 0.00044177 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2325-11_0_4_load_68 | 82 | 0.0026888 | 0.00067387 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2325-11_0_4_load_126 | 83 | 0.0017348 | 0.00043477 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2325-11_0_4_load_178 | 84 | 0.0012649 | 0.00031702 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2325-11_0_4_load_77 | 85 | 0.0016489 | 0.00041324 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2325-11_0_4_load_78 | 86 | 0.00098644 | 0.00024723 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2325-11_0_4_load_79 | 87 | 0.00098418 | 0.00024666 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2325-11_0_4_load_80 | 88 | 0.00080133 | 0.00020083 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2325-11_0_4_load_81 | 89 | 0.0024455 | 0.0006129 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2325-11_0_4_load_82 | 90 | 0.0007517 | 0.00018839 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2325-11_0_4_load_94 | 91 | 0.00099806 | 0.00025014 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2325-11_0_4_load_172 | 92 | 0.0022545 | 0.00056503 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2325-11_0_4_load_95 | 93 | 0.00074474 | 0.00018665 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2325-11_0_4_load_87 | 95 | 0.0030821 | 0.00077244 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2325-11_0_4_load_88 | 96 | 0.0016082 | 0.00040305 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2325-11_0_4_load_89 | 97 | 0.0019242 | 0.00048226 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2325-11_0_4_load_90 | 98 | 0.0019229 | 0.00048193 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2325-11_0_4_load_91 | 99 | 0.0021378 | 0.00053579 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2325-11_0_4_load_93 | 101 | 0.0019226 | 0.00048184 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2325-11_0_4_load_113 | 102 | 0.0017347 | 0.00043475 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2325-11_0_4_load_111 | 103 | 0.00067147 | 0.00016829 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2325-11_0_4_load_181 | 104 | 0.0010008 | 0.00025083 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2325-11_0_4_load_112 | 106 | 0.0024386 | 0.00061117 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2325-11_0_4_load_209 | 107 | 0.0010021 | 0.00025115 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2325-11_0_4_load_244 | 108 | 0.0010933 | 0.00027399 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2325-11_0_4_load_246 | 109 | 0.0015551 | 0.00038976 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2325-11_0_4_load_247 | 110 | 0.0037797 | 0.00094728 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2325-11_0_4_load_171 | 111 | 0.001985 | 0.00049749 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2325-11_0_4_load_235 | 112 | 0.00070564 | 0.00017685 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2325-11_0_4_load_175 | 113 | 0.0010081 | 0.00025265 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2325-11_0_4_load_237 | 114 | 0.001232 | 0.00030876 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2325-11_0_4_load_167 | 115 | 0.0011022 | 0.00027624 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2325-11_0_4_load_168 | 116 | 0.0016318 | 0.00040896 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2325-11_0_4_load_170 | 117 | 0.0010878 | 0.00027264 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2325-11_0_4_load_173 | 118 | 0.001883 | 0.00047193 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2325-11_0_4_load_291 | 119 | 0.0025687 | 0.00064378 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2325-11_0_4_load_290 | 120 | 0.0030008 | 0.00075208 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2325-11_0_4_load_284 | 121 | 0.0019113 | 0.00047903 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2325-11_0_4_load_177 | 122 | 0.0018271 | 0.00045792 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2325-11_0_4_load_180 | 123 | 0.0010301 | 0.00025816 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2325-11_0_4_load_201 | 124 | 0.001449 | 0.00036316 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2325-11_0_4_load_206 | 126 | 0.00072162 | 0.00018086 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2325-11_0_4_load_203 | 127 | 0.00067388 | 0.00016889 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2325-11_0_4_load_204 | 128 | 0.00089367 | 0.00022398 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2325-11_0_4_load_205 | 129 | 0.00091126 | 0.00022838 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2325-11_0_4_load_191 | 130 | 0.0010801 | 0.0002707 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2325-11_0_4_load_239 | 131 | 0.00084351 | 0.0002114 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2325-11_0_4_load_289 | 133 | 0.0018091 | 0.00045341 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2325-11_0_4_load_287 | 134 | 0.0015394 | 0.0003858 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2325-11_0_4_load_288 | 135 | 0.0029194 | 0.00073167 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2325-11_0_4_load_238 | 136 | 0.0010984 | 0.00027528 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2325-11_0_4_load_217 | 137 | 0.0012246 | 0.00030692 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2325-11_0_4_load_286 | 139 | 0.0030979 | 0.0007764 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2325-11_0_4_load_223 | 140 | 0.0025994 | 0.00065148 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2325-11_0_4_load_268 | 141 | 0.00072554 | 0.00018184 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2325-11_0_4_load_267 | 142 | 0.0015471 | 0.00038774 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2325-11_0_4_load_241 | 144 | 0.0010856 | 0.00027208 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2325-11_0_4_load_242 | 145 | 0.0010762 | 0.00026972 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2325-11_0_4_load_266 | 146 | 0.0011322 | 0.00028375 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2325-11_0_4_load_271 | 147 | 0.0019685 | 0.00049334 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2325-11_0_4_load_272 | 148 | 0.0031245 | 0.00078307 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2325-11_0_4_load_275 | 149 | 0.0060395 | 0.0015136 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2325-11_0_4_load_292 | 150 | 0.0031606 | 0.00079211 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2325-11_0_4_load_293 | 151 | 0.0017478 | 0.00043805 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-11_0_4_line_0 |  | 0 | 1 | 0.0082261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-11_0_4_line_1 |  | 0 | 2 | 0.053495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-11_0_4_line_2 |  | 1 | 3 | 0.087722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-11_0_4_line_3 |  | 2 | 4 | 0.040153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-11_0_4_line_4 |  | 2 | 5 | 0.041669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-11_0_4_line_5 |  | 2 | 6 | 0.022491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-11_0_4_line_6 |  | 3 | 7 | 0.044533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-11_0_4_line_7 |  | 4 | 75 | 0.0029616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-11_0_4_line_8 |  | 5 | 8 | 0.039255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-11_0_4_line_9 |  | 6 | 12 | 0.021566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-11_0_4_line_10 |  | 6 | 9 | 0.009977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-11_0_4_line_11 |  | 7 | 84 | 0.0067711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-11_0_4_line_12 |  | 7 | 113 | 0.019401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-11_0_4_line_13 |  | 9 | 10 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-11_0_4_line_14 |  | 10 | 11 | 0.0020443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-11_0_4_line_15 |  | 11 | 13 | 0.0034765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-11_0_4_line_16 |  | 12 | 14 | 0.024326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-11_0_4_line_17 |  | 14 | 124 | 0.025406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-11_0_4_line_18 |  | 15 | 16 | 0.027763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-11_0_4_line_19 |  | 16 | 17 | 0.017388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-11_0_4_line_20 |  | 16 | 18 | 0.040901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-11_0_4_line_21 |  | 17 | 19 | 0.014092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-11_0_4_line_22 |  | 18 | 20 | 0.004611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-11_0_4_line_23 |  | 19 | 21 | 0.0092379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-11_0_4_line_24 |  | 20 | 22 | 0.036251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-11_0_4_line_25 |  | 21 | 23 | 0.022366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-11_0_4_line_26 |  | 22 | 24 | 0.021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-11_0_4_line_27 |  | 22 | 25 | 0.010783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-11_0_4_line_28 |  | 23 | 147 | 0.085361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-11_0_4_line_29 |  | 24 | 130 | 0.024574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-11_0_4_line_30 |  | 26 | 27 | 0.010973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-11_0_4_line_31 |  | 26 | 28 | 0.020816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-11_0_4_line_32 |  | 27 | 29 | 0.016943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2325-11_0_4_line_33 |  | 27 | 30 | 0.011465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2325-11_0_4_line_34 |  | 28 | 31 | 0.013451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-11_0_4_line_35 |  | 29 | 35 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2325-11_0_4_line_36 |  | 30 | 36 | 0.020797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2325-11_0_4_line_37 |  | 31 | 37 | 0.010582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-11_0_4_line_38 |  | 32 | 33 | 0.068291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2325-11_0_4_line_39 |  | 32 | 34 | 0.028215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2325-11_0_4_line_40 |  | 33 | 121 | 0.004714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2325-11_0_4_line_41 |  | 34 | 139 | 0.099633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2325-11_0_4_line_42 |  | 34 | 138 | 0.035908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-11_0_4_line_43 |  | 35 | 38 | 0.034079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2325-11_0_4_line_44 |  | 36 | 39 | 0.021566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2325-11_0_4_line_45 |  | 37 | 40 | 0.016338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-11_0_4_line_46 |  | 38 | 41 | 0.02843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2325-11_0_4_line_47 |  | 38 | 42 | 0.022413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2325-11_0_4_line_48 |  | 39 | 43 | 0.0040257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2325-11_0_4_line_49 |  | 40 | 140 | 0.03128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-11_0_4_line_50 |  | 41 | 47 | 0.036261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2325-11_0_4_line_51 |  | 42 | 44 | 0.028319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2325-11_0_4_line_52 |  | 43 | 73 | 0.227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2325-11_0_4_line_53 |  | 44 | 45 | 0.0034482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2325-11_0_4_line_54 |  | 45 | 46 | 0.02499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_2325-11_0_4_line_55 |  | 46 | 48 | 0.0061885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_2325-11_0_4_line_56 |  | 47 | 49 | 0.020953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2325-11_0_4_line_57 |  | 47 | 50 | 0.026553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2325-11_0_4_line_58 |  | 48 | 51 | 0.021906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_2325-11_0_4_line_59 |  | 49 | 52 | 0.017365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2325-11_0_4_line_60 |  | 51 | 121 | 0.026569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2325-11_0_4_line_61 |  | 52 | 104 | 0.0094118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2325-11_0_4_line_62 |  | 53 | 54 | 0.020295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2325-11_0_4_line_63 |  | 54 | 55 | 0.038533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2325-11_0_4_line_64 |  | 54 | 56 | 0.018553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2325-11_0_4_line_65 |  | 55 | 59 | 0.022284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-11_0_4_line_66 |  | 55 | 60 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2325-11_0_4_line_67 |  | 56 | 61 | 0.020218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2325-11_0_4_line_68 |  | 57 | 58 | 0.014693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2325-11_0_4_line_69 |  | 58 | 62 | 0.013345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2325-11_0_4_line_70 |  | 58 | 63 | 0.03037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2325-11_0_4_line_71 |  | 59 | 64 | 0.023162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2325-11_0_4_line_72 |  | 60 | 65 | 0.029647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2325-11_0_4_line_73 |  | 61 | 66 | 0.021377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2325-11_0_4_line_74 |  | 62 | 67 | 0.0075597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2325-11_0_4_line_75 |  | 63 | 68 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2325-11_0_4_line_76 |  | 64 | 69 | 0.019618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2325-11_0_4_line_77 |  | 65 | 70 | 0.030243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2325-11_0_4_line_78 |  | 66 | 71 | 0.026953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2325-11_0_4_line_79 |  | 66 | 72 | 0.0044808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2325-11_0_4_line_80 |  | 67 | 111 | 0.019197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2325-11_0_4_line_81 |  | 68 | 112 | 0.024653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2325-11_0_4_line_82 |  | 70 | 76 | 0.020706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2325-11_0_4_line_83 |  | 71 | 83 | 0.018322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2325-11_0_4_line_84 |  | 72 | 79 | 0.0069499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2325-11_0_4_line_85 |  | 73 | 74 | 0.022104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_2325-11_0_4_line_86 |  | 74 | 107 | 0.012659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2325-11_0_4_line_87 |  | 76 | 77 | 0.060463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2325-11_0_4_line_88 |  | 77 | 78 | 0.00092314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2325-11_0_4_line_89 |  | 79 | 80 | 0.019849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2325-11_0_4_line_90 |  | 80 | 81 | 0.021687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2325-11_0_4_line_91 |  | 81 | 82 | 0.014934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2325-11_0_4_line_92 |  | 83 | 84 | 0.044436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2325-11_0_4_line_93 |  | 85 | 86 | 0.019299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2325-11_0_4_line_94 |  | 85 | 87 | 0.010226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2325-11_0_4_line_95 |  | 86 | 88 | 0.0029757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2325-11_0_4_line_96 |  | 87 | 89 | 0.0036299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2325-11_0_4_line_97 |  | 88 | 90 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2325-11_0_4_line_98 |  | 89 | 91 | 0.014435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2325-11_0_4_line_99 |  | 90 | 92 | 0.0035304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2325-11_0_4_line_100 |  | 91 | 93 | 0.0047869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2325-11_0_4_line_101 |  | 92 | 94 | 0.018711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2325-11_0_4_line_102 |  | 93 | 107 | 0.018838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2325-11_0_4_line_103 |  | 94 | 111 | 0.015911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2325-11_0_4_line_104 |  | 94 | 115 | 0.035503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2325-11_0_4_line_105 |  | 95 | 96 | 0.018146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2325-11_0_4_line_106 |  | 95 | 97 | 0.021192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2325-11_0_4_line_107 |  | 96 | 98 | 0.020447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2325-11_0_4_line_108 |  | 97 | 99 | 0.013244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2325-11_0_4_line_109 |  | 98 | 100 | 0.012464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2325-11_0_4_line_110 |  | 99 | 101 | 0.0088929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2325-11_0_4_line_111 |  | 100 | 102 | 0.016677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2325-11_0_4_line_112 |  | 100 | 103 | 0.029817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2325-11_0_4_line_113 |  | 101 | 104 | 0.030576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2325-11_0_4_line_114 |  | 102 | 105 | 0.059865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2325-11_0_4_line_115 |  | 103 | 106 | 0.015737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2325-11_0_4_line_116 |  | 105 | 109 | 0.026846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2325-11_0_4_line_117 |  | 105 | 110 | 0.029122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2325-11_0_4_line_118 |  | 107 | 108 | 0.028708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_2325-11_0_4_line_119 |  | 108 | 123 | 0.0078258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_2325-11_0_4_line_120 |  | 109 | 132 | 0.036039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2325-11_0_4_line_121 |  | 112 | 114 | 0.013878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2325-11_0_4_line_122 |  | 113 | 122 | 0.021966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_2325-11_0_4_line_123 |  | 115 | 116 | 0.0033131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2325-11_0_4_line_124 |  | 116 | 117 | 0.016973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2325-11_0_4_line_125 |  | 117 | 118 | 0.010533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2325-11_0_4_line_126 |  | 118 | 119 | 0.025418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2325-11_0_4_line_127 |  | 119 | 120 | 0.010987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2325-11_0_4_line_128 |  | 120 | 150 | 0.043041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2325-11_0_4_line_129 |  | 122 | 123 | 0.020031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_2325-11_0_4_line_130 |  | 124 | 125 | 0.015904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2325-11_0_4_line_131 |  | 125 | 126 | 0.044651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2325-11_0_4_line_132 |  | 126 | 129 | 0.00023627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2325-11_0_4_line_133 |  | 127 | 128 | 0.025864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2325-11_0_4_line_134 |  | 127 | 129 | 0.027451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2325-11_0_4_line_135 |  | 130 | 131 | 0.015664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2325-11_0_4_line_136 |  | 131 | 136 | 0.011544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2325-11_0_4_line_137 |  | 132 | 133 | 0.01497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2325-11_0_4_line_138 |  | 132 | 134 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2325-11_0_4_line_139 |  | 134 | 135 | 0.023538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2325-11_0_4_line_140 |  | 136 | 143 | 0.0302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2325-11_0_4_line_141 |  | 137 | 138 | 0.23535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2325-11_0_4_line_142 |  | 139 | 141 | 0.008276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_2325-11_0_4_line_143 |  | 141 | 142 | 0.035367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
144 | LV_2325-11_0_4_line_144 |  | 142 | 146 | 0.011983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
145 | LV_2325-11_0_4_line_145 |  | 143 | 144 | 0.01512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2325-11_0_4_line_146 |  | 143 | 145 | 0.0050278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2325-11_0_4_line_147 |  | 145 | 146 | 0.12366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2325-11_0_4_line_148 |  | 147 | 148 | 0.024622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2325-11_0_4_line_149 |  | 148 | 149 | 0.31207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2325-11_0_4_line_150 |  | 150 | 151 | 0.048354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-11_0_4_trafo_27 | 0.63 MVA 20/0.4 kV | 152 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2562614.0743 | 1152093.3091 | 2562610.0088 | 1152094.824 | 2562606.1776 | 1152095.4835
1 | 2562552.7685 | 1152098.5158 | 2562606.1776 | 1152095.4835
2 | 2562701.0576 | 1152081.9515 | 2562614.0743 | 1152093.3091
3 | 2562552.7685 | 1152098.5158 | 2562539.9792 | 1152092.8815 | 2562526.7306 | 1152091.1299 | 2562514.2072 | 1152093.8406
4 | 2562552.7685 | 1152098.5158 | 2562555.1067 | 1152085.8281 | 2562558.3594 | 1152075.8138 | 2562565.9901 | 1152059.2484
5 | 2562552.7685 | 1152098.5158 | 2562553.3939 | 1152110.1956 | 2562555.7234 | 1152120.7309
6 | 2562701.0576 | 1152081.9515 | 2562722.1599 | 1152082.9989 | 2562736.3636 | 1152084.0891 | 2562745.3041 | 1152086.6016
7 | 2562514.2072 | 1152093.8406 | 2562511.3126 | 1152094.4672
8 | 2562565.9901 | 1152059.2484 | 2562571.1932 | 1152047.953 | 2562579.7333 | 1152030.5354 | 2562584.1934 | 1152024.6046 | 2562584.1934 | 1152024.6046
9 | 2562555.7234 | 1152120.7309 | 2562542.0053 | 1152124.8963 | 2562535.2957 | 1152127.5872
10 | 2562555.7234 | 1152120.7309 | 2562558.5227 | 1152130.3072
11 | 2562745.3041 | 1152086.6016 | 2562741.3869 | 1152092.1246
12 | 2562745.3041 | 1152086.6016 | 2562748.385 | 1152082.2469 | 2562758.173 | 1152072.1443
13 | 2562558.5227 | 1152130.3072 | 2562559.5278 | 1152141.351 | 2562559.0218 | 1152148.3569
14 | 2562559.0218 | 1152148.3569 | 2562558.8745 | 1152150.3959
15 | 2562558.3952 | 1152153.8296 | 2562558.7366 | 1152152.3059 | 2562558.8745 | 1152150.3959
16 | 2562512.8437 | 1152136.9329 | 2562517.931 | 1152134.5513 | 2562535.2957 | 1152127.5872
17 | 2562489.6702 | 1152147.3389 | 2562500.8909 | 1152142.5284 | 2562512.8437 | 1152136.9329
18 | 2562384.7194 | 1151475.4932 | 2562371.7157 | 1151450.9638
19 | 2562384.7194 | 1151475.4932 | 2562379.6835 | 1151476.5141 | 2562368.0015 | 1151480.2011
20 | 2562384.7194 | 1151475.4932 | 2562388.184 | 1151474.7933 | 2562396.1332 | 1151475.7107 | 2562420.6779 | 1151484.4171 | 2562423.6961 | 1151485.8034
21 | 2562354.9267 | 1151485.4181 | 2562364.3029 | 1151481.3684 | 2562368.0015 | 1151480.2011
22 | 2562427.8863 | 1151487.7279 | 2562423.6961 | 1151485.8034
23 | 2562354.9267 | 1151485.4181 | 2562346.4463 | 1151489.0817
24 | 2562462.2174 | 1151498.498 | 2562443.7686 | 1151495.0226 | 2562427.8863 | 1151487.7279
25 | 2562324.6442 | 1151493.1118 | 2562331.4361 | 1151493.0692 | 2562343.5681 | 1151490.3251 | 2562346.4463 | 1151489.0817
26 | 2562462.2174 | 1151498.498 | 2562471.5965 | 1151498.5839 | 2562483.5225 | 1151497.2643 | 2562483.5225 | 1151497.2643
27 | 2562462.2174 | 1151498.498 | 2562453.6354 | 1151491.9693
28 | 2562324.6442 | 1151493.1118 | 2562239.396 | 1151488.7225
29 | 2562483.5225 | 1151497.2643 | 2562488.1342 | 1151492.2107 | 2562493.8829 | 1151479.9797 | 2562493.9894 | 1151475.7629
30 | 2562784.4762 | 1151744.2515 | 2562785.1533 | 1151733.2989
31 | 2562786.4377 | 1151712.5226 | 2562785.1533 | 1151733.2989
32 | 2562784.4762 | 1151744.2515 | 2562772.6838 | 1151746.0032 | 2562767.8671 | 1151747.4198
33 | 2562784.4762 | 1151744.2515 | 2562783.9497 | 1151755.7046
34 | 2562786.4377 | 1151712.5226 | 2562787.2676 | 1151699.0975
35 | 2562754.0605 | 1151751.4803 | 2562767.8671 | 1151747.4198
36 | 2562783.9497 | 1151755.7046 | 2562782.9946 | 1151776.4801
37 | 2562787.9205 | 1151688.536 | 2562787.2676 | 1151699.0975
38 | 2562736.6264 | 1151556.4198 | 2562719.6161 | 1151622.5584
39 | 2562747.0401 | 1151530.1969 | 2562736.6264 | 1151556.4198
40 | 2562719.6161 | 1151622.5584 | 2562719.6757 | 1151627.272
41 | 2562747.0401 | 1151530.1969 | 2562661.8891 | 1151478.4659
42 | 2562780.613 | 1151543.1843 | 2562747.0401 | 1151530.1969
43 | 2562721.3664 | 1151761.0957 | 2562754.0605 | 1151751.4803
44 | 2562781.1638 | 1151797.9659 | 2562782.8532 | 1151779.5572 | 2562782.9946 | 1151776.4801
45 | 2562788.9286 | 1151672.2296 | 2562787.9205 | 1151688.536
46 | 2562721.3664 | 1151761.0957 | 2562694.3085 | 1151769.8208
47 | 2562721.3664 | 1151761.0957 | 2562721.0833 | 1151738.6843
48 | 2562781.1638 | 1151797.9659 | 2562781.1638 | 1151797.9659 | 2562780.3088 | 1151801.8998
49 | 2562788.9286 | 1151672.2296 | 2562789.6379 | 1151660.7548 | 2562791.7619 | 1151641.0855
50 | 2562660.6957 | 1151767.787 | 2562665.3017 | 1151771.7048 | 2562667.7128 | 1151773.1572 | 2562672.2078 | 1151774.0408 | 2562676.9149 | 1151774.4785 | 2562680.7657 | 1151774.1878 | 2562694.3085 | 1151769.8208
51 | 2562720.7255 | 1151710.3671 | 2562721.0833 | 1151738.6843
52 | 2562772.4753 | 1152028.7633 | 2562780.3088 | 1151801.8998
53 | 2562720.7255 | 1151710.3671 | 2562720.6819 | 1151706.9192
54 | 2562720.6819 | 1151706.9192 | 2562720.3662 | 1151681.9311
55 | 2562720.2881 | 1151675.7431 | 2562720.3662 | 1151681.9311
56 | 2562660.6957 | 1151767.787 | 2562658.9873 | 1151763.3398 | 2562657.1162 | 1151756.1589 | 2562656.5715 | 1151748.7918 | 2562656.533 | 1151747.4114
57 | 2562660.6957 | 1151767.787 | 2562657.2141 | 1151770.6768 | 2562635.6684 | 1151775.2612
58 | 2562720.2881 | 1151675.7431 | 2562720.0113 | 1151653.839
59 | 2562656.533 | 1151747.4114 | 2562656.0493 | 1151730.0536
60 | 2562719.6757 | 1151627.272 | 2562720.0113 | 1151653.839
61 | 2562655.787 | 1151720.6454 | 2562656.0493 | 1151730.0536
62 | 2562868.9236 | 1152147.2449 | 2562887.7485 | 1152139.6606
63 | 2562882.2742 | 1152182.9138 | 2562882.8832 | 1152180.8757 | 2562868.9236 | 1152147.2449
64 | 2562851.8409 | 1152154.5987 | 2562868.9236 | 1152147.2449
65 | 2562882.2742 | 1152182.9138 | 2562888.0224 | 1152183.0006 | 2562903.1526 | 1152176.3311
66 | 2562882.2742 | 1152182.9138 | 2562881.5298 | 1152185.3975 | 2562868.6503 | 1152190.7257
67 | 2562851.8409 | 1152154.5987 | 2562848.7269 | 1152147.4143 | 2562842.1348 | 1152141.1852 | 2562839.2826 | 1152139.4888
68 | 2562946.0878 | 1152111.6503 | 2562933.2996 | 1152118.8853
69 | 2562946.0878 | 1152111.6503 | 2562945.1013 | 1152102.2628 | 2562943.9208 | 1152098.5397
70 | 2562946.0878 | 1152111.6503 | 2562954.9835 | 1152105.6813 | 2562965.3135 | 1152100.8485 | 2562973.1275 | 1152098.1928
71 | 2562903.1526 | 1152176.3311 | 2562924.3465 | 1152166.9887
72 | 2562841.2555 | 1152202.059 | 2562868.6503 | 1152190.7257
73 | 2562820.4531 | 1152129.569 | 2562825.1897 | 1152131.1071 | 2562839.2826 | 1152139.4888
74 | 2562943.9208 | 1152098.5397 | 2562942.4873 | 1152094.0192 | 2562940.9762 | 1152091.6413
75 | 2562973.1275 | 1152098.1928 | 2562973.8751 | 1152097.9387 | 2562981.2775 | 1152096.2033 | 2562987.6709 | 1152095.1189 | 2562996.6369 | 1152094.3189 | 2562996.6369 | 1152094.3189
76 | 2562942.2979 | 1152159.0756 | 2562924.3465 | 1152166.9887
77 | 2562841.2555 | 1152202.059 | 2562818.4051 | 1152211.5122 | 2562813.3761 | 1152213.7735
78 | 2562820.4531 | 1152129.569 | 2562809.188 | 1152125.9035 | 2562794.5715 | 1152122.0861
79 | 2562820.4531 | 1152129.569 | 2562816.1802 | 1152130.9182
80 | 2562925.9367 | 1152080.402 | 2562928.2121 | 1152081.3341 | 2562938.5042 | 1152087.7516 | 2562940.9762 | 1152091.6413
81 | 2563020.7264 | 1152099.0892 | 2563003.7992 | 1152094.7305 | 2562996.6369 | 1152094.3189
82 | 2562794.7223 | 1152222.7341 | 2562801.4088 | 1152219.1546 | 2562813.3761 | 1152213.7735
83 | 2562794.5715 | 1152122.0861 | 2562787.8583 | 1152120.3328 | 2562776.5187 | 1152119.3336
84 | 2562809.5528 | 1152133.0108 | 2562816.1802 | 1152130.9182
85 | 2562793.8383 | 1152034.3703 | 2562789.4879 | 1152032.856 | 2562772.4753 | 1152028.7633
86 | 2562793.8383 | 1152034.3703 | 2562805.7933 | 1152038.5315
87 | 2562794.7223 | 1152222.7341 | 2562758.7381 | 1152241.9973 | 2562752.7281 | 1152243.0017 | 2562750.0109 | 1152241.6623 | 2562747.4111 | 1152239.444 | 2562743.8084 | 1152233.3175
88 | 2562743.8084 | 1152233.3175 | 2562743.3405 | 1152232.5218
89 | 2562809.5528 | 1152133.0108 | 2562790.6249 | 1152138.9874
90 | 2562769.9448 | 1152145.5172 | 2562790.6249 | 1152138.9874
91 | 2562755.7043 | 1152150.0138 | 2562769.9448 | 1152145.5172
92 | 2562776.5187 | 1152119.3336 | 2562741.3869 | 1152092.1246
93 | 2562854.9606 | 1152054.8553 | 2562871.2671 | 1152057.1179 | 2562874.1001 | 1152057.2437
94 | 2562845.1047 | 1152052.3907 | 2562849.5616 | 1152054.1061 | 2562854.9606 | 1152054.8553
95 | 2562877.0729 | 1152057.3758 | 2562874.1001 | 1152057.2437
96 | 2562845.1047 | 1152052.3907 | 2562841.7171 | 1152051.0867
97 | 2562877.0729 | 1152057.3758 | 2562890.6033 | 1152057.9767 | 2562898.9279 | 1152058.8949
98 | 2562841.7171 | 1152051.0867 | 2562832.9614 | 1152047.7167 | 2562828.1717 | 1152046.1047
99 | 2562902.437 | 1152059.282 | 2562898.9279 | 1152058.8949
100 | 2562823.6348 | 1152044.5779 | 2562828.1717 | 1152046.1047
101 | 2562917.6397 | 1152069.2821 | 2562915.493 | 1152065.8825 | 2562911.1391 | 1152062.9635 | 2562902.437 | 1152059.282
102 | 2562823.6348 | 1152044.5779 | 2562809.4452 | 1152039.8026 | 2562805.7933 | 1152038.5315
103 | 2562917.6397 | 1152069.2821 | 2562917.1126 | 1152072.1646 | 2562919.7108 | 1152077.8515 | 2562925.9367 | 1152080.402
104 | 2562917.6397 | 1152069.2821 | 2562921.3075 | 1152049.3382 | 2562926.3583 | 1152037.112 | 2562928.0093 | 1152035.9908
105 | 2562613.765 | 1151658.1271 | 2562614.1721 | 1151657.876 | 2562629.2536 | 1151656.8038 | 2562631.6717 | 1151657.6071
106 | 2562648.3633 | 1151669.3624 | 2562644.6998 | 1151663.7669 | 2562638.09 | 1151659.7393 | 2562631.6717 | 1151657.6071
107 | 2562613.765 | 1151658.1271 | 2562602.5744 | 1151665.0296 | 2562598.36 | 1151670.9884
108 | 2562648.3633 | 1151669.3624 | 2562652.014 | 1151674.9382 | 2562653.4381 | 1151681.3618
109 | 2562591.1631 | 1151681.1644 | 2562598.36 | 1151670.9884
110 | 2562655.0766 | 1151690.0783 | 2562655.0461 | 1151688.6152 | 2562653.4381 | 1151681.3618
111 | 2562591.1631 | 1151681.1644 | 2562587.5845 | 1151686.9563 | 2562581.6287 | 1151694.8258
112 | 2562591.1631 | 1151681.1644 | 2562594.8565 | 1151690.1015 | 2562595.6842 | 1151710.2315
113 | 2562655.787 | 1151720.6454 | 2562655.4947 | 1151710.1567 | 2562655.0766 | 1151690.0783
114 | 2562539.6314 | 1151734.5126 | 2562547.9876 | 1151733.0709 | 2562557.9898 | 1151726.0605 | 2562581.6287 | 1151694.8258
115 | 2562596.3307 | 1151725.955 | 2562595.6842 | 1151710.2315
116 | 2562539.6314 | 1151734.5126 | 2562539.0494 | 1151729.7916 | 2562539.3345 | 1151707.7044
117 | 2562514.5317 | 1151733.8354 | 2562528.7884 | 1151739.5828 | 2562536.8769 | 1151739.5323 | 2562539.6314 | 1151734.5126
118 | 2562805.7933 | 1152038.5315 | 2562803.698 | 1152067.1632
119 | 2562803.698 | 1152067.1632 | 2562796.0395 | 1152065.5534
120 | 2562539.7996 | 1151671.6685 | 2562539.3345 | 1151707.7044
121 | 2563034.1877 | 1152102.4594 | 2563030.1936 | 1152101.527 | 2563020.7264 | 1152099.0892
122 | 2562758.173 | 1152072.1443 | 2562766.0145 | 1152064.0506 | 2562774.6789 | 1152061.6401 | 2562776.3699 | 1152061.8411
123 | 2562930.7501 | 1152034.1296 | 2562928.0093 | 1152035.9908
124 | 2562930.7501 | 1152034.1296 | 2562936.568 | 1152030.1788 | 2562946.3491 | 1152028.4046
125 | 2562956.8082 | 1152027.1928 | 2562947.798 | 1152028.1418 | 2562946.3491 | 1152028.4046
126 | 2562982.1004 | 1152024.7842 | 2562979.525 | 1152024.8001 | 2562956.8082 | 1152027.1928
127 | 2562993.0872 | 1152024.7165 | 2562982.1004 | 1152024.7842
128 | 2562993.0872 | 1152024.7165 | 2562998.6481 | 1152024.6822 | 2563006.3227 | 1152022.2782 | 2563009.8429 | 1152016.9427 | 2563011.1625 | 1152006.9183 | 2563008.3454 | 1151998.0868 | 2563004.9282 | 1151996.7626
129 | 2562776.3699 | 1152061.8411 | 2562780.9916 | 1152062.3903 | 2562796.0395 | 1152065.5534
130 | 2562474.6613 | 1152152.3416 | 2562479.3069 | 1152151.5678 | 2562485.5764 | 1152149.094 | 2562489.6702 | 1152147.3389
131 | 2562474.6613 | 1152152.3416 | 2562452.4236 | 1152113.6223
132 | 2562452.1889 | 1152113.5953 | 2562452.4236 | 1152113.6223
133 | 2562434.8989 | 1152078.1301 | 2562426.5418 | 1152087.9318 | 2562428.0471 | 1152094.259 | 2562430.7999 | 1152100.1246
134 | 2562430.7999 | 1152100.1246 | 2562432.916 | 1152104.6338 | 2562436.5999 | 1152109.6133 | 2562443.2103 | 1152112.5624 | 2562452.1889 | 1152113.5953
135 | 2562494.385 | 1151460.104 | 2562493.9894 | 1151475.7629
136 | 2562494.385 | 1151460.104 | 2562494.6764 | 1151448.5637
137 | 2562539.7996 | 1151671.6685 | 2562540.1727 | 1151661.3387 | 2562541.8033 | 1151657.0041
138 | 2562539.7996 | 1151671.6685 | 2562520.5552 | 1151670.9659 | 2562520.1013 | 1151671.0785
139 | 2562502.7917 | 1151684.9839 | 2562511.36 | 1151673.2466 | 2562520.1013 | 1151671.0785
140 | 2562494.803 | 1151418.3871 | 2562495.2674 | 1151425.1654 | 2562494.6764 | 1151448.5637
141 | 2562780.613 | 1151543.1843 | 2563015.0595 | 1151522.5262
142 | 2562655.4948 | 1151473.2117 | 2562661.8891 | 1151478.4659
143 | 2562655.4948 | 1151473.2117 | 2562651.7379 | 1151470.1247 | 2562640.4577 | 1151460.5344 | 2562628.3714 | 1151450.5155
144 | 2562619.1463 | 1151442.8683 | 2562628.3714 | 1151450.5155
145 | 2562494.803 | 1151418.3871 | 2562487.94 | 1151410.7483 | 2562485.8695 | 1151406.3613
146 | 2562494.803 | 1151418.3871 | 2562497.1155 | 1151422.8515
147 | 2562497.1155 | 1151422.8515 | 2562619.1463 | 1151442.8683
148 | 2562227.9536 | 1151470.5296 | 2562229.0555 | 1151482.2175 | 2562230.9334 | 1151485.4852 | 2562235.1064 | 1151487.6045 | 2562239.396 | 1151488.7225
149 | 2562227.9536 | 1151470.5296 | 2561915.8862 | 1151468.775
150 | 2562956.9433 | 1151994.9416 | 2562974.8056 | 1151994.9473 | 2562999.8452 | 1151994.793 | 2563004.9282 | 1151996.7626

## bus_geodata
| x | y | coords
0 | 2562606.1776 | 1152095.4835
1 | 2562614.0743 | 1152093.3091
2 | 2562552.7685 | 1152098.5158
3 | 2562701.0576 | 1152081.9515
4 | 2562514.2072 | 1152093.8406
5 | 2562565.9901 | 1152059.2484
6 | 2562555.7234 | 1152120.7309
7 | 2562745.3041 | 1152086.6016
8 | 2562584.1934 | 1152024.6046
9 | 2562558.5227 | 1152130.3072
10 | 2562559.0218 | 1152148.3569
11 | 2562558.8745 | 1152150.3959
12 | 2562535.2957 | 1152127.5872
13 | 2562558.3952 | 1152153.8296
14 | 2562512.8437 | 1152136.9329
15 | 2562371.7157 | 1151450.9638
16 | 2562384.7194 | 1151475.4932
17 | 2562368.0015 | 1151480.2011
18 | 2562423.6961 | 1151485.8034
19 | 2562354.9267 | 1151485.4181
20 | 2562427.8863 | 1151487.7279
21 | 2562346.4463 | 1151489.0817
22 | 2562462.2174 | 1151498.498
23 | 2562324.6442 | 1151493.1118
24 | 2562483.5225 | 1151497.2643
25 | 2562453.6354 | 1151491.9693
26 | 2562785.1533 | 1151733.2989
27 | 2562784.4762 | 1151744.2515
28 | 2562786.4377 | 1151712.5226
29 | 2562767.8671 | 1151747.4198
30 | 2562783.9497 | 1151755.7046
31 | 2562787.2676 | 1151699.0975
32 | 2562736.6264 | 1151556.4198
33 | 2562719.6161 | 1151622.5584
34 | 2562747.0401 | 1151530.1969
35 | 2562754.0605 | 1151751.4803
36 | 2562782.9946 | 1151776.4801
37 | 2562787.9205 | 1151688.536
38 | 2562721.3664 | 1151761.0957
39 | 2562781.1638 | 1151797.9659
40 | 2562788.9286 | 1151672.2296
41 | 2562694.3085 | 1151769.8208
42 | 2562721.0833 | 1151738.6843
43 | 2562780.3088 | 1151801.8998
44 | 2562720.7255 | 1151710.3671
45 | 2562720.6819 | 1151706.9192
46 | 2562720.3662 | 1151681.9311
47 | 2562660.6957 | 1151767.787
48 | 2562720.2881 | 1151675.7431
49 | 2562656.533 | 1151747.4114
50 | 2562635.6684 | 1151775.2612
51 | 2562720.0113 | 1151653.839
52 | 2562656.0493 | 1151730.0536
53 | 2562887.7485 | 1152139.6606
54 | 2562868.9236 | 1152147.2449
55 | 2562882.2742 | 1152182.9138
56 | 2562851.8409 | 1152154.5987
57 | 2562933.2996 | 1152118.8853
58 | 2562946.0878 | 1152111.6503
59 | 2562903.1526 | 1152176.3311
60 | 2562868.6503 | 1152190.7257
61 | 2562839.2826 | 1152139.4888
62 | 2562943.9208 | 1152098.5397
63 | 2562973.1275 | 1152098.1928
64 | 2562924.3465 | 1152166.9887
65 | 2562841.2555 | 1152202.059
66 | 2562820.4531 | 1152129.569
67 | 2562940.9762 | 1152091.6413
68 | 2562996.6369 | 1152094.3189
69 | 2562942.2979 | 1152159.0756
70 | 2562813.3761 | 1152213.7735
71 | 2562794.5715 | 1152122.0861
72 | 2562816.1802 | 1152130.9182
73 | 2562772.4753 | 1152028.7633
74 | 2562793.8383 | 1152034.3703
75 | 2562511.3126 | 1152094.4672
76 | 2562794.7223 | 1152222.7341
77 | 2562743.8084 | 1152233.3175
78 | 2562743.3405 | 1152232.5218
79 | 2562809.5528 | 1152133.0108
80 | 2562790.6249 | 1152138.9874
81 | 2562769.9448 | 1152145.5172
82 | 2562755.7043 | 1152150.0138
83 | 2562776.5187 | 1152119.3336
84 | 2562741.3869 | 1152092.1246
85 | 2562854.9606 | 1152054.8553
86 | 2562874.1001 | 1152057.2437
87 | 2562845.1047 | 1152052.3907
88 | 2562877.0729 | 1152057.3758
89 | 2562841.7171 | 1152051.0867
90 | 2562898.9279 | 1152058.8949
91 | 2562828.1717 | 1152046.1047
92 | 2562902.437 | 1152059.282
93 | 2562823.6348 | 1152044.5779
94 | 2562917.6397 | 1152069.2821
95 | 2562631.6717 | 1151657.6071
96 | 2562613.765 | 1151658.1271
97 | 2562648.3633 | 1151669.3624
98 | 2562598.36 | 1151670.9884
99 | 2562653.4381 | 1151681.3618
100 | 2562591.1631 | 1151681.1644
101 | 2562655.0766 | 1151690.0783
102 | 2562581.6287 | 1151694.8258
103 | 2562595.6842 | 1151710.2315
104 | 2562655.787 | 1151720.6454
105 | 2562539.6314 | 1151734.5126
106 | 2562596.3307 | 1151725.955
107 | 2562805.7933 | 1152038.5315
108 | 2562803.698 | 1152067.1632
109 | 2562539.3345 | 1151707.7044
110 | 2562514.5317 | 1151733.8354
111 | 2562925.9367 | 1152080.402
112 | 2563020.7264 | 1152099.0892
113 | 2562758.173 | 1152072.1443
114 | 2563034.1877 | 1152102.4594
115 | 2562928.0093 | 1152035.9908
116 | 2562930.7501 | 1152034.1296
117 | 2562946.3491 | 1152028.4046
118 | 2562956.8082 | 1152027.1928
119 | 2562982.1004 | 1152024.7842
120 | 2562993.0872 | 1152024.7165
121 | 2562719.6757 | 1151627.272
122 | 2562776.3699 | 1152061.8411
123 | 2562796.0396 | 1152065.5534
124 | 2562489.6702 | 1152147.3389
125 | 2562474.6613 | 1152152.3416
126 | 2562452.4236 | 1152113.6223
127 | 2562430.7999 | 1152100.1246
128 | 2562434.8989 | 1152078.1301
129 | 2562452.1889 | 1152113.5953
130 | 2562493.9894 | 1151475.7629
131 | 2562494.385 | 1151460.104
132 | 2562539.7996 | 1151671.6685
133 | 2562541.8033 | 1151657.0041
134 | 2562520.1013 | 1151671.0785
135 | 2562502.7917 | 1151684.9839
136 | 2562494.6764 | 1151448.5637
137 | 2563015.0595 | 1151522.5262
138 | 2562780.613 | 1151543.1843
139 | 2562661.8891 | 1151478.4659
140 | 2562791.7619 | 1151641.0856
141 | 2562655.4948 | 1151473.2117
142 | 2562628.3714 | 1151450.5155
143 | 2562494.803 | 1151418.3871
144 | 2562485.8695 | 1151406.3613
145 | 2562497.1155 | 1151422.8515
146 | 2562619.1463 | 1151442.8683
147 | 2562239.396 | 1151488.7225
148 | 2562227.9536 | 1151470.5296
149 | 2561915.8862 | 1151468.775
150 | 2563004.9282 | 1151996.7626
151 | 2562956.9433 | 1151994.9416
152 | 2562721.3664 | 1151761.0957

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97199 | -0.53941 | 0.0007254 | 0.0001818
1 | 0.97211 | -0.53703 | 0.0014877 | 0.00037286
2 | 0.97124 | -0.55421 | 0 | 0
3 | 0.97352 | -0.50925 | 0.0016937 | 0.00042447
4 | 0.97116 | -0.55588 | 0.00076472 | 0.00019166
5 | 0.97116 | -0.55585 | 0.0013212 | 0.00033112
6 | 0.97102 | -0.5586 | 0 | 0
7 | 0.9743 | -0.49379 | 0 | 0
8 | 0.97113 | -0.55645 | 0.00081812 | 0.00020504
9 | 0.97099 | -0.55915 | 0 | 0
10 | 0.97094 | -0.56015 | 0.00069665 | 0.0001746
11 | 0.97094 | -0.56024 | 0.00068867 | 0.0001726
12 | 0.97087 | -0.56163 | 0.0011297 | 0.00028312
13 | 0.97093 | -0.56034 | 0.0015968 | 0.0004002
14 | 0.97072 | -0.56453 | 0.0018058 | 0.00045259
15 | 0.97367 | -0.50705 | 0.010657 | 0.0026709
16 | 0.97394 | -0.50161 | 0 | 0
17 | 0.97365 | -0.50745 | 0.0016463 | 0.00041261
18 | 0.97505 | -0.4799 | 0.0027162 | 0.00068074
19 | 0.97343 | -0.51175 | 0 | 0
20 | 0.97518 | -0.47723 | 0.0018711 | 0.00046895
21 | 0.97329 | -0.51458 | 0.0054654 | 0.0013698
22 | 0.97631 | -0.45499 | 0 | 0
23 | 0.97306 | -0.51916 | 0 | 0
24 | 0.97701 | -0.44139 | 0.0012132 | 0.00030407
25 | 0.9763 | -0.45525 | 0.0013184 | 0.00033043
26 | 0.99066 | -0.17705 | 0.0031677 | 0.00079389
27 | 0.99082 | -0.17384 | 0 | 0
28 | 0.9904 | -0.18198 | 0.0026364 | 0.00066074
29 | 0.99174 | -0.1564 | 0.0018051 | 0.00045241
30 | 0.99029 | -0.18398 | 0.0013909 | 0.00034858
31 | 0.99027 | -0.18453 | 0.0039419 | 0.00098792
32 | 0.9888 | -0.21281 | 0.0030802 | 0.00077198
33 | 0.99045 | -0.18117 | 0.0026447 | 0.00066282
34 | 0.98816 | -0.22513 | 0 | 0
35 | 0.99252 | -0.14138 | 0.0009796 | 0.00024551
36 | 0.98934 | -0.20215 | 0.0026147 | 0.00065532
37 | 0.99021 | -0.1858 | 0.0025917 | 0.00064953
38 | 0.99441 | -0.10561 | 0 | 0
39 | 0.98838 | -0.22052 | 0.0010721 | 0.00026869
40 | 0.99014 | -0.187 | 0.0015429 | 0.0003867
41 | 0.99685 | -0.059344 | 0.0020838 | 0.00052225
42 | 0.99372 | -0.11871 | 0.0011911 | 0.00029852
43 | 0.9882 | -0.22392 | 0.0011442 | 0.00028676
44 | 0.99287 | -0.13498 | 0.0013389 | 0.00033557
45 | 0.99276 | -0.13692 | 0.0012404 | 0.00031088
46 | 0.99204 | -0.15074 | 0.0022607 | 0.00056659
47 | 1 | 0 | -0.22603 | -0.057721
48 | 0.99187 | -0.15404 | 0.0010198 | 0.00025559
49 | 0.99939 | -0.011631 | 0.00054994 | 0.00013783
50 | 0.99996 | -0.00070528 | 0.0015235 | 0.00038181
51 | 0.99127 | -0.16553 | 0.0025663 | 0.00064317
52 | 0.9989 | -0.021113 | 0.0012183 | 0.00030533
53 | 0.97153 | -0.54852 | 0.00056543 | 0.00014171
54 | 0.97154 | -0.54831 | 0 | 0
55 | 0.97112 | -0.55658 | 0 | 0
56 | 0.97175 | -0.54414 | 0 | 0
57 | 0.97307 | -0.51811 | 0.0012932 | 0.0003241
58 | 0.97309 | -0.51776 | 0 | 0
59 | 0.97105 | -0.55807 | 0.0015692 | 0.00039327
60 | 0.971 | -0.55901 | 0.00080681 | 0.00020221
61 | 0.97198 | -0.5396 | 0.00066539 | 0.00016676
62 | 0.9732 | -0.51563 | 0.0011483 | 0.00028779
63 | 0.97288 | -0.52189 | 0.0039096 | 0.00097984
64 | 0.971 | -0.55896 | 0.0010748 | 0.00026937
65 | 0.9708 | -0.56294 | 0.00050987 | 0.00012779
66 | 0.97224 | -0.53453 | 0 | 0
67 | 0.97327 | -0.51426 | 0.0014548 | 0.0003646
68 | 0.9728 | -0.52342 | 0.0015384 | 0.00038556
69 | 0.97098 | -0.55932 | 0.0009886 | 0.00024777
70 | 0.97061 | -0.56667 | 0.00096712 | 0.00024238
71 | 0.97276 | -0.52409 | 0.0012608 | 0.00031598
72 | 0.9722 | -0.53521 | 0.00057233 | 0.00014344
73 | 0.97832 | -0.41496 | 0.0014166 | 0.00035504
74 | 0.97737 | -0.43348 | 0.00070522 | 0.00017674
75 | 0.97115 | -0.55596 | 0.0014945 | 0.00037455
76 | 0.9705 | -0.56885 | 0.0016555 | 0.0004149
77 | 0.97027 | -0.57336 | 0.0013822 | 0.00034641
78 | 0.97027 | -0.5734 | 0.0026485 | 0.00066377
79 | 0.97215 | -0.53619 | 0.00086736 | 0.00021738
80 | 0.97203 | -0.53866 | 0.0022919 | 0.0005744
81 | 0.97194 | -0.54044 | 0.0017627 | 0.00044177
82 | 0.9719 | -0.54118 | 0.0026888 | 0.00067387
83 | 0.97315 | -0.51657 | 0.0017348 | 0.00043477
84 | 0.97414 | -0.49694 | 0.0012649 | 0.00031702
85 | 0.97565 | -0.46722 | 0.0016489 | 0.00041324
86 | 0.97504 | -0.47933 | 0.00098644 | 0.00024723
87 | 0.976 | -0.4605 | 0.00098418 | 0.00024666
88 | 0.97495 | -0.48114 | 0.00080133 | 0.00020083
89 | 0.97612 | -0.45805 | 0.0024455 | 0.0006129
90 | 0.97428 | -0.4942 | 0.0007517 | 0.00018839
91 | 0.97639 | -0.45285 | 0.00099806 | 0.00025014
92 | 0.97418 | -0.49626 | 0.0022545 | 0.00056503
93 | 0.97648 | -0.45109 | 0.00074474 | 0.00018665
94 | 0.97367 | -0.50639 | 0 | 0
95 | 0.99687 | -0.060193 | 0.0030821 | 0.00077244
96 | 0.99654 | -0.066557 | 0.0016082 | 0.00040305
97 | 0.99731 | -0.051621 | 0.0019242 | 0.00048226
98 | 0.99619 | -0.073155 | 0.0019229 | 0.00048193
99 | 0.99761 | -0.045822 | 0.0021378 | 0.00053579
100 | 0.99601 | -0.076758 | 0 | 0
101 | 0.99783 | -0.041597 | 0.0019226 | 0.00048184
102 | 0.99581 | -0.080669 | 0.0017347 | 0.00043475
103 | 0.99592 | -0.078388 | 0.00067147 | 0.00016829
104 | 0.99864 | -0.026057 | 0.0010008 | 0.00025083
105 | 0.99517 | -0.092892 | 0 | 0
106 | 0.99589 | -0.079062 | 0.0024386 | 0.00061117
107 | 0.97684 | -0.44402 | 0.0010021 | 0.00025115
108 | 0.97618 | -0.45691 | 0.0010933 | 0.00027399
109 | 0.99498 | -0.09659 | 0.0015551 | 0.00038976
110 | 0.99507 | -0.094829 | 0.0037797 | 0.00094728
111 | 0.97347 | -0.51027 | 0.001985 | 0.00049749
112 | 0.97276 | -0.5243 | 0.00070564 | 0.00017685
113 | 0.9751 | -0.47807 | 0.0010081 | 0.00025265
114 | 0.97274 | -0.52461 | 0.001232 | 0.00030876
115 | 0.97313 | -0.51696 | 0.0011022 | 0.00027624
116 | 0.97308 | -0.51788 | 0.0016318 | 0.00040896
117 | 0.97287 | -0.52209 | 0.0010878 | 0.00027264
118 | 0.97275 | -0.52448 | 0.001883 | 0.00047193
119 | 0.9725 | -0.52939 | 0.0025687 | 0.00064378
120 | 0.97242 | -0.53099 | 0.0030008 | 0.00075208
121 | 0.99057 | -0.17888 | 0.0019113 | 0.00047903
122 | 0.97556 | -0.46897 | 0.0018271 | 0.00045792
123 | 0.976 | -0.46035 | 0.0010301 | 0.00025816
124 | 0.97061 | -0.56672 | 0.001449 | 0.00036316
125 | 0.97056 | -0.56766 | 0 | 0
126 | 0.97043 | -0.57031 | 0.00072162 | 0.00018086
127 | 0.97039 | -0.57112 | 0.00067388 | 0.00016889
128 | 0.97037 | -0.57155 | 0.00089367 | 0.00022398
129 | 0.97043 | -0.57032 | 0.00091126 | 0.00022838
130 | 0.97783 | -0.42523 | 0.0010801 | 0.0002707
131 | 0.97837 | -0.41464 | 0.00084351 | 0.0002114
132 | 0.99478 | -0.10057 | 0 | 0
133 | 0.99475 | -0.10105 | 0.0018091 | 0.00045341
134 | 0.9947 | -0.10212 | 0.0015394 | 0.0003858
135 | 0.99463 | -0.10333 | 0.0029194 | 0.00073167
136 | 0.97878 | -0.40666 | 0.0010984 | 0.00027528
137 | 0.98785 | -0.23109 | 0.0012246 | 0.00030692
138 | 0.98812 | -0.22592 | 0 | 0
139 | 0.98595 | -0.26768 | 0.0030979 | 0.0007764
140 | 0.99007 | -0.18845 | 0.0025994 | 0.00065148
141 | 0.98577 | -0.27099 | 0.00072554 | 0.00018184
142 | 0.98505 | -0.28493 | 0.0015471 | 0.00038774
143 | 0.97988 | -0.38522 | 0 | 0
144 | 0.97987 | -0.38552 | 0.0010856 | 0.00027208
145 | 0.98007 | -0.38156 | 0.0010762 | 0.00026972
146 | 0.98482 | -0.28949 | 0.0011322 | 0.00028375
147 | 0.97217 | -0.53669 | 0.0019685 | 0.00049334
148 | 0.97196 | -0.54086 | 0.0031245 | 0.00078307
149 | 0.9702 | -0.57572 | 0.0060395 | 0.0015136
150 | 0.97222 | -0.53489 | 0.0031606 | 0.00079211
151 | 0.97214 | -0.53645 | 0.0017478 | 0.00043805
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015708 | -0.0039379 | 0.015709 | 0.0039389 | 1.7838e-06 | 1.0397e-06 | 0.024047 | 0.024047 | 0.024047 | 0.97199 | -0.53941 | 0.97211 | -0.53703 | 6.6063
1 | 0.014982 | 0.0037561 | -0.014972 | -0.00375 | 1.0554e-05 | 6.0918e-06 | 0.022937 | 0.022937 | 0.022937 | 0.97199 | -0.53941 | 0.97124 | -0.55421 | 6.3013
2 | -0.017197 | -0.0043118 | 0.01722 | 0.0043253 | 2.2795e-05 | 1.35e-05 | 0.026324 | 0.026324 | 0.026324 | 0.97211 | -0.53703 | 0.97352 | -0.50925 | 7.2319
3 | 0.0022594 | 0.00056579 | -0.0022592 | -0.00056617 | 1.8041e-07 | -3.8141e-07 | 0.0034614 | 0.0034615 | 0.0034615 | 0.97124 | -0.55421 | 0.97116 | -0.55588 | 0.95097
4 | 0.0021395 | 0.00053528 | -0.0021393 | -0.00053569 | 1.6787e-07 | -4.082e-07 | 0.0032775 | 0.0032777 | 0.0032777 | 0.97124 | -0.55421 | 0.97116 | -0.55585 | 0.90047
5 | 0.010573 | 0.0026489 | -0.01057 | -0.0026478 | 2.2129e-06 | 1.138e-06 | 0.016198 | 0.016198 | 0.016198 | 0.97124 | -0.55421 | 0.97102 | -0.5586 | 4.45
6 | -0.018913 | -0.0047498 | 0.018927 | 0.0047582 | 1.396e-05 | 8.3803e-06 | 0.028913 | 0.028912 | 0.028913 | 0.97352 | -0.50925 | 0.9743 | -0.49379 | 7.943
7 | 0.0014945 | 0.00037452 | -0.0014945 | -0.00037455 | 5.8233e-09 | -3.2918e-08 | 0.0022898 | 0.0022899 | 0.0022899 | 0.97116 | -0.55588 | 0.97115 | -0.55596 | 0.62908
8 | 0.00081815 | 0.00020457 | -0.00081812 | -0.00020504 | 2.313e-08 | -4.7091e-07 | 0.0012534 | 0.0012536 | 0.0012536 | 0.97116 | -0.55585 | 0.97113 | -0.55645 | 0.34439
9 | 0.0075881 | 0.0019007 | -0.007587 | -0.0019002 | 1.0934e-06 | 4.3307e-07 | 0.011628 | 0.011628 | 0.011628 | 0.97102 | -0.5586 | 0.97087 | -0.56163 | 3.1945
10 | 0.0029824 | 0.00074713 | -0.0029823 | -0.00074721 | 7.8145e-08 | -7.3398e-08 | 0.0045702 | 0.0045702 | 0.0045702 | 0.97102 | -0.5586 | 0.97099 | -0.55915 | 1.2556
11 | 0.025342 | 0.0063701 | -0.025338 | -0.0063678 | 3.8049e-06 | 2.3508e-06 | 0.03871 | 0.03871 | 0.03871 | 0.9743 | -0.49379 | 0.97414 | -0.49694 | 10.6346
12 | -0.044269 | -0.011128 | 0.044302 | 0.011149 | 3.3269e-05 | 2.105e-05 | 0.067622 | 0.067622 | 0.067622 | 0.9743 | -0.49379 | 0.9751 | -0.47807 | 18.5776
13 | 0.0029823 | 0.00074721 | -0.0029822 | -0.00074734 | 1.4188e-07 | -1.3324e-07 | 0.0045702 | 0.0045703 | 0.0045703 | 0.97099 | -0.55915 | 0.97094 | -0.56015 | 1.2556
14 | 0.0022855 | 0.00057274 | -0.0022855 | -0.00057276 | 9.4055e-09 | -1.9265e-08 | 0.0035026 | 0.0035027 | 0.0035027 | 0.97094 | -0.56015 | 0.97094 | -0.56024 | 0.96227
15 | 0.0015968 | 0.00040016 | -0.0015968 | -0.0004002 | 7.8077e-09 | -3.7999e-08 | 0.0024472 | 0.0024472 | 0.0024472 | 0.97094 | -0.56024 | 0.97093 | -0.56034 | 0.67232
16 | 0.0064573 | 0.0016171 | -0.0064564 | -0.0016168 | 8.9346e-07 | 2.7104e-07 | 0.0098965 | 0.0098966 | 0.0098966 | 0.97087 | -0.56163 | 0.97072 | -0.56453 | 2.7188
17 | 0.0046506 | 0.0011643 | -0.0046501 | -0.0011643 | 4.8413e-07 | -4.1982e-09 | 0.0071284 | 0.0071285 | 0.0071285 | 0.97072 | -0.56453 | 0.97061 | -0.56672 | 1.9584
18 | -0.010657 | -0.0026709 | 0.01066 | 0.0026723 | 2.7616e-06 | 1.422e-06 | 0.016287 | 0.016287 | 0.016287 | 0.97367 | -0.50705 | 0.97394 | -0.50161 | 4.4744
19 | 0.018279 | 0.0045884 | -0.018273 | -0.0045854 | 5.0863e-06 | 3.0389e-06 | 0.027929 | 0.027929 | 0.027929 | 0.97394 | -0.50161 | 0.97365 | -0.50745 | 7.6728
20 | -0.028938 | -0.0072607 | 0.028968 | 0.0072794 | 2.9986e-05 | 1.8681e-05 | 0.044216 | 0.044215 | 0.044216 | 0.97394 | -0.50161 | 0.97505 | -0.4799 | 12.1471
21 | 0.016627 | 0.0041727 | -0.016624 | -0.0041707 | 3.4128e-06 | 2.009e-06 | 0.025413 | 0.025413 | 0.025413 | 0.97365 | -0.50745 | 0.97343 | -0.51175 | 6.9816
22 | -0.031684 | -0.0079601 | 0.031689 | 0.0079627 | 4.044e-06 | 2.5306e-06 | 0.048361 | 0.048361 | 0.048361 | 0.97505 | -0.4799 | 0.97518 | -0.47723 | 13.2859
23 | 0.016624 | 0.0041707 | -0.016621 | -0.0041694 | 2.2373e-06 | 1.317e-06 | 0.025413 | 0.025413 | 0.025413 | 0.97343 | -0.51175 | 0.97329 | -0.51458 | 6.9816
24 | -0.03356 | -0.0084316 | 0.033595 | 0.008454 | 3.5658e-05 | 2.2368e-05 | 0.051216 | 0.051215 | 0.051216 | 0.97518 | -0.47723 | 0.97631 | -0.45499 | 14.0702
25 | 0.011156 | 0.0027997 | -0.011154 | -0.0027984 | 2.4403e-06 | 1.2839e-06 | 0.017057 | 0.017057 | 0.017057 | 0.97329 | -0.51458 | 0.97306 | -0.51916 | 4.6861
26 | -0.034914 | -0.0087843 | 0.034936 | 0.0087986 | 2.2711e-05 | 1.4267e-05 | 0.053225 | 0.053225 | 0.053225 | 0.97631 | -0.45499 | 0.97701 | -0.44139 | 14.6222
27 | 0.0013184 | 0.0003303 | -0.0013184 | -0.00033043 | 1.6327e-08 | -1.2439e-07 | 0.0020094 | 0.0020095 | 0.0020095 | 0.97631 | -0.45499 | 0.9763 | -0.45525 | 0.55205
28 | 0.011154 | 0.0027984 | -0.011144 | -0.0027935 | 9.3138e-06 | 4.9014e-06 | 0.017057 | 0.017058 | 0.017058 | 0.97306 | -0.51916 | 0.97217 | -0.53669 | 4.6862
29 | -0.03615 | -0.0091026 | 0.036178 | 0.0091202 | 2.795e-05 | 1.758e-05 | 0.055073 | 0.055072 | 0.055073 | 0.97701 | -0.44139 | 0.97783 | -0.42523 | 15.1298
30 | -0.016485 | -0.0041324 | 0.016488 | 0.0041339 | 2.5231e-06 | 1.4735e-06 | 0.024762 | 0.024762 | 0.024762 | 0.99066 | -0.17705 | 0.99082 | -0.17384 | 6.8027
31 | 0.013318 | 0.0033385 | -0.013314 | -0.0033368 | 3.1236e-06 | 1.7312e-06 | 0.020004 | 0.020004 | 0.020004 | 0.99066 | -0.17705 | 0.9904 | -0.18198 | 5.4956
32 | -0.1176 | -0.030065 | 0.1177 | 0.030128 | 9.9324e-05 | 6.313e-05 | 0.17682 | 0.17682 | 0.17682 | 0.99082 | -0.17384 | 0.99174 | -0.1564 | 24.2888
33 | 0.10111 | 0.025931 | -0.10106 | -0.0259 | 4.9707e-05 | 3.1517e-05 | 0.15206 | 0.15206 | 0.15206 | 0.99082 | -0.17384 | 0.99029 | -0.18398 | 20.8875
34 | 0.010678 | 0.0026761 | -0.010677 | -0.0026754 | 1.2982e-06 | 6.5779e-07 | 0.016043 | 0.016043 | 0.016043 | 0.9904 | -0.18198 | 0.99027 | -0.18453 | 4.4074
35 | -0.1195 | -0.030581 | 0.11959 | 0.030636 | 8.6972e-05 | 5.529e-05 | 0.17953 | 0.17953 | 0.17953 | 0.99174 | -0.1564 | 0.99252 | -0.14138 | 24.6608
36 | 0.099671 | 0.025551 | -0.099583 | -0.025496 | 8.7705e-05 | 5.5597e-05 | 0.14997 | 0.14997 | 0.14997 | 0.99029 | -0.18398 | 0.98934 | -0.20215 | 20.6004
37 | 0.0067349 | 0.0016875 | -0.0067344 | -0.0016874 | 4.0638e-07 | 1.2396e-07 | 0.01012 | 0.01012 | 0.01012 | 0.99027 | -0.18453 | 0.99021 | -0.1858 | 2.7802
38 | -0.052609 | -0.013399 | 0.052689 | 0.013448 | 8.0411e-05 | 4.9708e-05 | 0.079246 | 0.079245 | 0.079246 | 0.9888 | -0.21281 | 0.99045 | -0.18117 | 10.8854
39 | 0.049528 | 0.012627 | -0.049499 | -0.012609 | 2.945e-05 | 1.8125e-05 | 0.07461 | 0.074611 | 0.074611 | 0.9888 | -0.21281 | 0.98816 | -0.22513 | 10.2487
40 | -0.055334 | -0.014111 | 0.05534 | 0.014115 | 6.1211e-06 | 3.7962e-06 | 0.083218 | 0.083218 | 0.083218 | 0.99045 | -0.18117 | 0.99057 | -0.17888 | 11.4311
41 | 0.048274 | 0.012305 | -0.048175 | -0.012244 | 9.892e-05 | 6.0762e-05 | 0.072767 | 0.072768 | 0.072768 | 0.98816 | -0.22513 | 0.98595 | -0.26768 | 9.9956
42 | 0.001225 | 0.00030367 | -0.0012249 | -0.0003041 | 4.5763e-08 | -4.3069e-07 | 0.0018434 | 0.0018436 | 0.0018436 | 0.98816 | -0.22513 | 0.98812 | -0.22592 | 0.50648
43 | -0.12057 | -0.030882 | 0.12078 | 0.031015 | 0.00020933 | 0.00013309 | 0.181 | 0.181 | 0.181 | 0.99252 | -0.14138 | 0.99441 | -0.10561 | 24.8625
44 | 0.096969 | 0.02484 | -0.096882 | -0.024786 | 8.6241e-05 | 5.4641e-05 | 0.14604 | 0.14604 | 0.14604 | 0.98934 | -0.20215 | 0.98838 | -0.22052 | 20.0602
45 | 0.0041428 | 0.0010378 | -0.0041425 | -0.0010379 | 2.3744e-07 | -5.8186e-08 | 0.0062253 | 0.0062254 | 0.0062254 | 0.99021 | -0.1858 | 0.99014 | -0.187 | 1.7103
46 | -0.18787 | -0.048158 | 0.18829 | 0.048427 | 0.00042244 | 0.00026962 | 0.28151 | 0.28151 | 0.28151 | 0.99441 | -0.10561 | 0.99685 | -0.059344 | 38.6689
47 | 0.067091 | 0.017143 | -0.067048 | -0.017117 | 4.2455e-05 | 2.659e-05 | 0.10051 | 0.10051 | 0.10051 | 0.99441 | -0.10561 | 0.99372 | -0.11871 | 13.8065
48 | 0.09581 | 0.024517 | -0.095794 | -0.024507 | 1.5744e-05 | 9.9732e-06 | 0.14442 | 0.14442 | 0.14442 | 0.98838 | -0.22052 | 0.9882 | -0.22392 | 19.8385
49 | 0.0025996 | 0.00065119 | -0.0025994 | -0.00065148 | 1.7903e-07 | -2.8772e-07 | 0.0039066 | 0.0039068 | 0.0039068 | 0.99014 | -0.187 | 0.99007 | -0.18845 | 1.0733
50 | -0.19038 | -0.04895 | 0.19093 | 0.049301 | 0.00055078 | 0.00035155 | 0.28462 | 0.28462 | 0.28462 | 0.99685 | -0.059344 | 1 | 0 | 39.0961
51 | 0.065857 | 0.016818 | -0.065806 | -0.016786 | 5.1756e-05 | 3.2391e-05 | 0.098728 | 0.098728 | 0.098728 | 0.99372 | -0.11871 | 0.99287 | -0.13498 | 13.5615
52 | 0.09465 | 0.02422 | -0.093783 | -0.023671 | 0.00086674 | 0.00054896 | 0.1427 | 0.1427 | 0.1427 | 0.9882 | -0.22392 | 0.97832 | -0.41496 | 19.6022
53 | 0.064467 | 0.01645 | -0.064461 | -0.016446 | 6.0483e-06 | 3.7817e-06 | 0.096721 | 0.096721 | 0.096721 | 0.99287 | -0.13498 | 0.99276 | -0.13692 | 13.2859
54 | 0.06322 | 0.016135 | -0.063178 | -0.016109 | 4.2165e-05 | 2.634e-05 | 0.094862 | 0.094862 | 0.094862 | 0.99276 | -0.13692 | 0.99204 | -0.15074 | 13.0305
55 | 0.060917 | 0.015543 | -0.060908 | -0.015536 | 9.7086e-06 | 6.0537e-06 | 0.091471 | 0.091471 | 0.091471 | 0.99204 | -0.15074 | 0.99187 | -0.15404 | 12.5647
56 | 0.031925 | 0.0080381 | -0.031907 | -0.0080271 | 1.7741e-05 | 1.108e-05 | 0.047517 | 0.047517 | 0.047517 | 1 | 0 | 0.99939 | -0.011631 | 13.0542
57 | 0.0015235 | 0.0003815 | -0.0015235 | -0.00038181 | 5.1171e-08 | -3.1559e-07 | 0.0022669 | 0.002267 | 0.002267 | 1 | 0 | 0.99996 | -0.00070528 | 0.6228
58 | 0.059888 | 0.015281 | -0.059854 | -0.01526 | 3.3226e-05 | 2.07e-05 | 0.089941 | 0.089942 | 0.089942 | 0.99187 | -0.15404 | 0.99127 | -0.16553 | 12.3546
59 | 0.031357 | 0.0078892 | -0.031343 | -0.0078804 | 1.42e-05 | 8.8609e-06 | 0.046699 | 0.046699 | 0.046699 | 0.99939 | -0.011631 | 0.9989 | -0.021113 | 12.8293
60 | 0.057288 | 0.014617 | -0.057251 | -0.014594 | 3.6921e-05 | 2.2945e-05 | 0.086089 | 0.08609 | 0.08609 | 0.99127 | -0.16553 | 0.99057 | -0.17888 | 11.8255
61 | 0.030124 | 0.007575 | -0.030117 | -0.0075706 | 7.1102e-06 | 4.4274e-06 | 0.044884 | 0.044884 | 0.044884 | 0.9989 | -0.021113 | 0.99864 | -0.026057 | 12.3307
62 | -0.00056543 | -0.00014171 | 0.00056544 | 0.00014146 | 5.7075e-09 | -2.4766e-07 | 0.00086603 | 0.00086594 | 0.00086603 | 0.97153 | -0.54852 | 0.97154 | -0.54831 | 0.23792
63 | 0.011612 | 0.0029109 | -0.011608 | -0.0029085 | 4.571e-06 | 2.4485e-06 | 0.017786 | 0.017786 | 0.017786 | 0.97154 | -0.54831 | 0.97112 | -0.55658 | 4.8862
64 | -0.012178 | -0.0030524 | 0.01218 | 0.0030537 | 2.4204e-06 | 1.3192e-06 | 0.018652 | 0.018652 | 0.018652 | 0.97154 | -0.54831 | 0.97175 | -0.54414 | 5.1241
65 | 0.0036329 | 0.00090983 | -0.0036327 | -0.00090994 | 2.5892e-07 | -1.0998e-07 | 0.0055663 | 0.0055664 | 0.0055664 | 0.97112 | -0.55658 | 0.97105 | -0.55807 | 1.5292
66 | 0.0079749 | 0.0019986 | -0.0079739 | -0.0019983 | 9.2564e-07 | 3.8791e-07 | 0.01222 | 0.01222 | 0.01222 | 0.97112 | -0.55658 | 0.971 | -0.55901 | 3.357
67 | -0.01218 | -0.0030537 | 0.012183 | 0.0030551 | 2.6376e-06 | 1.4375e-06 | 0.018652 | 0.018652 | 0.018652 | 0.97175 | -0.54414 | 0.97198 | -0.5396 | 5.1241
68 | -0.0012932 | -0.0003241 | 0.0012932 | 0.00032393 | 2.1545e-08 | -1.6873e-07 | 0.0019775 | 0.0019774 | 0.0019775 | 0.97307 | -0.51811 | 0.97309 | -0.51776 | 0.54327
69 | -0.0086806 | -0.0021749 | 0.0086815 | 0.0021753 | 8.8175e-07 | 3.9852e-07 | 0.013274 | 0.013274 | 0.013274 | 0.97309 | -0.51776 | 0.9732 | -0.51563 | 3.6467
70 | 0.0073874 | 0.001851 | -0.007386 | -0.0018505 | 1.4533e-06 | 5.5294e-07 | 0.011296 | 0.011297 | 0.011297 | 0.97309 | -0.51776 | 0.97288 | -0.52189 | 3.1035
71 | 0.0020635 | 0.00051667 | -0.0020634 | -0.0005169 | 8.6838e-08 | -2.3093e-07 | 0.0031619 | 0.003162 | 0.003162 | 0.97105 | -0.55807 | 0.971 | -0.55896 | 0.86868
72 | 0.0071671 | 0.001796 | -0.0071658 | -0.0017956 | 1.3411e-06 | 4.9169e-07 | 0.010983 | 0.010983 | 0.010983 | 0.971 | -0.55901 | 0.9708 | -0.56294 | 3.0174
73 | -0.012848 | -0.0032219 | 0.012851 | 0.0032236 | 3.1017e-06 | 1.72e-06 | 0.01967 | 0.01967 | 0.01967 | 0.97198 | -0.5396 | 0.97224 | -0.53453 | 5.4039
74 | -0.0098298 | -0.0024631 | 0.0098304 | 0.0024634 | 6.4037e-07 | 3.1589e-07 | 0.01503 | 0.01503 | 0.01503 | 0.9732 | -0.51563 | 0.97327 | -0.51426 | 4.129
75 | 0.0034764 | 0.00087062 | -0.0034761 | -0.00087076 | 2.5314e-07 | -1.3448e-07 | 0.0053169 | 0.005317 | 0.005317 | 0.97288 | -0.52189 | 0.9728 | -0.52342 | 1.4607
76 | 0.00098862 | 0.00024754 | -0.0009886 | -0.00024777 | 1.6885e-08 | -2.3185e-07 | 0.0015149 | 0.001515 | 0.001515 | 0.971 | -0.55896 | 0.97098 | -0.55932 | 0.41621
77 | 0.0066559 | 0.0016678 | -0.0066547 | -0.0016674 | 1.1804e-06 | 3.8157e-07 | 0.010202 | 0.010202 | 0.010202 | 0.9708 | -0.56294 | 0.97061 | -0.56667 | 2.8027
78 | -0.021036 | -0.0052748 | 0.021047 | 0.0052812 | 1.0478e-05 | 6.3714e-06 | 0.032197 | 0.032197 | 0.032197 | 0.97224 | -0.53453 | 0.97276 | -0.52409 | 8.8454
79 | 0.0081849 | 0.0020512 | -0.0081847 | -0.0020511 | 2.6369e-07 | 1.1319e-07 | 0.012527 | 0.012527 | 0.012527 | 0.97224 | -0.53453 | 0.9722 | -0.53521 | 3.4415
80 | -0.011285 | -0.002828 | 0.011287 | 0.0028292 | 2.143e-06 | 1.1329e-06 | 0.017254 | 0.017254 | 0.017254 | 0.97327 | -0.51426 | 0.97347 | -0.51027 | 4.74
81 | 0.0019377 | 0.0004852 | -0.0019376 | -0.00048546 | 8.1214e-08 | -2.5409e-07 | 0.0029638 | 0.0029639 | 0.0029639 | 0.9728 | -0.52342 | 0.97276 | -0.5243 | 0.81427
82 | 0.0056876 | 0.001425 | -0.005687 | -0.0014249 | 5.9033e-07 | 1.2193e-07 | 0.0087193 | 0.0087194 | 0.0087194 | 0.97061 | -0.56667 | 0.9705 | -0.56885 | 2.3954
83 | -0.022308 | -0.0055972 | 0.022316 | 0.0056021 | 8.0013e-06 | 4.8933e-06 | 0.034126 | 0.034126 | 0.034126 | 0.97276 | -0.52409 | 0.97315 | -0.51657 | 9.3752
84 | 0.0076123 | 0.0019077 | -0.007612 | -0.0019075 | 3.5379e-07 | 1.4025e-07 | 0.011651 | 0.011651 | 0.011651 | 0.9722 | -0.53521 | 0.97215 | -0.53619 | 3.2009
85 | 0.092367 | 0.023316 | -0.092285 | -0.023264 | 8.1872e-05 | 5.1844e-05 | 0.14055 | 0.14055 | 0.14055 | 0.97832 | -0.41496 | 0.97737 | -0.43348 | 19.3062
86 | 0.09158 | 0.023088 | -0.091534 | -0.023058 | 4.6172e-05 | 2.9233e-05 | 0.13948 | 0.13948 | 0.13948 | 0.97737 | -0.43348 | 0.97684 | -0.44402 | 19.1588
87 | 0.0040315 | 0.00101 | -0.0040307 | -0.0010102 | 8.6633e-07 | -1.925e-07 | 0.0061812 | 0.0061814 | 0.0061814 | 0.9705 | -0.56885 | 0.97027 | -0.57336 | 1.6982
88 | 0.0026485 | 0.00066376 | -0.0026485 | -0.00066377 | 5.711e-09 | -7.7466e-09 | 0.0040617 | 0.0040617 | 0.0040617 | 0.97027 | -0.57336 | 0.97027 | -0.5734 | 1.1159
89 | 0.0067446 | 0.0016902 | -0.0067438 | -0.0016899 | 7.9329e-07 | 2.6163e-07 | 0.010324 | 0.010324 | 0.010324 | 0.97215 | -0.53619 | 0.97203 | -0.53866 | 2.8362
90 | 0.0044519 | 0.0011155 | -0.0044516 | -0.0011155 | 3.7772e-07 | -2.705e-08 | 0.0068151 | 0.0068152 | 0.0068152 | 0.97203 | -0.53866 | 0.97194 | -0.54044 | 1.8723
91 | 0.0026889 | 0.00067375 | -0.0026888 | -0.00067387 | 9.49e-08 | -1.2433e-07 | 0.0041165 | 0.0041166 | 0.0041166 | 0.97194 | -0.54044 | 0.9719 | -0.54118 | 1.1309
92 | -0.02405 | -0.0060369 | 0.024073 | 0.0060507 | 2.2539e-05 | 1.3873e-05 | 0.036778 | 0.036778 | 0.036778 | 0.97315 | -0.51657 | 0.97414 | -0.49694 | 10.1039
93 | 0.034329 | 0.0086316 | -0.034309 | -0.0086191 | 1.9846e-05 | 1.246e-05 | 0.052367 | 0.052367 | 0.052367 | 0.97565 | -0.46722 | 0.97504 | -0.47933 | 14.3865
94 | -0.035978 | -0.0090448 | 0.035989 | 0.0090521 | 1.1551e-05 | 7.2646e-06 | 0.054881 | 0.054881 | 0.054881 | 0.97565 | -0.46722 | 0.976 | -0.4605 | 15.0773
95 | 0.033323 | 0.0083719 | -0.03332 | -0.0083701 | 2.8867e-06 | 1.8104e-06 | 0.050861 | 0.050861 | 0.050861 | 0.97504 | -0.47933 | 0.97495 | -0.48114 | 13.9729
96 | -0.036974 | -0.0092988 | 0.036978 | 0.0093015 | 4.3272e-06 | 2.7241e-06 | 0.056382 | 0.056382 | 0.056382 | 0.976 | -0.4605 | 0.97612 | -0.45805 | 15.4895
97 | 0.032518 | 0.0081693 | -0.032498 | -0.0081566 | 2.0253e-05 | 1.2689e-05 | 0.049638 | 0.049638 | 0.049638 | 0.97495 | -0.48114 | 0.97428 | -0.4942 | 13.6369
98 | -0.039423 | -0.0099144 | 0.039433 | 0.0099203 | 9.7796e-06 | 5.898e-06 | 0.06011 | 0.06011 | 0.06011 | 0.97612 | -0.45805 | 0.97639 | -0.45285 | 8.2568
99 | 0.031746 | 0.0079682 | -0.031743 | -0.0079662 | 3.1129e-06 | 1.9483e-06 | 0.04849 | 0.04849 | 0.04849 | 0.97428 | -0.4942 | 0.97418 | -0.49626 | 13.3215
100 | -0.040431 | -0.01017 | 0.040435 | 0.010172 | 3.4092e-06 | 2.0621e-06 | 0.061631 | 0.061631 | 0.061631 | 0.97639 | -0.45285 | 0.97648 | -0.45109 | 8.4658
101 | 0.029489 | 0.0074012 | -0.029475 | -0.0073923 | 1.4238e-05 | 8.8797e-06 | 0.045047 | 0.045047 | 0.045047 | 0.97418 | -0.49626 | 0.97367 | -0.50639 | 12.3755
102 | -0.041179 | -0.010359 | 0.041193 | 0.010368 | 1.3915e-05 | 8.4342e-06 | 0.062766 | 0.062765 | 0.062766 | 0.97648 | -0.45109 | 0.97684 | -0.44402 | 8.6216
103 | 0.013275 | 0.003328 | -0.013272 | -0.0033267 | 2.4558e-06 | 1.3738e-06 | 0.020288 | 0.020288 | 0.020288 | 0.97367 | -0.50639 | 0.97347 | -0.51027 | 5.5736
104 | 0.0162 | 0.0040643 | -0.016192 | -0.0040595 | 8.1614e-06 | 4.782e-06 | 0.024759 | 0.024759 | 0.024759 | 0.97367 | -0.50639 | 0.97313 | -0.51696 | 6.802
105 | 0.020006 | 0.0050206 | -0.02 | -0.005017 | 6.0695e-06 | 3.648e-06 | 0.029866 | 0.029866 | 0.029866 | 0.99687 | -0.060193 | 0.99654 | -0.066557 | 8.2048
106 | -0.023088 | -0.0057931 | 0.023098 | 0.0057988 | 9.4401e-06 | 5.7653e-06 | 0.034466 | 0.034466 | 0.034466 | 0.99687 | -0.060193 | 0.99731 | -0.051621 | 9.4687
107 | 0.018392 | 0.0046139 | -0.018386 | -0.0046105 | 5.7835e-06 | 3.4352e-06 | 0.027464 | 0.027464 | 0.027464 | 0.99654 | -0.066557 | 0.99619 | -0.073155 | 7.5452
108 | -0.025022 | -0.0062811 | 0.025029 | 0.0062854 | 6.9237e-06 | 4.2583e-06 | 0.037337 | 0.037337 | 0.037337 | 0.99731 | -0.051621 | 0.99761 | -0.045822 | 10.2574
109 | 0.016463 | 0.0041286 | -0.01646 | -0.0041269 | 2.8267e-06 | 1.6468e-06 | 0.024592 | 0.024592 | 0.024592 | 0.99619 | -0.073155 | 0.99601 | -0.076758 | 6.7561
110 | -0.027167 | -0.0068211 | 0.027172 | 0.0068245 | 5.4769e-06 | 3.3891e-06 | 0.040526 | 0.040526 | 0.040526 | 0.99761 | -0.045822 | 0.99783 | -0.041597 | 11.1334
111 | 0.01335 | 0.0033479 | -0.013348 | -0.0033465 | 2.488e-06 | 1.3753e-06 | 0.019945 | 0.019946 | 0.019946 | 0.99601 | -0.076758 | 0.99581 | -0.080669 | 5.4796
112 | 0.0031104 | 0.00077907 | -0.0031101 | -0.0007793 | 2.4143e-07 | -2.3351e-07 | 0.0046467 | 0.0046468 | 0.0046468 | 0.99601 | -0.076758 | 0.99592 | -0.078388 | 1.2766
113 | -0.029095 | -0.0073064 | 0.029116 | 0.0073198 | 2.1589e-05 | 1.3417e-05 | 0.043393 | 0.043393 | 0.043393 | 0.99783 | -0.041597 | 0.99864 | -0.026057 | 11.9211
114 | 0.011613 | 0.0029117 | -0.011606 | -0.0029082 | 6.7606e-06 | 3.5485e-06 | 0.017353 | 0.017354 | 0.017354 | 0.99581 | -0.080669 | 0.99517 | -0.092892 | 4.7675
115 | 0.0024387 | 0.00061101 | -0.0024386 | -0.00061117 | 7.8344e-08 | -1.5463e-07 | 0.0036436 | 0.0036436 | 0.0036436 | 0.99592 | -0.078388 | 0.99589 | -0.079062 | 1.001
116 | 0.0078261 | 0.0019611 | -0.0078248 | -0.0019605 | 1.3785e-06 | 5.3352e-07 | 0.011702 | 0.011702 | 0.011702 | 0.99517 | -0.092892 | 0.99498 | -0.09659 | 3.2148
117 | 0.00378 | 0.00094712 | -0.0037797 | -0.00094728 | 3.4887e-07 | -1.5507e-07 | 0.0056519 | 0.0056521 | 0.0056521 | 0.99517 | -0.092892 | 0.99507 | -0.094829 | 1.5528
118 | 0.049338 | 0.01244 | -0.049308 | -0.012421 | 3.0427e-05 | 1.8755e-05 | 0.075184 | 0.075184 | 0.075184 | 0.97684 | -0.44402 | 0.97618 | -0.45691 | 10.3275
119 | 0.048215 | 0.012147 | -0.048207 | -0.012142 | 7.9307e-06 | 4.88e-06 | 0.073518 | 0.073518 | 0.073518 | 0.97618 | -0.45691 | 0.976 | -0.46035 | 10.0986
120 | 0.0062696 | 0.0015708 | -0.0062684 | -0.0015705 | 1.1881e-06 | 2.9242e-07 | 0.0093762 | 0.0093763 | 0.0093763 | 0.99498 | -0.09659 | 0.99478 | -0.10057 | 2.5759
121 | 0.001232 | 0.0003086 | -0.001232 | -0.00030876 | 1.8482e-08 | -1.6045e-07 | 0.0018845 | 0.0018846 | 0.0018846 | 0.97276 | -0.5243 | 0.97274 | -0.52461 | 0.51774
122 | -0.04531 | -0.011402 | 0.04533 | 0.011414 | 1.97e-05 | 1.206e-05 | 0.069161 | 0.069161 | 0.069161 | 0.9751 | -0.47807 | 0.97556 | -0.46897 | 9.5001
123 | 0.015089 | 0.0037833 | -0.015089 | -0.0037829 | 6.6146e-07 | 3.8218e-07 | 0.023074 | 0.023074 | 0.023074 | 0.97313 | -0.51696 | 0.97308 | -0.51788 | 6.339
124 | 0.013457 | 0.0033739 | -0.013454 | -0.0033724 | 2.6954e-06 | 1.5143e-06 | 0.020579 | 0.020579 | 0.020579 | 0.97308 | -0.51788 | 0.97287 | -0.52209 | 5.6535
125 | 0.012366 | 0.0030998 | -0.012365 | -0.003099 | 1.4131e-06 | 7.7362e-07 | 0.018915 | 0.018915 | 0.018915 | 0.97287 | -0.52209 | 0.97275 | -0.52448 | 5.1964
126 | 0.010482 | 0.0026271 | -0.01048 | -0.0026258 | 2.4507e-06 | 1.253e-06 | 0.016034 | 0.016035 | 0.016035 | 0.97275 | -0.52448 | 0.9725 | -0.52939 | 4.4051
127 | 0.0079109 | 0.001982 | -0.0079103 | -0.0019818 | 6.0364e-07 | 2.5002e-07 | 0.012104 | 0.012104 | 0.012104 | 0.9725 | -0.52939 | 0.97242 | -0.53099 | 3.3253
128 | 0.0049094 | 0.0012297 | -0.0049085 | -0.0012296 | 9.1089e-07 | 4.913e-08 | 0.0075123 | 0.0075125 | 0.0075125 | 0.97242 | -0.53099 | 0.97222 | -0.53489 | 2.0639
129 | -0.047157 | -0.011872 | 0.047177 | 0.011884 | 1.9442e-05 | 1.1942e-05 | 0.071947 | 0.071947 | 0.071947 | 0.97556 | -0.46897 | 0.976 | -0.46035 | 9.8829
130 | 0.0032011 | 0.0008011 | -0.0032009 | -0.0008012 | 1.4361e-07 | -1.0464e-07 | 0.004907 | 0.0049071 | 0.0049071 | 0.97061 | -0.56672 | 0.97056 | -0.56766 | 1.3481
131 | 0.0032009 | 0.0008012 | -0.0032005 | -0.00080149 | 4.0321e-07 | -2.9368e-07 | 0.0049071 | 0.0049073 | 0.0049073 | 0.97056 | -0.56766 | 0.97043 | -0.57031 | 1.3482
132 | 0.0024789 | 0.00062064 | -0.0024789 | -0.00062064 | 1.28e-09 | -2.0997e-09 | 0.0038008 | 0.0038008 | 0.0038008 | 0.97043 | -0.57031 | 0.97043 | -0.57032 | 1.0442
133 | 0.00089369 | 0.00022367 | -0.00089367 | -0.00022398 | 1.8213e-08 | -3.0786e-07 | 0.0013703 | 0.0013704 | 0.0013704 | 0.97039 | -0.57112 | 0.97037 | -0.57155 | 0.37649
134 | -0.0015676 | -0.00039256 | 0.0015676 | 0.00039226 | 5.9471e-08 | -3.0108e-07 | 0.0024036 | 0.0024035 | 0.0024036 | 0.97039 | -0.57112 | 0.97043 | -0.57032 | 0.66034
135 | -0.037258 | -0.0093909 | 0.037277 | 0.0094028 | 1.8895e-05 | 1.1896e-05 | 0.056716 | 0.056716 | 0.056716 | 0.97783 | -0.42523 | 0.97837 | -0.41464 | 15.5813
136 | -0.03812 | -0.0096142 | 0.038135 | 0.0096234 | 1.4562e-05 | 9.1747e-06 | 0.057999 | 0.057999 | 0.057999 | 0.97837 | -0.41464 | 0.97878 | -0.40666 | 15.9338
137 | 0.0018092 | 0.00045324 | -0.0018091 | -0.00045341 | 4.1112e-08 | -1.6803e-07 | 0.0027062 | 0.0027062 | 0.0027062 | 0.99478 | -0.10057 | 0.99475 | -0.10105 | 0.74347
138 | 0.0044593 | 0.0011172 | -0.0044589 | -0.0011173 | 3.291e-07 | -4.5436e-08 | 0.0066702 | 0.0066703 | 0.0066703 | 0.99478 | -0.10057 | 0.9947 | -0.10212 | 1.8325
139 | 0.0029196 | 0.00073148 | -0.0029194 | -0.00073167 | 1.6837e-07 | -1.9776e-07 | 0.0043675 | 0.0043676 | 0.0043676 | 0.9947 | -0.10212 | 0.99463 | -0.10333 | 1.1999
140 | -0.039233 | -0.0098987 | 0.039273 | 0.0099241 | 4.0321e-05 | 2.5425e-05 | 0.059669 | 0.059669 | 0.059669 | 0.97878 | -0.40666 | 0.97988 | -0.38522 | 16.3925
141 | -0.0012246 | -0.00030692 | 0.0012249 | 0.0003041 | 3.0015e-07 | -2.8218e-06 | 0.0018447 | 0.0018436 | 0.0018447 | 0.98785 | -0.23109 | 0.98812 | -0.22592 | 0.50677
142 | 0.045077 | 0.011468 | -0.04507 | -0.011463 | 7.1949e-06 | 4.3937e-06 | 0.068093 | 0.068093 | 0.068093 | 0.98595 | -0.26768 | 0.98577 | -0.27099 | 9.3534
143 | 0.044345 | 0.011282 | -0.044315 | -0.011263 | 2.9767e-05 | 1.8149e-05 | 0.066998 | 0.066998 | 0.066998 | 0.98577 | -0.27099 | 0.98505 | -0.28493 | 9.203
144 | 0.042768 | 0.010876 | -0.042758 | -0.01087 | 9.3937e-06 | 5.707e-06 | 0.064661 | 0.064661 | 0.064661 | 0.98505 | -0.28493 | 0.98482 | -0.28949 | 8.882
145 | 0.0010856 | 0.0002719 | -0.0010856 | -0.00027208 | 1.541e-08 | -1.806e-07 | 0.0016485 | 0.0016486 | 0.0016486 | 0.97988 | -0.38522 | 0.97987 | -0.38552 | 0.45292
146 | -0.040359 | -0.010196 | 0.040366 | 0.0102 | 7.0888e-06 | 4.4735e-06 | 0.061317 | 0.061317 | 0.061317 | 0.97988 | -0.38522 | 0.98007 | -0.38156 | 16.8454
147 | -0.041442 | -0.01047 | 0.041626 | 0.010586 | 0.00018377 | 0.00011605 | 0.062951 | 0.06295 | 0.062951 | 0.98007 | -0.38156 | 0.98482 | -0.28949 | 17.2942
148 | 0.0091758 | 0.0023001 | -0.009174 | -0.0022993 | 1.8213e-06 | 8.6041e-07 | 0.014045 | 0.014045 | 0.014045 | 0.97217 | -0.53669 | 0.97196 | -0.54086 | 3.8585
149 | 0.0060495 | 0.0015162 | -0.0060395 | -0.0015136 | 1.004e-05 | 2.5645e-06 | 0.0092615 | 0.0092629 | 0.0092629 | 0.97196 | -0.54086 | 0.9702 | -0.57572 | 2.5447
150 | 0.001748 | 0.00043753 | -0.0017478 | -0.00043805 | 1.2977e-07 | -5.1651e-07 | 0.0026751 | 0.0026753 | 0.0026753 | 0.97222 | -0.53489 | 0.97214 | -0.53645 | 0.73498

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.22603 | 0.057721

## res_load
| p_mw | q_mvar
0 | 0.0007254 | 0.0001818
1 | 0.0014877 | 0.00037286
2 | 0.0016937 | 0.00042447
3 | 0.00076472 | 0.00019166
4 | 0.0013212 | 0.00033112
5 | 0.00081812 | 0.00020504
6 | 0.00069665 | 0.0001746
7 | 0.00068867 | 0.0001726
8 | 0.0011297 | 0.00028312
9 | 0.0015968 | 0.0004002
10 | 0.0018058 | 0.00045259
11 | 0.010657 | 0.0026709
12 | 0.0016463 | 0.00041261
13 | 0.0027162 | 0.00068074
14 | 0.0018711 | 0.00046895
15 | 0.0054654 | 0.0013698
16 | 0.0012132 | 0.00030407
17 | 0.0013184 | 0.00033043
18 | 0.0031677 | 0.00079389
19 | 0.0026364 | 0.00066074
20 | 0.0018051 | 0.00045241
21 | 0.0013909 | 0.00034858
22 | 0.0039419 | 0.00098792
23 | 0.0030802 | 0.00077198
24 | 0.0026447 | 0.00066282
25 | 0.0009796 | 0.00024551
26 | 0.0026147 | 0.00065532
27 | 0.0025917 | 0.00064953
28 | 0.0010721 | 0.00026869
29 | 0.0015429 | 0.0003867
30 | 0.0020838 | 0.00052225
31 | 0.0011911 | 0.00029852
32 | 0.0011442 | 0.00028676
33 | 0.0013389 | 0.00033557
34 | 0.0012404 | 0.00031088
35 | 0.0022607 | 0.00056659
36 | 0.0010198 | 0.00025559
37 | 0.00054994 | 0.00013783
38 | 0.0015235 | 0.00038181
39 | 0.0025663 | 0.00064317
40 | 0.0012183 | 0.00030533
41 | 0.00056543 | 0.00014171
42 | 0.0012932 | 0.0003241
43 | 0.0015692 | 0.00039327
44 | 0.00080681 | 0.00020221
45 | 0.00066539 | 0.00016676
46 | 0.0011483 | 0.00028779
47 | 0.0039096 | 0.00097984
48 | 0.0010748 | 0.00026937
49 | 0.00050987 | 0.00012779
50 | 0.0014548 | 0.0003646
51 | 0.0015384 | 0.00038556
52 | 0.0009886 | 0.00024777
53 | 0.00096712 | 0.00024238
54 | 0.0012608 | 0.00031598
55 | 0.00057233 | 0.00014344
56 | 0.0014166 | 0.00035504
57 | 0.00070522 | 0.00017674
58 | 0.0014945 | 0.00037455
59 | 0.0016555 | 0.0004149
60 | 0.0013822 | 0.00034641
61 | 0.0026485 | 0.00066377
62 | 0.00086736 | 0.00021738
63 | 0.0022919 | 0.0005744
64 | 0.0017627 | 0.00044177
65 | 0.0026888 | 0.00067387
66 | 0.0017348 | 0.00043477
67 | 0.0012649 | 0.00031702
68 | 0.0016489 | 0.00041324
69 | 0.00098644 | 0.00024723
70 | 0.00098418 | 0.00024666
71 | 0.00080133 | 0.00020083
72 | 0.0024455 | 0.0006129
73 | 0.0007517 | 0.00018839
74 | 0.00099806 | 0.00025014
75 | 0.0022545 | 0.00056503
76 | 0.00074474 | 0.00018665
77 | 0.0030821 | 0.00077244
78 | 0.0016082 | 0.00040305
79 | 0.0019242 | 0.00048226
80 | 0.0019229 | 0.00048193
81 | 0.0021378 | 0.00053579
82 | 0.0019226 | 0.00048184
83 | 0.0017347 | 0.00043475
84 | 0.00067147 | 0.00016829
85 | 0.0010008 | 0.00025083
86 | 0.0024386 | 0.00061117
87 | 0.0010021 | 0.00025115
88 | 0.0010933 | 0.00027399
89 | 0.0015551 | 0.00038976
90 | 0.0037797 | 0.00094728
91 | 0.001985 | 0.00049749
92 | 0.00070564 | 0.00017685
93 | 0.0010081 | 0.00025265
94 | 0.001232 | 0.00030876
95 | 0.0011022 | 0.00027624
96 | 0.0016318 | 0.00040896
97 | 0.0010878 | 0.00027264
98 | 0.001883 | 0.00047193
99 | 0.0025687 | 0.00064378
100 | 0.0030008 | 0.00075208
101 | 0.0019113 | 0.00047903
102 | 0.0018271 | 0.00045792
103 | 0.0010301 | 0.00025816
104 | 0.001449 | 0.00036316
105 | 0.00072162 | 0.00018086
106 | 0.00067388 | 0.00016889
107 | 0.00089367 | 0.00022398
108 | 0.00091126 | 0.00022838
109 | 0.0010801 | 0.0002707
110 | 0.00084351 | 0.0002114
111 | 0.0018091 | 0.00045341
112 | 0.0015394 | 0.0003858
113 | 0.0029194 | 0.00073167
114 | 0.0010984 | 0.00027528
115 | 0.0012246 | 0.00030692
116 | 0.0030979 | 0.0007764
117 | 0.0025994 | 0.00065148
118 | 0.00072554 | 0.00018184
119 | 0.0015471 | 0.00038774
120 | 0.0010856 | 0.00027208
121 | 0.0010762 | 0.00026972
122 | 0.0011322 | 0.00028375
123 | 0.0019685 | 0.00049334
124 | 0.0031245 | 0.00078307
125 | 0.0060395 | 0.0015136
126 | 0.0031606 | 0.00079211
127 | 0.0017478 | 0.00043805

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1