## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-11_1_3_node_47 | 0.4 | n |  | TRUE
1 | bus_LV_2325-11_1_3_node_48 | 0.4 | n |  | TRUE
2 | bus_LV_2325-11_1_3_node_49 | 0.4 | n |  | TRUE
3 | bus_LV_2325-11_1_3_node_232 | 0.4 | n |  | TRUE
4 | bus_LV_2325-11_1_3_node_50 | 0.4 | n |  | TRUE
5 | bus_LV_2325-11_1_3_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_2325-11_1_3_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_2325-11_1_3_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_2325-11_1_3_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_2325-11_1_3_node_55 | 0.4 | n |  | TRUE
10 | bus_LV_2325-11_1_3_node_158 | 0.4 | n |  | TRUE
11 | bus_LV_2325-11_1_3_node_156 | 0.4 | n |  | TRUE
12 | bus_LV_2325-11_1_3_node_128 | 0.4 | n |  | TRUE
13 | bus_LV_2325-11_1_3_node_127 | 0.4 | n |  | TRUE
14 | bus_LV_2325-11_1_3_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_2325-11_1_3_node_57 | 0.4 | n |  | TRUE
16 | bus_LV_2325-11_1_3_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_2325-11_1_3_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_2325-11_1_3_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_2325-11_1_3_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_2325-11_1_3_node_114 | 0.4 | n |  | TRUE
21 | bus_LV_2325-11_1_3_node_115 | 0.4 | n |  | TRUE
22 | bus_LV_2325-11_1_3_node_116 | 0.4 | n |  | TRUE
23 | bus_LV_2325-11_1_3_node_215 | 0.4 | n |  | TRUE
24 | bus_LV_2325-11_1_3_node_69 | 0.4 | n |  | TRUE
25 | bus_LV_2325-11_1_3_node_70 | 0.4 | n |  | TRUE
26 | bus_LV_2325-11_1_3_node_71 | 0.4 | n |  | TRUE
27 | bus_LV_2325-11_1_3_node_72 | 0.4 | n |  | TRUE
28 | bus_LV_2325-11_1_3_node_73 | 0.4 | n |  | TRUE
29 | bus_LV_2325-11_1_3_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_2325-11_1_3_node_75 | 0.4 | n |  | TRUE
31 | bus_LV_2325-11_1_3_node_250 | 0.4 | n |  | TRUE
32 | bus_LV_2325-11_1_3_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_2325-11_1_3_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_2325-11_1_3_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_2325-11_1_3_node_260 | 0.4 | n |  | TRUE
36 | bus_LV_2325-11_1_3_node_86 | 0.4 | n |  | TRUE
37 | bus_LV_2325-11_1_3_node_159 | 0.4 | n |  | TRUE
38 | bus_LV_2325-11_1_3_node_99 | 0.4 | n |  | TRUE
39 | bus_LV_2325-11_1_3_node_100 | 0.4 | n |  | TRUE
40 | bus_LV_2325-11_1_3_node_101 | 0.4 | n |  | TRUE
41 | bus_LV_2325-11_1_3_node_102 | 0.4 | n |  | TRUE
42 | bus_LV_2325-11_1_3_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_2325-11_1_3_node_104 | 0.4 | n |  | TRUE
44 | bus_LV_2325-11_1_3_node_105 | 0.4 | n |  | TRUE
45 | bus_LV_2325-11_1_3_node_106 | 0.4 | n |  | TRUE
46 | bus_LV_2325-11_1_3_node_107 | 0.4 | n |  | TRUE
47 | bus_LV_2325-11_1_3_node_134 | 0.4 | n |  | TRUE
48 | bus_LV_2325-11_1_3_node_276 | 0.4 | n |  | TRUE
49 | bus_LV_2325-11_1_3_node_117 | 0.4 | n |  | TRUE
50 | bus_LV_2325-11_1_3_node_132 | 0.4 | n |  | TRUE
51 | bus_LV_2325-11_1_3_node_118 | 0.4 | n |  | TRUE
52 | bus_LV_2325-11_1_3_node_253 | 0.4 | n |  | TRUE
53 | bus_LV_2325-11_1_3_node_121 | 0.4 | n |  | TRUE
54 | bus_LV_2325-11_1_3_node_122 | 0.4 | n |  | TRUE
55 | bus_LV_2325-11_1_3_node_123 | 0.4 | n |  | TRUE
56 | bus_LV_2325-11_1_3_node_124 | 0.4 | n |  | TRUE
57 | bus_LV_2325-11_1_3_node_125 | 0.4 | n |  | TRUE
58 | bus_LV_2325-11_1_3_node_154 | 0.4 | n |  | TRUE
59 | bus_LV_2325-11_1_3_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_2325-11_1_3_node_130 | 0.4 | n |  | TRUE
61 | bus_LV_2325-11_1_3_node_131 | 0.4 | n |  | TRUE
62 | bus_LV_2325-11_1_3_node_133 | 0.4 | n |  | TRUE
63 | bus_LV_2325-11_1_3_node_193 | 0.4 | n |  | TRUE
64 | bus_LV_2325-11_1_3_node_194 | 0.4 | n |  | TRUE
65 | bus_LV_2325-11_1_3_node_135 | 0.4 | n |  | TRUE
66 | bus_LV_2325-11_1_3_node_136 | 0.4 | n |  | TRUE
67 | bus_LV_2325-11_1_3_node_137 | 0.4 | n |  | TRUE
68 | bus_LV_2325-11_1_3_node_138 | 0.4 | n |  | TRUE
69 | bus_LV_2325-11_1_3_node_139 | 0.4 | n |  | TRUE
70 | bus_LV_2325-11_1_3_node_256 | 0.4 | n |  | TRUE
71 | bus_LV_2325-11_1_3_node_264 | 0.4 | n |  | TRUE
72 | bus_LV_2325-11_1_3_node_140 | 0.4 | n |  | TRUE
73 | bus_LV_2325-11_1_3_node_141 | 0.4 | n |  | TRUE
74 | bus_LV_2325-11_1_3_node_142 | 0.4 | n |  | TRUE
75 | bus_LV_2325-11_1_3_node_146 | 0.4 | n |  | TRUE
76 | bus_LV_2325-11_1_3_node_143 | 0.4 | n |  | TRUE
77 | bus_LV_2325-11_1_3_node_144 | 0.4 | n |  | TRUE
78 | bus_LV_2325-11_1_3_node_145 | 0.4 | n |  | TRUE
79 | bus_LV_2325-11_1_3_node_211 | 0.4 | n |  | TRUE
80 | bus_LV_2325-11_1_3_node_147 | 0.4 | n |  | TRUE
81 | bus_LV_2325-11_1_3_node_166 | 0.4 | n |  | TRUE
82 | bus_LV_2325-11_1_3_node_148 | 0.4 | n |  | TRUE
83 | bus_LV_2325-11_1_3_node_149 | 0.4 | n |  | TRUE
84 | bus_LV_2325-11_1_3_node_150 | 0.4 | n |  | TRUE
85 | bus_LV_2325-11_1_3_node_151 | 0.4 | n |  | TRUE
86 | bus_LV_2325-11_1_3_node_153 | 0.4 | n |  | TRUE
87 | bus_LV_2325-11_1_3_node_152 | 0.4 | n |  | TRUE
88 | bus_LV_2325-11_1_3_node_212 | 0.4 | n |  | TRUE
89 | bus_LV_2325-11_1_3_node_197 | 0.4 | n |  | TRUE
90 | bus_LV_2325-11_1_3_node_216 | 0.4 | n |  | TRUE
91 | bus_LV_2325-11_1_3_node_155 | 0.4 | n |  | TRUE
92 | bus_LV_2325-11_1_3_node_282 | 0.4 | n |  | TRUE
93 | bus_LV_2325-11_1_3_node_280 | 0.4 | n |  | TRUE
94 | bus_LV_2325-11_1_3_node_157 | 0.4 | n |  | TRUE
95 | bus_LV_2325-11_1_3_node_243 | 0.4 | n |  | TRUE
96 | bus_LV_2325-11_1_3_node_231 | 0.4 | n |  | TRUE
97 | bus_LV_2325-11_1_3_node_161 | 0.4 | n |  | TRUE
98 | bus_LV_2325-11_1_3_node_162 | 0.4 | n |  | TRUE
99 | bus_LV_2325-11_1_3_node_163 | 0.4 | n |  | TRUE
100 | bus_LV_2325-11_1_3_node_164 | 0.4 | n |  | TRUE
101 | bus_LV_2325-11_1_3_node_165 | 0.4 | n |  | TRUE
102 | bus_LV_2325-11_1_3_node_229 | 0.4 | n |  | TRUE
103 | bus_LV_2325-11_1_3_node_182 | 0.4 | n |  | TRUE
104 | bus_LV_2325-11_1_3_node_183 | 0.4 | n |  | TRUE
105 | bus_LV_2325-11_1_3_node_184 | 0.4 | n |  | TRUE
106 | bus_LV_2325-11_1_3_node_185 | 0.4 | n |  | TRUE
107 | bus_LV_2325-11_1_3_node_186 | 0.4 | n |  | TRUE
108 | bus_LV_2325-11_1_3_node_187 | 0.4 | n |  | TRUE
109 | bus_LV_2325-11_1_3_node_214 | 0.4 | n |  | TRUE
110 | bus_LV_2325-11_1_3_node_195 | 0.4 | n |  | TRUE
111 | bus_LV_2325-11_1_3_node_196 | 0.4 | n |  | TRUE
112 | bus_LV_2325-11_1_3_node_198 | 0.4 | n |  | TRUE
113 | bus_LV_2325-11_1_3_node_270 | 0.4 | n |  | TRUE
114 | bus_LV_2325-11_1_3_node_294 | 0.4 | n |  | TRUE
115 | bus_LV_2325-11_1_3_node_210 | 0.4 | n |  | TRUE
116 | bus_LV_2325-11_1_3_node_213 | 0.4 | n |  | TRUE
117 | bus_LV_2325-11_1_3_node_225 | 0.4 | n |  | TRUE
118 | bus_LV_2325-11_1_3_node_218 | 0.4 | n |  | TRUE
119 | bus_LV_2325-11_1_3_node_221 | 0.4 | n |  | TRUE
120 | bus_LV_2325-11_1_3_node_230 | 0.4 | n |  | TRUE
121 | bus_LV_2325-11_1_3_node_226 | 0.4 | n |  | TRUE
122 | bus_LV_2325-11_1_3_node_227 | 0.4 | n |  | TRUE
123 | bus_LV_2325-11_1_3_node_228 | 0.4 | n |  | TRUE
124 | bus_LV_2325-11_1_3_node_252 | 0.4 | n |  | TRUE
125 | bus_LV_2325-11_1_3_node_254 | 0.4 | n |  | TRUE
126 | bus_LV_2325-11_1_3_node_255 | 0.4 | n |  | TRUE
127 | bus_LV_2325-11_1_3_node_257 | 0.4 | n |  | TRUE
128 | bus_LV_2325-11_1_3_node_258 | 0.4 | n |  | TRUE
129 | bus_LV_2325-11_1_3_node_261 | 0.4 | n |  | TRUE
130 | bus_LV_2325-11_1_3_node_262 | 0.4 | n |  | TRUE
131 | bus_LV_2325-11_1_3_node_263 | 0.4 | n |  | TRUE
132 | bus_LV_2325-11_1_3_node_269 | 0.4 | n |  | TRUE
133 | bus_LV_2325-11_1_3_node_265 | 0.4 | n |  | TRUE
134 | bus_LV_2325-11_1_3_node_278 | 0.4 | n |  | TRUE
135 | bus_LV_2325-11_1_3_node_277 | 0.4 | n |  | TRUE
136 | bus_LV_2325-11_1_3_node_279 | 0.4 | n |  | TRUE
137 | bus_LV_2325-11_1_3_node_281 | 0.4 | n |  | TRUE
138 | bus_LV_2325-11_1_3_node_295 | 0.4 | n |  | TRUE
139 | bus_MV_37_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-11_1_3_load_47 | 0 | 0.0021852 | 0.00054767 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-11_1_3_load_49 | 2 | 0.0021719 | 0.00054433 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-11_1_3_load_232 | 3 | 0.0012859 | 0.00032226 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-11_1_3_load_50 | 4 | 0.0015413 | 0.00038628 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-11_1_3_load_51 | 5 | 0.0014972 | 0.00037524 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-11_1_3_load_52 | 6 | 0.00092839 | 0.00023268 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-11_1_3_load_53 | 7 | 0.0012438 | 0.00031173 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-11_1_3_load_158 | 10 | 0.0016135 | 0.00040438 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-11_1_3_load_128 | 12 | 0.0012142 | 0.00030431 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-11_1_3_load_127 | 13 | 0.00081382 | 0.00020396 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-11_1_3_load_56 | 14 | 0.00096993 | 0.00024309 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-11_1_3_load_57 | 15 | 0.00094241 | 0.00023619 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-11_1_3_load_58 | 16 | 0.00076151 | 0.00019085 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-11_1_3_load_59 | 17 | 0.0037566 | 0.00094149 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-11_1_3_load_61 | 19 | 0.0031183 | 0.00078153 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-11_1_3_load_115 | 21 | 0.00060478 | 0.00015157 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-11_1_3_load_116 | 22 | 0.0016694 | 0.0004184 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-11_1_3_load_215 | 23 | 0.0034601 | 0.00086718 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-11_1_3_load_69 | 24 | 0.0027232 | 0.00068249 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-11_1_3_load_70 | 25 | 0.0016067 | 0.00040269 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-11_1_3_load_72 | 27 | 0.0013701 | 0.00034338 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-11_1_3_load_73 | 28 | 0.00059278 | 0.00014856 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-11_1_3_load_74 | 29 | 0.0027393 | 0.00068653 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-11_1_3_load_250 | 31 | 0.0055709 | 0.0013962 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-11_1_3_load_83 | 33 | 0.0021 | 0.00052631 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-11_1_3_load_84 | 34 | 0.00086115 | 0.00021582 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-11_1_3_load_260 | 35 | 0.0011725 | 0.00029385 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-11_1_3_load_86 | 36 | 0.0010033 | 0.00025145 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-11_1_3_load_99 | 38 | 0.0020443 | 0.00051234 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-11_1_3_load_100 | 39 | 0.0015312 | 0.00038376 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-11_1_3_load_102 | 41 | 0.00095506 | 0.00023936 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-11_1_3_load_103 | 42 | 0.00075085 | 0.00018818 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-11_1_3_load_104 | 43 | 0.0013456 | 0.00033723 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-11_1_3_load_105 | 44 | 0.0006664 | 0.00016701 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-11_1_3_load_106 | 45 | 0.0017756 | 0.00044501 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-11_1_3_load_107 | 46 | 0.0013929 | 0.00034908 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-11_1_3_load_134 | 47 | 0.00060933 | 0.00015271 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-11_1_3_load_276 | 48 | 0.0026942 | 0.00067524 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-11_1_3_load_117 | 49 | 0.00073065 | 0.00018312 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-11_1_3_load_132 | 50 | 0.00057523 | 0.00014417 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-11_1_3_load_118 | 51 | 0.00068792 | 0.00017241 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-11_1_3_load_253 | 52 | 0.00087925 | 0.00022036 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-11_1_3_load_121 | 53 | 0.00080187 | 0.00020097 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-11_1_3_load_122 | 54 | 0.0016528 | 0.00041423 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-11_1_3_load_123 | 55 | 0.00092292 | 0.0002313 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-11_1_3_load_124 | 56 | 0.0013772 | 0.00034516 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-11_1_3_load_125 | 57 | 0.00073761 | 0.00018486 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-11_1_3_load_129 | 59 | 0.00067402 | 0.00016893 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-11_1_3_load_130 | 60 | 0.0013495 | 0.00033821 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-11_1_3_load_131 | 61 | 0.0024861 | 0.00062308 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-11_1_3_load_193 | 63 | 0.0013874 | 0.00034771 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2325-11_1_3_load_194 | 64 | 0.002383 | 0.00059724 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2325-11_1_3_load_135 | 65 | 0.0010688 | 0.00026787 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2325-11_1_3_load_136 | 66 | 0.0027354 | 0.00068556 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2325-11_1_3_load_137 | 67 | 0.0016782 | 0.00042059 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2325-11_1_3_load_138 | 68 | 0.0014147 | 0.00035455 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2325-11_1_3_load_139 | 69 | 0.00071298 | 0.00017869 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2325-11_1_3_load_140 | 72 | 0.00092328 | 0.0002314 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2325-11_1_3_load_142 | 74 | 0.0015133 | 0.00037928 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2325-11_1_3_load_146 | 75 | 0.0014372 | 0.0003602 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2325-11_1_3_load_143 | 76 | 0.0016164 | 0.00040511 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2325-11_1_3_load_144 | 77 | 0.0014419 | 0.00036137 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2325-11_1_3_load_145 | 78 | 0.0016154 | 0.00040487 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2325-11_1_3_load_211 | 79 | 0.00206 | 0.00051628 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2325-11_1_3_load_147 | 80 | 0.0033951 | 0.00085089 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2325-11_1_3_load_166 | 81 | 0.001053 | 0.0002639 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2325-11_1_3_load_148 | 82 | 0.0023672 | 0.00059328 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2325-11_1_3_load_149 | 83 | 0.0017025 | 0.00042668 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2325-11_1_3_load_150 | 84 | 0.0014755 | 0.0003698 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2325-11_1_3_load_151 | 85 | 0.00092794 | 0.00023256 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2325-11_1_3_load_152 | 87 | 0.00088577 | 0.000222 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2325-11_1_3_load_212 | 88 | 0.00092391 | 0.00023155 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2325-11_1_3_load_197 | 89 | 0.0029226 | 0.00073247 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2325-11_1_3_load_216 | 90 | 0.0047993 | 0.0012028 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2325-11_1_3_load_280 | 93 | 0.001186 | 0.00029725 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2325-11_1_3_load_157 | 94 | 0.0015912 | 0.0003988 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2325-11_1_3_load_243 | 95 | 0.0014892 | 0.00037322 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2325-11_1_3_load_231 | 96 | 0.0030721 | 0.00076995 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2325-11_1_3_load_161 | 97 | 0.00098369 | 0.00024654 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2325-11_1_3_load_162 | 98 | 0.0013516 | 0.00033875 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2325-11_1_3_load_163 | 99 | 0.0013288 | 0.00033302 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2325-11_1_3_load_165 | 101 | 0.002575 | 0.00064536 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2325-11_1_3_load_182 | 103 | 0.0009113 | 0.00022839 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2325-11_1_3_load_183 | 104 | 0.0025358 | 0.00063552 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2325-11_1_3_load_184 | 105 | 0.0017266 | 0.00043274 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2325-11_1_3_load_186 | 107 | 0.0017198 | 0.00043102 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2325-11_1_3_load_187 | 108 | 0.0034767 | 0.00087135 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2325-11_1_3_load_214 | 109 | 0.0039215 | 0.00098281 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2325-11_1_3_load_195 | 110 | 0.0030811 | 0.00077221 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2325-11_1_3_load_196 | 111 | 0.0017596 | 0.000441 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2325-11_1_3_load_198 | 112 | 0.0024219 | 0.00060699 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2325-11_1_3_load_294 | 114 | 0.0021913 | 0.0005492 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2325-11_1_3_load_210 | 115 | 0.0014293 | 0.00035821 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2325-11_1_3_load_213 | 116 | 0.00082114 | 0.0002058 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2325-11_1_3_load_225 | 117 | 0.0014597 | 0.00036583 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2325-11_1_3_load_218 | 118 | 0.0017571 | 0.00044037 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2325-11_1_3_load_221 | 119 | 0.0011362 | 0.00028475 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2325-11_1_3_load_230 | 120 | 0.0013696 | 0.00034325 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2325-11_1_3_load_226 | 121 | 0.00065867 | 0.00016508 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2325-11_1_3_load_227 | 122 | 0.0011708 | 0.00029342 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2325-11_1_3_load_228 | 123 | 0.00091807 | 0.00023009 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2325-11_1_3_load_252 | 124 | 0.00091822 | 0.00023013 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2325-11_1_3_load_254 | 125 | 0.0024743 | 0.00062012 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2325-11_1_3_load_255 | 126 | 0.0016636 | 0.00041695 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2325-11_1_3_load_257 | 127 | 0.0024058 | 0.00060295 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2325-11_1_3_load_258 | 128 | 0.001632 | 0.00040903 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2325-11_1_3_load_261 | 129 | 0.0011866 | 0.0002974 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2325-11_1_3_load_262 | 130 | 0.0013115 | 0.00032868 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2325-11_1_3_load_263 | 131 | 0.001102 | 0.00027618 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2325-11_1_3_load_269 | 132 | 0.0010633 | 0.00026648 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2325-11_1_3_load_278 | 134 | 0.0020781 | 0.00052083 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2325-11_1_3_load_277 | 135 | 0.0014909 | 0.00037366 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2325-11_1_3_load_281 | 137 | 0.00076263 | 0.00019113 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2325-11_1_3_load_295 | 138 | 0.0021298 | 0.00053379 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-11_1_3_line_0 |  | 0 | 1 | 0.19713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-11_1_3_line_1 |  | 1 | 2 | 0.056557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-11_1_3_line_2 |  | 2 | 3 | 0.47057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-11_1_3_line_3 |  | 3 | 46 | 0.1756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-11_1_3_line_4 |  | 4 | 5 | 0.018897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-11_1_3_line_5 |  | 4 | 6 | 0.0058643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-11_1_3_line_6 |  | 5 | 7 | 0.0025116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-11_1_3_line_7 |  | 6 | 8 | 0.03077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-11_1_3_line_8 |  | 7 | 9 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-11_1_3_line_9 |  | 8 | 10 | 0.020395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-11_1_3_line_10 |  | 8 | 11 | 0.024664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-11_1_3_line_11 |  | 9 | 12 | 0.01438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-11_1_3_line_12 |  | 9 | 13 | 0.02155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-11_1_3_line_13 |  | 10 | 95 | 0.019756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-11_1_3_line_14 |  | 11 | 94 | 0.018971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-11_1_3_line_15 |  | 11 | 78 | 0.020068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-11_1_3_line_16 |  | 14 | 15 | 0.028888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-11_1_3_line_17 |  | 14 | 16 | 0.0044997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-11_1_3_line_18 |  | 15 | 17 | 0.0056708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-11_1_3_line_19 |  | 16 | 18 | 0.022115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-11_1_3_line_20 |  | 17 | 19 | 0.00042697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-11_1_3_line_21 |  | 18 | 20 | 0.026034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-11_1_3_line_22 |  | 18 | 21 | 0.03905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-11_1_3_line_23 |  | 18 | 22 | 0.018237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-11_1_3_line_24 |  | 19 | 23 | 0.024086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-11_1_3_line_25 |  | 20 | 49 | 0.016279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-11_1_3_line_26 |  | 20 | 50 | 0.052696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-11_1_3_line_27 |  | 21 | 51 | 0.0013349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-11_1_3_line_28 |  | 23 | 109 | 0.0024579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-11_1_3_line_29 |  | 24 | 25 | 0.024749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_2325-11_1_3_line_30 |  | 24 | 26 | 0.031627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_2325-11_1_3_line_31 |  | 25 | 27 | 0.026402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_2325-11_1_3_line_32 |  | 26 | 28 | 0.0052992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-11_1_3_line_33 |  | 27 | 29 | 0.0092518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_2325-11_1_3_line_34 |  | 28 | 30 | 0.039349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-11_1_3_line_35 |  | 29 | 31 | 0.022275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_2325-11_1_3_line_36 |  | 30 | 32 | 0.011886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-11_1_3_line_37 |  | 31 | 92 | 0.022969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_2325-11_1_3_line_38 |  | 32 | 36 | 0.040799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-11_1_3_line_39 |  | 32 | 33 | 0.046675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-11_1_3_line_40 |  | 33 | 34 | 0.014674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-11_1_3_line_41 |  | 34 | 35 | 0.034986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-11_1_3_line_42 |  | 36 | 37 | 0.029758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-11_1_3_line_43 |  | 37 | 96 | 0.022626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-11_1_3_line_44 |  | 37 | 94 | 0.039283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-11_1_3_line_45 |  | 38 | 39 | 0.023389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_2325-11_1_3_line_46 |  | 38 | 40 | 0.014978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2325-11_1_3_line_47 |  | 39 | 41 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2325-11_1_3_line_48 |  | 40 | 42 | 0.0068625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2325-11_1_3_line_49 |  | 40 | 43 | 0.022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-11_1_3_line_50 |  | 41 | 44 | 0.02206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2325-11_1_3_line_51 |  | 42 | 45 | 0.018906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_2325-11_1_3_line_52 |  | 43 | 46 | 0.014748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2325-11_1_3_line_53 |  | 44 | 47 | 0.031606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2325-11_1_3_line_54 |  | 45 | 48 | 0.023164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_2325-11_1_3_line_55 |  | 47 | 65 | 0.034517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_2325-11_1_3_line_56 |  | 47 | 66 | 0.037786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2325-11_1_3_line_57 |  | 48 | 135 | 0.010521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_2325-11_1_3_line_58 |  | 50 | 60 | 0.0033065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2325-11_1_3_line_59 |  | 51 | 52 | 0.023671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2325-11_1_3_line_60 |  | 52 | 124 | 0.027359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2325-11_1_3_line_61 |  | 53 | 54 | 0.012403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2325-11_1_3_line_62 |  | 53 | 55 | 0.015098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2325-11_1_3_line_63 |  | 54 | 56 | 0.033598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2325-11_1_3_line_64 |  | 56 | 57 | 0.040076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2325-11_1_3_line_65 |  | 57 | 58 | 0.053553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-11_1_3_line_66 |  | 58 | 91 | 0.04078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2325-11_1_3_line_67 |  | 59 | 60 | 0.035979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_2325-11_1_3_line_68 |  | 59 | 61 | 0.025122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2325-11_1_3_line_69 |  | 61 | 62 | 0.0067529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_2325-11_1_3_line_70 |  | 62 | 63 | 0.046833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_2325-11_1_3_line_71 |  | 62 | 64 | 0.025344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2325-11_1_3_line_72 |  | 63 | 110 | 0.030546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2325-11_1_3_line_73 |  | 63 | 111 | 0.029141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2325-11_1_3_line_74 |  | 64 | 112 | 0.011505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2325-11_1_3_line_75 |  | 65 | 67 | 0.038689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_2325-11_1_3_line_76 |  | 66 | 68 | 0.04127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_2325-11_1_3_line_77 |  | 67 | 69 | 0.0097327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2325-11_1_3_line_78 |  | 68 | 70 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_2325-11_1_3_line_79 |  | 69 | 71 | 0.017429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2325-11_1_3_line_80 |  | 70 | 125 | 0.0039078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_2325-11_1_3_line_81 |  | 71 | 133 | 0.002615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2325-11_1_3_line_82 |  | 72 | 73 | 0.017545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2325-11_1_3_line_83 |  | 72 | 74 | 0.019423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2325-11_1_3_line_84 |  | 72 | 75 | 0.072983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2325-11_1_3_line_85 |  | 73 | 76 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2325-11_1_3_line_86 |  | 74 | 77 | 0.0075164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2325-11_1_3_line_87 |  | 75 | 80 | 0.013613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2325-11_1_3_line_88 |  | 76 | 78 | 0.015668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2325-11_1_3_line_89 |  | 77 | 79 | 0.01755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2325-11_1_3_line_90 |  | 79 | 115 | 0.0066242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2325-11_1_3_line_91 |  | 80 | 81 | 0.012565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2325-11_1_3_line_92 |  | 81 | 101 | 0.0081574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2325-11_1_3_line_93 |  | 82 | 83 | 0.021643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2325-11_1_3_line_94 |  | 82 | 84 | 0.021569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2325-11_1_3_line_95 |  | 83 | 85 | 0.011808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2325-11_1_3_line_96 |  | 85 | 86 | 0.01787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2325-11_1_3_line_97 |  | 86 | 89 | 0.0051633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2325-11_1_3_line_98 |  | 86 | 90 | 0.026135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2325-11_1_3_line_99 |  | 87 | 88 | 0.029937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2325-11_1_3_line_100 |  | 88 | 116 | 0.027714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2325-11_1_3_line_101 |  | 90 | 107 | 0.0092921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2325-11_1_3_line_102 |  | 91 | 92 | 0.011524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2325-11_1_3_line_103 |  | 91 | 93 | 0.020106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_2325-11_1_3_line_104 |  | 93 | 136 | 0.021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_2325-11_1_3_line_105 |  | 97 | 98 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2325-11_1_3_line_106 |  | 97 | 99 | 0.0060812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2325-11_1_3_line_107 |  | 98 | 100 | 0.011214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2325-11_1_3_line_108 |  | 99 | 101 | 0.017219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2325-11_1_3_line_109 |  | 100 | 102 | 0.06164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2325-11_1_3_line_110 |  | 102 | 120 | 0.016242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2325-11_1_3_line_111 |  | 103 | 104 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2325-11_1_3_line_112 |  | 103 | 105 | 0.0077527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2325-11_1_3_line_113 |  | 104 | 106 | 0.018338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2325-11_1_3_line_114 |  | 106 | 107 | 0.0056302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2325-11_1_3_line_115 |  | 106 | 108 | 0.016108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2325-11_1_3_line_116 |  | 108 | 109 | 0.029369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2325-11_1_3_line_117 |  | 110 | 113 | 0.019903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_2325-11_1_3_line_118 |  | 112 | 114 | 0.02325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2325-11_1_3_line_119 |  | 113 | 132 | 0.011738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_2325-11_1_3_line_120 |  | 114 | 138 | 0.023913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2325-11_1_3_line_121 |  | 116 | 117 | 0.024964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2325-11_1_3_line_122 |  | 117 | 121 | 0.035082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2325-11_1_3_line_123 |  | 118 | 119 | 0.19032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2325-11_1_3_line_124 |  | 119 | 120 | 0.088635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2325-11_1_3_line_125 |  | 121 | 122 | 0.029619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2325-11_1_3_line_126 |  | 122 | 123 | 0.00055663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2325-11_1_3_line_127 |  | 123 | 124 | 1.0754e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2325-11_1_3_line_128 |  | 125 | 126 | 0.027671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_2325-11_1_3_line_129 |  | 126 | 127 | 0.027764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_2325-11_1_3_line_130 |  | 127 | 128 | 0.029516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_2325-11_1_3_line_131 |  | 128 | 129 | 0.0026564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
132 | LV_2325-11_1_3_line_132 |  | 129 | 130 | 0.025418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_2325-11_1_3_line_133 |  | 130 | 131 | 0.0099152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
134 | LV_2325-11_1_3_line_134 |  | 131 | 132 | 0.017989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
135 | LV_2325-11_1_3_line_135 |  | 133 | 134 | 0.020371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2325-11_1_3_line_136 |  | 134 | 137 | 0.006402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2325-11_1_3_line_137 |  | 135 | 136 | 0.020663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-11_1_3_trafo_137 | 0.63 MVA 20/0.4 kV | 139 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2563804.6132 | 1152466.93 | 2563779.8797 | 1152662.5005
1 | 2563804.6132 | 1152466.93 | 2563812.07 | 1152441.1497 | 2563812.4254 | 1152440.2916 | 2563815.9497 | 1152431.7216 | 2563819.8017 | 1152424.0611 | 2563824.5036 | 1152414.1715
2 | 2563635.7069 | 1151983.1348 | 2563824.5036 | 1152414.1715
3 | 2563467.1516 | 1151933.9073 | 2563635.7069 | 1151983.1348
4 | 2563097.5233 | 1152077.4187 | 2563084.7519 | 1152091.3466
5 | 2563097.5233 | 1152077.4187 | 2563101.4866 | 1152073.0965 | 2563101.4866 | 1152073.0965
6 | 2563083.0545 | 1152093.1977 | 2563084.7519 | 1152091.3466
7 | 2563129.8088 | 1152063.918 | 2563116.7161 | 1152065.0434 | 2563109.0082 | 1152067.0139 | 2563101.4866 | 1152073.0965
8 | 2563065.996 | 1152103.3077 | 2563076.8074 | 1152098.1275 | 2563083.0545 | 1152093.1977
9 | 2563129.8088 | 1152063.918 | 2563129.7044 | 1152043.5233
10 | 2563129.8088 | 1152063.918 | 2563134.7136 | 1152064.0991 | 2563154.5116 | 1152065.1893
11 | 2563065.996 | 1152103.3077 | 2563055.4907 | 1152104.6286 | 2563051.7101 | 1152104.9219
12 | 2563065.996 | 1152103.3077 | 2563064.9232 | 1152124.8308
13 | 2563123.887 | 1152025.5904 | 2563129.6546 | 1152033.8036 | 2563129.7044 | 1152043.5233
14 | 2563154.5116 | 1152065.1893 | 2563173.4822 | 1152065.3198
15 | 2563154.5116 | 1152065.1893 | 2563158.4905 | 1152045.5201
16 | 2563475.9802 | 1151606.2612 | 2563502.2946 | 1151618.1807
17 | 2563475.9802 | 1151606.2612 | 2563471.8814 | 1151604.4046
18 | 2563502.2946 | 1151618.1807 | 2563507.4602 | 1151620.5205
19 | 2563451.7366 | 1151595.2797 | 2563471.8814 | 1151604.4046
20 | 2563507.8491 | 1151620.6967 | 2563507.4602 | 1151620.5205
21 | 2563451.7366 | 1151595.2797 | 2563442.0526 | 1151619.4508
22 | 2563451.7366 | 1151595.2797 | 2563465.1646 | 1151558.6108
23 | 2563435.1131 | 1151587.6769 | 2563451.7366 | 1151595.2797
24 | 2563529.789 | 1151630.6347 | 2563507.8491 | 1151620.6967
25 | 2563426.7683 | 1151613.7298 | 2563442.0526 | 1151619.4508
26 | 2563442.0526 | 1151619.4508 | 2563448.7023 | 1151671.7258
27 | 2563465.6236 | 1151557.3573 | 2563465.1646 | 1151558.6108
28 | 2563532.0279 | 1151631.6488 | 2563529.789 | 1151630.6347
29 | 2563313.456 | 1151993.5514 | 2563314.7359 | 1151989.5481 | 2563320.2729 | 1151969.7621
30 | 2563303.8247 | 1152023.6765 | 2563313.456 | 1151993.5514
31 | 2563327.3882 | 1151944.3365 | 2563320.2729 | 1151969.7621
32 | 2563303.8247 | 1152023.6765 | 2563299.4753 | 1152026.7038
33 | 2563327.3882 | 1151944.3365 | 2563329.8815 | 1151935.4269
34 | 2563272.0054 | 1152052.1187 | 2563271.8008 | 1152047.5177 | 2563275.8031 | 1152043.1799 | 2563299.4753 | 1152026.7038
35 | 2563337.0338 | 1151914.3771 | 2563333.2561 | 1151923.3681 | 2563329.8815 | 1151935.4269
36 | 2563272.0054 | 1152052.1187 | 2563273.6966 | 1152063.881
37 | 2563345.0803 | 1151892.9027 | 2563343.0292 | 1151900.1078 | 2563337.0338 | 1151914.3771
38 | 2563273.6966 | 1152063.881 | 2563233.3982 | 1152070.2513
39 | 2563273.6966 | 1152063.881 | 2563278.3187 | 1152066.7765 | 2563287.4018 | 1152070.056 | 2563291.1942 | 1152074.057 | 2563304.6191 | 1152096.3824
40 | 2563312.181 | 1152108.9577 | 2563304.6191 | 1152096.3824
41 | 2563312.181 | 1152108.9577 | 2563345.5949 | 1152098.5871
42 | 2563212.6293 | 1152063.0654 | 2563214.2191 | 1152073.2831 | 2563233.3982 | 1152070.2513
43 | 2563213.88 | 1152040.4796 | 2563212.6293 | 1152063.0654
44 | 2563212.6293 | 1152063.0654 | 2563206.075 | 1152064.195 | 2563197.224 | 1152064.994 | 2563177.573 | 1152065.348 | 2563173.4822 | 1152065.3198
45 | 2563488.4666 | 1151880.401 | 2563478.6653 | 1151890.2878 | 2563469.8808 | 1151893.8174
46 | 2563455.6698 | 1151898.543 | 2563469.226 | 1151894.0805 | 2563469.8808 | 1151893.8174
47 | 2563493.3227 | 1151868.7656 | 2563493.754 | 1151874.0768 | 2563488.4666 | 1151880.401 | 2563488.4666 | 1151880.401
48 | 2563455.6698 | 1151898.543 | 2563450.6252 | 1151893.8905
49 | 2563455.6698 | 1151898.543 | 2563457.7554 | 1151903.2994 | 2563462.0043 | 1151916.747 | 2563462.9143 | 1151919.7807
50 | 2563472.3834 | 1151861.8227 | 2563493.3227 | 1151868.7656
51 | 2563450.6252 | 1151893.8905 | 2563447.2036 | 1151890.735 | 2563437.8851 | 1151885.3667 | 2563434.6586 | 1151884.0179
52 | 2563467.1516 | 1151933.9073 | 2563462.9143 | 1151919.7807
53 | 2563472.3834 | 1151861.8227 | 2563489.8169 | 1151835.4601
54 | 2563413.2871 | 1151875.0836 | 2563434.6586 | 1151884.0179
55 | 2563457.7215 | 1151822.7597 | 2563489.8169 | 1151835.4601
56 | 2563489.8169 | 1151835.4601 | 2563511.3678 | 1151843.9878 | 2563516.9536 | 1151845.0656 | 2563522.1004 | 1151843.3668 | 2563525.0091 | 1151841.4187
57 | 2563403.5493 | 1151871.1039 | 2563405.4632 | 1151871.8128 | 2563413.2871 | 1151875.0836
58 | 2563448.7023 | 1151671.7258 | 2563451.7023 | 1151673.1162
59 | 2563465.6236 | 1151557.3573 | 2563470.7984 | 1151543.2262 | 2563474.2961 | 1151535.3454
60 | 2563499.0907 | 1151539.7671 | 2563483.2443 | 1151532.7341 | 2563478.613 | 1151532.1731 | 2563474.2961 | 1151535.3454 | 2563474.2961 | 1151535.3454
61 | 2563278.4325 | 1151743.8542 | 2563270.1519 | 1151734.6207
62 | 2563260.0715 | 1151723.3804 | 2563270.1519 | 1151734.6207
63 | 2563278.4325 | 1151743.8542 | 2563300.8641 | 1151768.8672
64 | 2563300.8641 | 1151768.8672 | 2563302.7561 | 1151770.977 | 2563305.8951 | 1151778.5283 | 2563304.396 | 1151786.8973 | 2563300.7443 | 1151807.1328
65 | 2563329.1741 | 1151845.5646 | 2563322.8229 | 1151833.5084 | 2563318.749 | 1151828.6753 | 2563313.5776 | 1151826.339 | 2563300.8108 | 1151820.5918 | 2563299.2245 | 1151817.2109 | 2563300.0238 | 1151811.1252 | 2563300.7443 | 1151807.1328
66 | 2563329.1741 | 1151845.5646 | 2563344.1282 | 1151873.9656 | 2563347.9975 | 1151881.757
67 | 2563484.3462 | 1151688.2454 | 2563451.7023 | 1151673.1162
68 | 2563484.3462 | 1151688.2454 | 2563507.1388 | 1151698.809
69 | 2563513.2657 | 1151701.6485 | 2563507.1388 | 1151698.809
70 | 2563513.2657 | 1151701.6485 | 2563469.0337 | 1151717.4031
71 | 2563513.2657 | 1151701.6485 | 2563536.4471 | 1151711.8914
72 | 2563469.0337 | 1151717.4031 | 2563456.6969 | 1151721.8026 | 2563440.2487 | 1151727.6257
73 | 2563469.0337 | 1151717.4031 | 2563473.4656 | 1151723.0679 | 2563493.8285 | 1151731.2595
74 | 2563536.4471 | 1151711.8914 | 2563546.9704 | 1151716.5412
75 | 2563421.7465 | 1151808.5242 | 2563457.7215 | 1151822.7597
76 | 2563525.0091 | 1151841.4187 | 2563533.206 | 1151835.9289 | 2563548.4586 | 1151821.3845 | 2563555.2948 | 1151813.6411
77 | 2563421.7465 | 1151808.5242 | 2563412.6966 | 1151804.9432
78 | 2563564.4037 | 1151803.3231 | 2563555.2948 | 1151813.6411
79 | 2563396.4903 | 1151798.5303 | 2563412.6966 | 1151804.9432
80 | 2563564.4037 | 1151803.3231 | 2563560.8678 | 1151801.6594
81 | 2563396.4903 | 1151798.5303 | 2563395.6075 | 1151800.9924
82 | 2563164.9837 | 1152013.421 | 2563168.462 | 1151996.2243
83 | 2563152.9264 | 1151986.6913 | 2563153.9153 | 1151986.7753 | 2563161.616 | 1151988.5957 | 2563166.1717 | 1151991.9139 | 2563168.462 | 1151996.2243
84 | 2563168.462 | 1151996.2243 | 2563224.9676 | 1151950.0324
85 | 2563164.9837 | 1152013.421 | 2563161.597 | 1152030.1629
86 | 2563152.9264 | 1151986.6913 | 2563145.437 | 1151986.0551
87 | 2563224.9676 | 1151950.0324 | 2563228.0867 | 1151936.7813
88 | 2563158.4905 | 1152045.5201 | 2563161.597 | 1152030.1629
89 | 2563127.9501 | 1151984.5697 | 2563145.437 | 1151986.0551
90 | 2563127.9501 | 1151984.5697 | 2563121.3497 | 1151984.009
91 | 2563230.9847 | 1151924.5552 | 2563230.51 | 1151926.4866 | 2563228.0867 | 1151936.7813
92 | 2563230.9847 | 1151924.5552 | 2563232.932 | 1151916.6337
93 | 2563637.3935 | 1151659.0317 | 2563657.407 | 1151650.7935 | 2563657.407 | 1151650.7935
94 | 2563657.407 | 1151650.7935 | 2563662.1099 | 1151645.4624 | 2563665.7991 | 1151636.202 | 2563666.7742 | 1151631.8172
95 | 2563626.4748 | 1151663.5262 | 2563637.3935 | 1151659.0317
96 | 2563609.592 | 1151669.359 | 2563622.9804 | 1151664.9646 | 2563626.4748 | 1151663.5262
97 | 2563609.592 | 1151669.359 | 2563604.6862 | 1151670.9691
98 | 2563609.592 | 1151669.359 | 2563604.0522 | 1151664.4901 | 2563587.0094 | 1151656.6496
99 | 2563634.2497 | 1151599.7533 | 2563606.8866 | 1151587.6091
100 | 2563581.5555 | 1151576.3666 | 2563606.8866 | 1151587.6091
101 | 2563578.5677 | 1151652.766 | 2563587.0094 | 1151656.6496
102 | 2563347.9975 | 1151881.757 | 2563346.7182 | 1151887.1565 | 2563345.0803 | 1151892.9027
103 | 2563347.9975 | 1151881.757 | 2563357.6918 | 1151878.2628 | 2563364.7764 | 1151871.4905
104 | 2563384.1727 | 1151863.9274 | 2563379.5909 | 1151863.8775 | 2563376.8413 | 1151866.0398 | 2563371.2265 | 1151866.4854 | 2563366.9849 | 1151869.3794 | 2563364.7764 | 1151871.4905
105 | 2563244.0214 | 1151871.5227 | 2563238.4941 | 1151894.0075
106 | 2563237.0424 | 1151899.9129 | 2563238.4941 | 1151894.0075
107 | 2563247.0137 | 1151860.7188 | 2563245.0811 | 1151867.2117 | 2563244.0214 | 1151871.5227
108 | 2563237.0424 | 1151899.9129 | 2563232.932 | 1151916.6337
109 | 2563200.0099 | 1151820.8419 | 2563247.0137 | 1151860.7188
110 | 2563200.0099 | 1151820.8419 | 2563197.9545 | 1151808.5371 | 2563197.9314 | 1151804.7705
111 | 2563581.6357 | 1151634.0017 | 2563587.7304 | 1151621.7785 | 2563589.101 | 1151617.468
112 | 2563587.1062 | 1151609.9763 | 2563589.101 | 1151617.468
113 | 2563573.4528 | 1151650.4129 | 2563581.6357 | 1151634.0017
114 | 2563573.4528 | 1151650.4129 | 2563578.5677 | 1151652.766
115 | 2563573.4528 | 1151650.4129 | 2563558.7802 | 1151643.7667
116 | 2563532.0279 | 1151631.6488 | 2563558.7802 | 1151643.7667
117 | 2563422.7282 | 1151736.6613 | 2563430.7212 | 1151730.9986 | 2563440.2487 | 1151727.6257
118 | 2563546.9704 | 1151716.5412 | 2563568.2365 | 1151725.9377
119 | 2563422.7282 | 1151736.6613 | 2563433.3491 | 1151741.6587
120 | 2563590.1091 | 1151735.6022 | 2563568.2365 | 1151725.9377
121 | 2563581.5555 | 1151576.3666 | 2563558.7383 | 1151566.2399
122 | 2563526.6725 | 1151552.0084 | 2563558.7383 | 1151566.2399
123 | 2563139.4243 | 1151738.1889 | 2563115.8048 | 1151549.3426
124 | 2563197.9314 | 1151804.7705 | 2563139.4243 | 1151738.1889
125 | 2563526.6725 | 1151552.0084 | 2563499.5996 | 1151539.9929
126 | 2563499.5996 | 1151539.9929 | 2563499.0908 | 1151539.7671
127 | 2563499.0908 | 1151539.7671 | 2563499.0907 | 1151539.7671
128 | 2563535.8301 | 1151789.8785 | 2563560.8678 | 1151801.6594
129 | 2563510.7082 | 1151778.0581 | 2563535.8301 | 1151789.8785
130 | 2563484.0011 | 1151765.4917 | 2563510.7082 | 1151778.0581
131 | 2563484.0011 | 1151765.4917 | 2563481.5975 | 1151764.3608
132 | 2563458.5984 | 1151753.5391 | 2563481.5975 | 1151764.3608
133 | 2563449.6267 | 1151749.3177 | 2563458.5984 | 1151753.5391
134 | 2563449.6267 | 1151749.3177 | 2563433.3491 | 1151741.6587
135 | 2563395.6075 | 1151800.9924 | 2563386.7319 | 1151792.7868 | 2563383.5312 | 1151785.1469
136 | 2563384.6746 | 1151778.8478 | 2563384.6746 | 1151778.8478 | 2563383.5312 | 1151785.1469
137 | 2563384.1727 | 1151863.9274 | 2563403.5493 | 1151871.1039

## bus_geodata
| x | y | coords
0 | 2563779.8797 | 1152662.5005
1 | 2563804.6132 | 1152466.93
2 | 2563824.5036 | 1152414.1715
3 | 2563635.7069 | 1151983.1348
4 | 2563097.5233 | 1152077.4187
5 | 2563084.7519 | 1152091.3466
6 | 2563101.4866 | 1152073.0965
7 | 2563083.0545 | 1152093.1977
8 | 2563129.8088 | 1152063.918
9 | 2563065.996 | 1152103.3077
10 | 2563129.7044 | 1152043.5233
11 | 2563154.5116 | 1152065.1893
12 | 2563051.7101 | 1152104.9219
13 | 2563064.9232 | 1152124.8308
14 | 2563475.9802 | 1151606.2612
15 | 2563502.2946 | 1151618.1807
16 | 2563471.8814 | 1151604.4046
17 | 2563507.4602 | 1151620.5205
18 | 2563451.7366 | 1151595.2797
19 | 2563507.8491 | 1151620.6967
20 | 2563442.0526 | 1151619.4508
21 | 2563465.1646 | 1151558.6108
22 | 2563435.1131 | 1151587.6769
23 | 2563529.789 | 1151630.6347
24 | 2563313.456 | 1151993.5514
25 | 2563320.2729 | 1151969.7621
26 | 2563303.8247 | 1152023.6765
27 | 2563327.3882 | 1151944.3365
28 | 2563299.4753 | 1152026.7038
29 | 2563329.8815 | 1151935.4269
30 | 2563272.0054 | 1152052.1187
31 | 2563337.0338 | 1151914.3771
32 | 2563273.6966 | 1152063.881
33 | 2563304.6191 | 1152096.3824
34 | 2563312.181 | 1152108.9577
35 | 2563345.5949 | 1152098.5871
36 | 2563233.3982 | 1152070.2513
37 | 2563212.6293 | 1152063.0654
38 | 2563469.8808 | 1151893.8174
39 | 2563488.4666 | 1151880.401
40 | 2563455.6698 | 1151898.543
41 | 2563493.3227 | 1151868.7656
42 | 2563450.6252 | 1151893.8905
43 | 2563462.9143 | 1151919.7807
44 | 2563472.3834 | 1151861.8227
45 | 2563434.6586 | 1151884.0179
46 | 2563467.1516 | 1151933.9073
47 | 2563489.8169 | 1151835.4601
48 | 2563413.2871 | 1151875.0836
49 | 2563426.7683 | 1151613.7298
50 | 2563448.7023 | 1151671.7258
51 | 2563465.6236 | 1151557.3573
52 | 2563474.2961 | 1151535.3454
53 | 2563270.1519 | 1151734.6207
54 | 2563278.4325 | 1151743.8542
55 | 2563260.0715 | 1151723.3804
56 | 2563300.8641 | 1151768.8672
57 | 2563300.7443 | 1151807.1328
58 | 2563329.1741 | 1151845.5646
59 | 2563484.3462 | 1151688.2454
60 | 2563451.7023 | 1151673.1162
61 | 2563507.1388 | 1151698.809
62 | 2563513.2657 | 1151701.6485
63 | 2563469.0337 | 1151717.4031
64 | 2563536.4471 | 1151711.8914
65 | 2563457.7215 | 1151822.7597
66 | 2563525.0091 | 1151841.4187
67 | 2563421.7465 | 1151808.5242
68 | 2563555.2948 | 1151813.6411
69 | 2563412.6966 | 1151804.9432
70 | 2563564.4037 | 1151803.3231
71 | 2563396.4903 | 1151798.5303
72 | 2563168.462 | 1151996.2243
73 | 2563164.9837 | 1152013.421
74 | 2563152.9264 | 1151986.6913
75 | 2563224.9676 | 1151950.0324
76 | 2563161.597 | 1152030.1629
77 | 2563145.437 | 1151986.0551
78 | 2563158.4905 | 1152045.5201
79 | 2563127.9501 | 1151984.5697
80 | 2563228.0867 | 1151936.7813
81 | 2563230.9847 | 1151924.5552
82 | 2563657.407 | 1151650.7935
83 | 2563637.3935 | 1151659.0317
84 | 2563666.7742 | 1151631.8172
85 | 2563626.4748 | 1151663.5262
86 | 2563609.592 | 1151669.359
87 | 2563634.2497 | 1151599.7533
88 | 2563606.8866 | 1151587.6091
89 | 2563604.6862 | 1151670.9691
90 | 2563587.0094 | 1151656.6496
91 | 2563347.9975 | 1151881.757
92 | 2563345.0803 | 1151892.9027
93 | 2563364.7764 | 1151871.4906
94 | 2563173.4822 | 1152065.3198
95 | 2563123.887 | 1152025.5904
96 | 2563213.88 | 1152040.4796
97 | 2563238.4941 | 1151894.0075
98 | 2563244.0214 | 1151871.5227
99 | 2563237.0424 | 1151899.9129
100 | 2563247.0137 | 1151860.7188
101 | 2563232.932 | 1151916.6337
102 | 2563200.0099 | 1151820.8419
103 | 2563589.101 | 1151617.468
104 | 2563581.6357 | 1151634.0017
105 | 2563587.1062 | 1151609.9763
106 | 2563573.4528 | 1151650.4129
107 | 2563578.5677 | 1151652.766
108 | 2563558.7802 | 1151643.7667
109 | 2563532.0279 | 1151631.6488
110 | 2563440.2487 | 1151727.6257
111 | 2563493.8285 | 1151731.2595
112 | 2563546.9704 | 1151716.5412
113 | 2563422.7282 | 1151736.6613
114 | 2563568.2365 | 1151725.9377
115 | 2563121.3497 | 1151984.009
116 | 2563581.5555 | 1151576.3666
117 | 2563558.7383 | 1151566.2399
118 | 2563115.8048 | 1151549.3426
119 | 2563139.4243 | 1151738.1889
120 | 2563197.9314 | 1151804.7705
121 | 2563526.6725 | 1151552.0084
122 | 2563499.5996 | 1151539.9929
123 | 2563499.0908 | 1151539.7671
124 | 2563499.0907 | 1151539.7671
125 | 2563560.8678 | 1151801.6594
126 | 2563535.8301 | 1151789.8785
127 | 2563510.7082 | 1151778.0581
128 | 2563484.0011 | 1151765.4917
129 | 2563481.5975 | 1151764.3608
130 | 2563458.5984 | 1151753.5391
131 | 2563449.6267 | 1151749.3177
132 | 2563433.3491 | 1151741.6587
133 | 2563395.6075 | 1151800.9924
134 | 2563383.5312 | 1151785.1469
135 | 2563403.5493 | 1151871.1039
136 | 2563384.1727 | 1151863.9274
137 | 2563384.6746 | 1151778.8478
138 | 2563590.1091 | 1151735.6022
139 | 2563396.4903 | 1151798.5303

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98602 | -0.26749 | 0.0021852 | 0.00054767
1 | 0.98642 | -0.25975 | 0 | 0
2 | 0.98653 | -0.25753 | 0.0021719 | 0.00054433
3 | 0.98841 | -0.22075 | 0.0012859 | 0.00032226
4 | 0.97402 | -0.50048 | 0.0015413 | 0.00038628
5 | 0.97394 | -0.50214 | 0.0014972 | 0.00037524
6 | 0.97406 | -0.4998 | 0.00092839 | 0.00023268
7 | 0.97393 | -0.50229 | 0.0012438 | 0.00031173
8 | 0.97426 | -0.49571 | 0 | 0
9 | 0.97389 | -0.50303 | 0 | 0
10 | 0.9742 | -0.49687 | 0.0016135 | 0.00040438
11 | 0.9745 | -0.49102 | 0 | 0
12 | 0.97388 | -0.50335 | 0.0012142 | 0.00030431
13 | 0.97388 | -0.50335 | 0.00081382 | 0.00020396
14 | 0.97406 | -0.49905 | 0.00096993 | 0.00024309
15 | 0.97299 | -0.52018 | 0.00094241 | 0.00023619
16 | 0.97423 | -0.49568 | 0.00076151 | 0.00019085
17 | 0.97278 | -0.52424 | 0.0037566 | 0.00094149
18 | 0.97509 | -0.47884 | 0 | 0
19 | 0.97277 | -0.52451 | 0.0031183 | 0.00078153
20 | 0.97638 | -0.45353 | 0 | 0
21 | 0.97473 | -0.48596 | 0.00060478 | 0.00015157
22 | 0.97506 | -0.4794 | 0.0016694 | 0.0004184
23 | 0.97205 | -0.5387 | 0.0034601 | 0.00086718
24 | 0.98257 | -0.33322 | 0.0027232 | 0.00068249
25 | 0.98316 | -0.32195 | 0.0016067 | 0.00040269
26 | 0.98187 | -0.34686 | 0 | 0
27 | 0.9838 | -0.30956 | 0.0013701 | 0.00034338
28 | 0.98164 | -0.35144 | 0.00059278 | 0.00014856
29 | 0.98403 | -0.3051 | 0.0027393 | 0.00068653
30 | 0.97991 | -0.38507 | 0 | 0
31 | 0.98461 | -0.29384 | 0.0055709 | 0.0013962
32 | 0.97939 | -0.39525 | 0 | 0
33 | 0.97921 | -0.39876 | 0.0021 | 0.00052631
34 | 0.97918 | -0.3993 | 0.00086115 | 0.00021582
35 | 0.97914 | -0.40005 | 0.0011725 | 0.00029385
36 | 0.97775 | -0.4272 | 0.0010033 | 0.00025145
37 | 0.97659 | -0.45002 | 0 | 0
38 | 0.99017 | -0.18665 | 0.0020443 | 0.00051234
39 | 0.9911 | -0.16886 | 0.0015312 | 0.00038376
40 | 0.98959 | -0.19779 | 0 | 0
41 | 0.99165 | -0.15837 | 0.00095506 | 0.00023936
42 | 0.98935 | -0.20238 | 0.00075085 | 0.00018818
43 | 0.98942 | -0.20115 | 0.0013456 | 0.00033723
44 | 0.99255 | -0.14116 | 0.0006664 | 0.00016701
45 | 0.9887 | -0.21492 | 0.0017756 | 0.00044501
46 | 0.98932 | -0.20301 | 0.0013929 | 0.00034908
47 | 0.99385 | -0.11637 | 0.00060933 | 0.00015271
48 | 0.98792 | -0.22993 | 0.0026942 | 0.00067524
49 | 0.97636 | -0.45375 | 0.00073065 | 0.00018312
50 | 0.97902 | -0.40179 | 0.00057523 | 0.00014417
51 | 0.97471 | -0.48619 | 0.00068792 | 0.00017241
52 | 0.97452 | -0.48994 | 0.00087925 | 0.00022036
53 | 0.98482 | -0.28987 | 0.00080187 | 0.00020097
54 | 0.98484 | -0.28948 | 0.0016528 | 0.00041423
55 | 0.98481 | -0.29012 | 0.00092292 | 0.0002313
56 | 0.98495 | -0.28744 | 0.0013772 | 0.00034516
57 | 0.98512 | -0.28402 | 0.00073761 | 0.00018486
58 | 0.98539 | -0.27873 | 0 | 0
59 | 0.98013 | -0.3803 | 0.00067402 | 0.00016893
60 | 0.97919 | -0.39852 | 0.0013495 | 0.00033821
61 | 0.98079 | -0.36745 | 0.0024861 | 0.00062308
62 | 0.98097 | -0.36384 | 0 | 0
63 | 0.98246 | -0.33502 | 0.0013874 | 0.00034771
64 | 0.98076 | -0.36803 | 0.002383 | 0.00059724
65 | 0.99674 | -0.061491 | 0.0010688 | 0.00026787
66 | 0.99224 | -0.14685 | 0.0027354 | 0.00068556
67 | 1 | 0 | -0.19049 | -0.04869
68 | 0.99055 | -0.17926 | 0.0014147 | 0.00035455
69 | 0.99997 | -0.00060315 | 0.00071298 | 0.00017869
70 | 0.98999 | -0.18992 | 0 | 0
71 | 0.99992 | -0.0014666 | 0 | 0
72 | 0.97286 | -0.52343 | 0.00092328 | 0.0002314
73 | 0.97324 | -0.51576 | 0 | 0
74 | 0.97274 | -0.52574 | 0.0015133 | 0.00037928
75 | 0.97174 | -0.5455 | 0.0014372 | 0.0003602
76 | 0.97362 | -0.50829 | 0.0016164 | 0.00040511
77 | 0.9727 | -0.52642 | 0.0014419 | 0.00036137
78 | 0.97399 | -0.50097 | 0.0016154 | 0.00040487
79 | 0.97265 | -0.52755 | 0.00206 | 0.00051628
80 | 0.97155 | -0.54927 | 0.0033951 | 0.00085089
81 | 0.97141 | -0.55195 | 0.001053 | 0.0002639
82 | 0.97031 | -0.57312 | 0.0023672 | 0.00059328
83 | 0.97039 | -0.57158 | 0.0017025 | 0.00042668
84 | 0.97028 | -0.57371 | 0.0014755 | 0.0003698
85 | 0.97045 | -0.57037 | 0.00092794 | 0.00023256
86 | 0.97056 | -0.56823 | 0 | 0
87 | 0.97393 | -0.50174 | 0.00088577 | 0.000222
88 | 0.97395 | -0.50125 | 0.00092391 | 0.00023155
89 | 0.97054 | -0.56851 | 0.0029226 | 0.00073247
90 | 0.97079 | -0.56369 | 0.0047993 | 0.0012028
91 | 0.9856 | -0.27471 | 0 | 0
92 | 0.98527 | -0.2811 | 0 | 0
93 | 0.98623 | -0.26258 | 0.001186 | 0.00029725
94 | 0.97516 | -0.47802 | 0.0015912 | 0.0003988
95 | 0.97418 | -0.49741 | 0.0014892 | 0.00037322
96 | 0.97652 | -0.45129 | 0.0030721 | 0.00076995
97 | 0.97117 | -0.5568 | 0.00098369 | 0.00024654
98 | 0.97105 | -0.55921 | 0.0013516 | 0.00033875
99 | 0.97121 | -0.55606 | 0.0013288 | 0.00033302
100 | 0.971 | -0.5601 | 0 | 0
101 | 0.97133 | -0.55353 | 0.002575 | 0.00064536
102 | 0.97076 | -0.56497 | 0 | 0
103 | 0.97086 | -0.56223 | 0.0009113 | 0.00022839
104 | 0.9709 | -0.56135 | 0.0025358 | 0.00063552
105 | 0.97085 | -0.56248 | 0.0017266 | 0.00043274
106 | 0.97099 | -0.55959 | 0 | 0
107 | 0.97091 | -0.56125 | 0.0017198 | 0.00043102
108 | 0.97131 | -0.55331 | 0.0034767 | 0.00087135
109 | 0.97198 | -0.53999 | 0.0039215 | 0.00098281
110 | 0.98347 | -0.3154 | 0.0030811 | 0.00077221
111 | 0.98241 | -0.33594 | 0.0017596 | 0.000441
112 | 0.98069 | -0.36944 | 0.0024219 | 0.00060699
113 | 0.98416 | -0.30208 | 0 | 0
114 | 0.98059 | -0.37126 | 0.0021913 | 0.0005492
115 | 0.97264 | -0.52772 | 0.0014293 | 0.00035821
116 | 0.974 | -0.50033 | 0.00082114 | 0.0002058
117 | 0.97406 | -0.49912 | 0.0014597 | 0.00036583
118 | 0.97014 | -0.57721 | 0.0017571 | 0.00044037
119 | 0.97045 | -0.57101 | 0.0011362 | 0.00028475
120 | 0.97069 | -0.56625 | 0.0013696 | 0.00034325
121 | 0.97419 | -0.49648 | 0.00065867 | 0.00016508
122 | 0.97432 | -0.4939 | 0.0011708 | 0.00029342
123 | 0.97433 | -0.49384 | 0.00091807 | 0.00023009
124 | 0.97433 | -0.49384 | 0.00091822 | 0.00023013
125 | 0.98983 | -0.19295 | 0.0024743 | 0.00062012
126 | 0.98874 | -0.21381 | 0.0016636 | 0.00041695
127 | 0.98767 | -0.23438 | 0.0024058 | 0.00060295
128 | 0.98656 | -0.25566 | 0.001632 | 0.00040903
129 | 0.98647 | -0.25753 | 0.0011866 | 0.0002974
130 | 0.98555 | -0.27526 | 0.0013115 | 0.00032868
131 | 0.98519 | -0.28206 | 0.001102 | 0.00027618
132 | 0.98456 | -0.29424 | 0.0010633 | 0.00026648
133 | 0.99992 | -0.0015961 | 0 | 0
134 | 0.99986 | -0.0026052 | 0.0020781 | 0.00052083
135 | 0.98758 | -0.2365 | 0.0014909 | 0.00037366
136 | 0.98692 | -0.24915 | 0 | 0
137 | 0.99986 | -0.0026903 | 0.00076263 | 0.00019113
138 | 0.98055 | -0.37218 | 0.0021298 | 0.00053379
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021852 | -0.00054767 | 0.002186 | 0.00054566 | 8.037e-07 | -2.001e-06 | 0.0032977 | 0.0032968 | 0.0032977 | 0.98602 | -0.26749 | 0.98642 | -0.25975 | 0.90597
1 | -0.002186 | -0.00054566 | 0.0021862 | 0.00054509 | 2.305e-07 | -5.7453e-07 | 0.0032968 | 0.0032966 | 0.0032968 | 0.98642 | -0.25975 | 0.98653 | -0.25753 | 0.90572
2 | -0.0043581 | -0.0010894 | 0.0043658 | 0.0010883 | 7.6204e-06 | -1.1428e-06 | 0.0065725 | 0.0065704 | 0.0065725 | 0.98653 | -0.25753 | 0.98841 | -0.22075 | 1.8056
3 | -0.0056516 | -0.0014105 | 0.0056564 | 0.0014113 | 4.764e-06 | 7.9627e-07 | 0.0085062 | 0.0085054 | 0.0085062 | 0.98841 | -0.22075 | 0.98932 | -0.20301 | 2.3369
4 | 0.0047696 | 0.0011946 | -0.0047692 | -0.0011946 | 3.7621e-07 | 5.5949e-09 | 0.0072862 | 0.0072863 | 0.0072863 | 0.97402 | -0.50048 | 0.97394 | -0.50214 | 2.0017
5 | -0.0063108 | -0.0015809 | 0.006311 | 0.0015809 | 2.0439e-07 | 5.7821e-08 | 0.0096408 | 0.0096408 | 0.0096408 | 0.97402 | -0.50048 | 0.97406 | -0.4998 | 2.6486
6 | 0.003272 | 0.00081935 | -0.0032719 | -0.00081937 | 2.3534e-08 | -1.6193e-08 | 0.0049988 | 0.0049988 | 0.0049988 | 0.97394 | -0.50214 | 0.97393 | -0.50229 | 1.3733
7 | -0.0072394 | -0.0018136 | 0.0072408 | 0.0018141 | 1.4112e-06 | 5.2008e-07 | 0.011059 | 0.011059 | 0.011059 | 0.97406 | -0.4998 | 0.97426 | -0.49571 | 3.0382
8 | 0.0020281 | 0.00050764 | -0.0020281 | -0.00050784 | 7.1811e-08 | -2.0225e-07 | 0.0030984 | 0.0030985 | 0.0030985 | 0.97393 | -0.50229 | 0.97389 | -0.50303 | 0.85124
9 | 0.0031029 | 0.00077724 | -0.0031027 | -0.00077738 | 1.7176e-07 | -1.4403e-07 | 0.0047389 | 0.004739 | 0.004739 | 0.97426 | -0.49571 | 0.9742 | -0.49687 | 1.3019
10 | -0.010344 | -0.0025914 | 0.010346 | 0.0025925 | 2.3083e-06 | 1.1701e-06 | 0.015798 | 0.015798 | 0.015798 | 0.97426 | -0.49571 | 0.9745 | -0.49102 | 4.3401
11 | 0.0012142 | 0.00030414 | -0.0012142 | -0.00030431 | 1.856e-08 | -1.6705e-07 | 0.0018552 | 0.0018552 | 0.0018552 | 0.97389 | -0.50303 | 0.97388 | -0.50335 | 0.50968
12 | 0.00081383 | 0.0002037 | -0.00081382 | -0.00020396 | 1.2494e-08 | -2.6015e-07 | 0.0012434 | 0.0012435 | 0.0012435 | 0.97389 | -0.50303 | 0.97388 | -0.50335 | 0.34161
13 | 0.0014892 | 0.000373 | -0.0014892 | -0.00037322 | 3.8329e-08 | -2.2145e-07 | 0.0022745 | 0.0022746 | 0.0022746 | 0.9742 | -0.49687 | 0.97418 | -0.49741 | 0.6249
14 | -0.0374 | -0.0093907 | 0.037423 | 0.0094054 | 2.3206e-05 | 1.4615e-05 | 0.057114 | 0.057114 | 0.057114 | 0.9745 | -0.49102 | 0.97516 | -0.47802 | 15.6906
15 | 0.027054 | 0.0067982 | -0.027041 | -0.0067902 | 1.2846e-05 | 7.9715e-06 | 0.041316 | 0.041316 | 0.041316 | 0.9745 | -0.49102 | 0.97399 | -0.50097 | 11.3506
16 | 0.039864 | 0.010027 | -0.039824 | -0.010001 | 4.0193e-05 | 2.5364e-05 | 0.060912 | 0.060912 | 0.060912 | 0.97406 | -0.49905 | 0.97299 | -0.52018 | 16.734
17 | -0.040834 | -0.01027 | 0.040841 | 0.010274 | 6.5689e-06 | 4.1481e-06 | 0.062393 | 0.062393 | 0.062393 | 0.97406 | -0.49905 | 0.97423 | -0.49568 | 17.141
18 | 0.038882 | 0.0097651 | -0.038874 | -0.0097604 | 7.5211e-06 | 4.7431e-06 | 0.05947 | 0.05947 | 0.05947 | 0.97299 | -0.52018 | 0.97278 | -0.52424 | 16.338
19 | -0.041602 | -0.010465 | 0.041636 | 0.010486 | 3.3499e-05 | 2.1164e-05 | 0.063556 | 0.063556 | 0.063556 | 0.97423 | -0.49568 | 0.97509 | -0.47884 | 17.4606
20 | 0.035118 | 0.0088189 | -0.035117 | -0.0088186 | 4.6213e-07 | 2.9046e-07 | 0.053724 | 0.053724 | 0.053724 | 0.97278 | -0.52424 | 0.97277 | -0.52451 | 14.7594
21 | -0.053241 | -0.013394 | 0.053306 | 0.013435 | 6.4476e-05 | 4.0939e-05 | 0.081267 | 0.081266 | 0.081267 | 0.97509 | -0.47884 | 0.97638 | -0.45353 | 22.326
22 | 0.009936 | 0.0024903 | -0.0099326 | -0.0024886 | 3.3668e-06 | 1.6678e-06 | 0.015163 | 0.015163 | 0.015163 | 0.97509 | -0.47884 | 0.97473 | -0.48596 | 4.1656
23 | 0.0016695 | 0.0004182 | -0.0016694 | -0.0004184 | 4.4388e-08 | -1.9907e-07 | 0.0025476 | 0.0025477 | 0.0025477 | 0.97509 | -0.47884 | 0.97506 | -0.4794 | 0.69991
24 | 0.031999 | 0.0080371 | -0.031977 | -0.0080235 | 2.1646e-05 | 1.3554e-05 | 0.048954 | 0.048954 | 0.048954 | 0.97277 | -0.52451 | 0.97205 | -0.5387 | 13.449
25 | 0.00073066 | 0.00018292 | -0.00073065 | -0.00018312 | 7.5691e-09 | -1.9875e-07 | 0.0011135 | 0.0011135 | 0.0011135 | 0.97638 | -0.45353 | 0.97636 | -0.45375 | 0.30592
26 | -0.054037 | -0.013618 | 0.054171 | 0.013703 | 0.00013411 | 8.5168e-05 | 0.08238 | 0.08238 | 0.08238 | 0.97638 | -0.45353 | 0.97902 | -0.40179 | 22.6319
27 | 0.0093279 | 0.002337 | -0.0093277 | -0.002337 | 1.015e-07 | 4.8324e-08 | 0.01424 | 0.01424 | 0.01424 | 0.97473 | -0.48596 | 0.97471 | -0.48619 | 3.912
28 | 0.028517 | 0.0071564 | -0.028515 | -0.0071553 | 1.7568e-06 | 1.0939e-06 | 0.043658 | 0.043658 | 0.043658 | 0.97205 | -0.5387 | 0.97198 | -0.53999 | 11.9938
29 | -0.050846 | -0.012885 | 0.050874 | 0.012902 | 2.7551e-05 | 1.7005e-05 | 0.077052 | 0.077052 | 0.077052 | 0.98257 | -0.33322 | 0.98316 | -0.32195 | 10.5841
30 | 0.048123 | 0.012202 | -0.048091 | -0.012183 | 3.154e-05 | 1.9385e-05 | 0.072929 | 0.072929 | 0.072929 | 0.98257 | -0.33322 | 0.98187 | -0.34686 | 10.0177
31 | -0.05248 | -0.013304 | 0.052512 | 0.013324 | 3.1276e-05 | 1.9346e-05 | 0.079484 | 0.079484 | 0.079484 | 0.98316 | -0.32195 | 0.9838 | -0.30956 | 10.9181
32 | 0.048091 | 0.012183 | -0.048081 | -0.012176 | 1.0569e-05 | 6.6972e-06 | 0.072929 | 0.072929 | 0.072929 | 0.98187 | -0.34686 | 0.98164 | -0.35144 | 20.0354
33 | -0.053882 | -0.013667 | 0.053893 | 0.013674 | 1.1538e-05 | 7.1495e-06 | 0.081556 | 0.081556 | 0.081556 | 0.9838 | -0.30956 | 0.98403 | -0.3051 | 11.2028
34 | 0.047488 | 0.012028 | -0.047412 | -0.011979 | 7.656e-05 | 4.8502e-05 | 0.07203 | 0.07203 | 0.07203 | 0.98164 | -0.35144 | 0.97991 | -0.38507 | 19.7886
35 | -0.056633 | -0.014361 | 0.056663 | 0.01438 | 3.0673e-05 | 1.9064e-05 | 0.085698 | 0.085698 | 0.085698 | 0.98403 | -0.3051 | 0.98461 | -0.29384 | 11.7718
36 | 0.047412 | 0.011979 | -0.047388 | -0.011965 | 2.3126e-05 | 1.4651e-05 | 0.07203 | 0.072031 | 0.072031 | 0.97991 | -0.38507 | 0.97939 | -0.39525 | 19.7886
37 | -0.062234 | -0.015776 | 0.062272 | 0.0158 | 3.8149e-05 | 2.3831e-05 | 0.094117 | 0.094117 | 0.094117 | 0.98461 | -0.29384 | 0.98527 | -0.2811 | 12.9282
38 | 0.043254 | 0.010929 | -0.043188 | -0.010887 | 6.614e-05 | 4.1817e-05 | 0.065749 | 0.065749 | 0.065749 | 0.97939 | -0.39525 | 0.97775 | -0.4272 | 18.063
39 | 0.0041344 | 0.0010353 | -0.0041337 | -0.0010354 | 6.9059e-07 | -1.4527e-07 | 0.0062812 | 0.0062814 | 0.0062814 | 0.97939 | -0.39525 | 0.97921 | -0.39876 | 1.7257
40 | 0.0020337 | 0.00050911 | -0.0020337 | -0.00050927 | 5.2551e-08 | -1.5095e-07 | 0.0030903 | 0.0030903 | 0.0030903 | 0.97921 | -0.39876 | 0.97918 | -0.3993 | 0.849
41 | 0.0011725 | 0.00029344 | -0.0011725 | -0.00029385 | 4.1652e-08 | -4.1341e-07 | 0.0017817 | 0.0017819 | 0.0017819 | 0.97918 | -0.3993 | 0.97914 | -0.40005 | 0.48952
42 | 0.042185 | 0.010636 | -0.042139 | -0.010607 | 4.6027e-05 | 2.9084e-05 | 0.064223 | 0.064223 | 0.064223 | 0.97775 | -0.4272 | 0.97659 | -0.45002 | 17.6436
43 | 0.0030723 | 0.00076979 | -0.0030721 | -0.00076995 | 1.8594e-07 | -1.6408e-07 | 0.0046812 | 0.0046813 | 0.0046813 | 0.97659 | -0.45002 | 0.97652 | -0.45129 | 1.2861
44 | 0.039066 | 0.0098371 | -0.039014 | -0.0098042 | 5.2225e-05 | 3.2933e-05 | 0.059541 | 0.059542 | 0.059542 | 0.97659 | -0.45002 | 0.97516 | -0.47802 | 16.3576
45 | -0.086435 | -0.021973 | 0.086509 | 0.02202 | 7.4118e-05 | 4.6833e-05 | 0.13 | 0.13 | 0.13 | 0.99017 | -0.18665 | 0.9911 | -0.16886 | 17.8577
46 | 0.084391 | 0.02146 | -0.084346 | -0.021432 | 4.5247e-05 | 2.8573e-05 | 0.12693 | 0.12693 | 0.12693 | 0.99017 | -0.18665 | 0.98959 | -0.19779 | 17.4357
47 | -0.088041 | -0.022403 | 0.088085 | 0.022431 | 4.4544e-05 | 2.8158e-05 | 0.1323 | 0.1323 | 0.1323 | 0.9911 | -0.16886 | 0.99165 | -0.15837 | 18.1735
48 | 0.075949 | 0.019333 | -0.075932 | -0.019323 | 1.6813e-05 | 1.0584e-05 | 0.11431 | 0.11431 | 0.11431 | 0.98959 | -0.19779 | 0.98935 | -0.20238 | 15.7017
49 | 0.0083968 | 0.0020984 | -0.0083954 | -0.0020979 | 1.3424e-06 | 5.7061e-07 | 0.012624 | 0.012624 | 0.012624 | 0.98959 | -0.19779 | 0.98942 | -0.20115 | 3.4681
50 | -0.08904 | -0.022671 | 0.089114 | 0.022718 | 7.3979e-05 | 4.6777e-05 | 0.13374 | 0.13374 | 0.13374 | 0.99165 | -0.15837 | 0.99255 | -0.14116 | 18.3703
51 | 0.075181 | 0.019135 | -0.075136 | -0.019106 | 4.5408e-05 | 2.8576e-05 | 0.11318 | 0.11318 | 0.11318 | 0.98935 | -0.20238 | 0.9887 | -0.21492 | 15.5466
52 | 0.0070498 | 0.0017606 | -0.0070492 | -0.0017604 | 6.2146e-07 | 2.0834e-07 | 0.0106 | 0.0106 | 0.0106 | 0.98942 | -0.20115 | 0.98932 | -0.20301 | 2.9122
53 | -0.089781 | -0.022885 | 0.089888 | 0.022953 | 0.00010758 | 6.8032e-05 | 0.13473 | 0.13473 | 0.13473 | 0.99255 | -0.14116 | 0.99385 | -0.11637 | 18.5075
54 | 0.07336 | 0.018661 | -0.073307 | -0.018628 | 5.3039e-05 | 3.3351e-05 | 0.11051 | 0.11051 | 0.11051 | 0.9887 | -0.21492 | 0.98792 | -0.22993 | 15.1796
55 | -0.18317 | -0.046867 | 0.18366 | 0.047178 | 0.000488 | 0.00031142 | 0.2746 | 0.2746 | 0.2746 | 0.99385 | -0.11637 | 0.99674 | -0.061491 | 37.7193
56 | 0.092677 | 0.023762 | -0.09254 | -0.023675 | 0.00013679 | 8.6567e-05 | 0.13895 | 0.13895 | 0.13895 | 0.99385 | -0.11637 | 0.99224 | -0.14685 | 19.0865
57 | 0.070613 | 0.017952 | -0.070591 | -0.017938 | 2.2354e-05 | 1.4037e-05 | 0.10645 | 0.10645 | 0.10645 | 0.98792 | -0.22993 | 0.98758 | -0.2365 | 14.6222
58 | -0.054746 | -0.013848 | 0.054754 | 0.013853 | 8.5943e-06 | 5.4588e-06 | 0.083254 | 0.083254 | 0.083254 | 0.97902 | -0.40179 | 0.97919 | -0.39852 | 22.872
59 | 0.0086398 | 0.0021646 | -0.0086383 | -0.0021639 | 1.5442e-06 | 6.933e-07 | 0.013189 | 0.01319 | 0.01319 | 0.97471 | -0.48619 | 0.97452 | -0.48994 | 3.6235
60 | 0.007759 | 0.0019435 | -0.0077576 | -0.0019429 | 1.44e-06 | 5.8078e-07 | 0.011847 | 0.011847 | 0.011847 | 0.97452 | -0.48994 | 0.97433 | -0.49384 | 3.2547
61 | -0.0017248 | -0.00043209 | 0.0017248 | 0.00043195 | 3.1586e-08 | -1.376e-07 | 0.002606 | 0.002606 | 0.002606 | 0.98482 | -0.28987 | 0.98484 | -0.28948 | 0.71594
62 | 0.00092293 | 0.00023112 | -0.00092292 | -0.0002313 | 1.101e-08 | -1.8506e-07 | 0.0013944 | 0.0013945 | 0.0013945 | 0.98482 | -0.28987 | 0.98481 | -0.29012 | 0.3831
63 | -0.0033776 | -0.00084618 | 0.003378 | 0.00084596 | 3.2811e-07 | -2.1757e-07 | 0.0051032 | 0.0051031 | 0.0051032 | 0.98484 | -0.28948 | 0.98495 | -0.28744 | 1.402
64 | -0.0047552 | -0.0011911 | 0.0047559 | 0.0011911 | 7.7554e-07 | -1.3808e-08 | 0.0071837 | 0.0071835 | 0.0071837 | 0.98495 | -0.28744 | 0.98512 | -0.28402 | 1.9735
65 | -0.0054935 | -0.001376 | 0.0054949 | 0.0013762 | 1.3826e-06 | 2.0288e-07 | 0.0082977 | 0.0082974 | 0.0082977 | 0.98512 | -0.28402 | 0.98539 | -0.27873 | 2.2796
66 | -0.0054949 | -0.0013762 | 0.005496 | 0.0013763 | 1.0528e-06 | 1.5421e-07 | 0.0082974 | 0.0082972 | 0.0082974 | 0.98539 | -0.27873 | 0.9856 | -0.27471 | 2.2795
67 | 0.056153 | 0.014222 | -0.056104 | -0.014191 | 4.9091e-05 | 3.0512e-05 | 0.085304 | 0.085305 | 0.085305 | 0.98013 | -0.3803 | 0.97919 | -0.39852 | 11.7177
68 | -0.056827 | -0.014391 | 0.056862 | 0.014413 | 3.5103e-05 | 2.1832e-05 | 0.086328 | 0.086327 | 0.086328 | 0.98013 | -0.3803 | 0.98079 | -0.36745 | 11.8582
69 | -0.059348 | -0.015036 | 0.059359 | 0.015042 | 1.0279e-05 | 6.4078e-06 | 0.090099 | 0.090099 | 0.090099 | 0.98079 | -0.36745 | 0.98097 | -0.36384 | 12.3763
70 | -0.068487 | -0.01733 | 0.068582 | 0.017389 | 9.4879e-05 | 5.9538e-05 | 0.10395 | 0.10395 | 0.10395 | 0.98097 | -0.36384 | 0.98246 | -0.33502 | 14.2784
71 | 0.0091288 | 0.0022879 | -0.009127 | -0.0022871 | 1.8224e-06 | 8.4642e-07 | 0.013847 | 0.013847 | 0.013847 | 0.98097 | -0.36384 | 0.98076 | -0.36803 | 3.8042
72 | -0.071729 | -0.018178 | 0.071797 | 0.01822 | 6.7689e-05 | 4.2547e-05 | 0.10871 | 0.10871 | 0.10871 | 0.98246 | -0.33502 | 0.98347 | -0.3154 | 14.933
73 | 0.0017597 | 0.00044068 | -0.0017596 | -0.000441 | 7.7622e-08 | -3.1932e-07 | 0.0026651 | 0.0026652 | 0.0026652 | 0.98246 | -0.33502 | 0.98241 | -0.33594 | 0.7322
74 | 0.006744 | 0.0016898 | -0.0067436 | -0.0016897 | 4.5168e-07 | 1.439e-07 | 0.010232 | 0.010232 | 0.010232 | 0.98076 | -0.36803 | 0.98069 | -0.36944 | 2.811
75 | -0.18473 | -0.047446 | 0.18528 | 0.047799 | 0.00055336 | 0.00035314 | 0.27619 | 0.27619 | 0.27619 | 0.99674 | -0.061491 | 1 | 0 | 37.9384
76 | 0.089805 | 0.02299 | -0.089664 | -0.022901 | 0.00014071 | 8.8991e-05 | 0.13485 | 0.13485 | 0.13485 | 0.99224 | -0.14685 | 0.99055 | -0.17926 | 18.5231
77 | 0.0035541 | 0.00089015 | -0.003554 | -0.00089022 | 1.0207e-07 | -6.2354e-08 | 0.0052884 | 0.0052884 | 0.0052884 | 1 | 0 | 0.99997 | -0.00060315 | 1.4529
78 | 0.088249 | 0.022546 | -0.088204 | -0.022517 | 4.5459e-05 | 2.874e-05 | 0.13272 | 0.13272 | 0.13272 | 0.99055 | -0.17926 | 0.98999 | -0.18992 | 18.2312
79 | 0.002841 | 0.00071153 | -0.0028409 | -0.00071168 | 1.1681e-07 | -1.5387e-07 | 0.0042275 | 0.0042276 | 0.0042276 | 0.99997 | -0.00060315 | 0.99992 | -0.0014666 | 1.1614
80 | 0.088204 | 0.022517 | -0.088191 | -0.022509 | 1.2907e-05 | 8.16e-06 | 0.13272 | 0.13272 | 0.13272 | 0.98999 | -0.18992 | 0.98983 | -0.19295 | 18.2312
81 | 0.0028409 | 0.00071168 | -0.0028409 | -0.0007117 | 1.7526e-08 | -2.3085e-08 | 0.0042276 | 0.0042276 | 0.0042276 | 0.99992 | -0.0014666 | 0.99992 | -0.0015961 | 1.1614
82 | -0.023783 | -0.0059642 | 0.023791 | 0.0059696 | 8.7068e-06 | 5.3544e-06 | 0.036378 | 0.036378 | 0.036378 | 0.97286 | -0.52343 | 0.97324 | -0.51576 | 9.9939
83 | 0.0064455 | 0.0016152 | -0.0064448 | -0.001615 | 7.079e-07 | 2.1192e-07 | 0.0098586 | 0.0098587 | 0.0098587 | 0.97286 | -0.52343 | 0.97274 | -0.52574 | 2.7084
84 | 0.016414 | 0.0041176 | -0.016397 | -0.0041075 | 1.7253e-05 | 1.0136e-05 | 0.025107 | 0.025107 | 0.025107 | 0.97286 | -0.52343 | 0.97174 | -0.5455 | 6.8976
85 | -0.023791 | -0.0059696 | 0.0238 | 0.0059748 | 8.4765e-06 | 5.2126e-06 | 0.036378 | 0.036378 | 0.036378 | 0.97324 | -0.51576 | 0.97362 | -0.50829 | 9.9939
86 | 0.0049315 | 0.0012357 | -0.0049313 | -0.0012357 | 1.604e-07 | 9.3543e-09 | 0.0075437 | 0.0075437 | 0.0075437 | 0.97274 | -0.52574 | 0.9727 | -0.52642 | 2.0725
87 | 0.014959 | 0.0037473 | -0.014957 | -0.0037457 | 2.6787e-06 | 1.5457e-06 | 0.022907 | 0.022907 | 0.022907 | 0.97174 | -0.5455 | 0.97155 | -0.54927 | 6.293
88 | -0.025416 | -0.0063799 | 0.025425 | 0.0063854 | 8.8673e-06 | 5.4801e-06 | 0.038848 | 0.038848 | 0.038848 | 0.97362 | -0.50829 | 0.97399 | -0.50097 | 10.6726
89 | 0.0034895 | 0.00087432 | -0.0034893 | -0.00087442 | 1.8753e-07 | -9.7813e-08 | 0.005338 | 0.0053381 | 0.0053381 | 0.9727 | -0.52642 | 0.97265 | -0.52755 | 1.4665
90 | 0.0014293 | 0.00035814 | -0.0014293 | -0.00035821 | 1.1877e-08 | -7.4613e-08 | 0.0021866 | 0.0021866 | 0.0021866 | 0.97265 | -0.52755 | 0.97264 | -0.52772 | 0.60072
91 | 0.011562 | 0.0028949 | -0.01156 | -0.0028941 | 1.4773e-06 | 7.899e-07 | 0.017707 | 0.017707 | 0.017707 | 0.97155 | -0.54927 | 0.97141 | -0.55195 | 4.8645
92 | 0.010507 | 0.0026302 | -0.010506 | -0.0026298 | 7.9232e-07 | 4.0611e-07 | 0.016094 | 0.016094 | 0.016094 | 0.97141 | -0.55195 | 0.97133 | -0.55353 | 4.4214
93 | -0.0038428 | -0.00096283 | 0.003843 | 0.00096275 | 2.8184e-07 | -8.697e-08 | 0.005893 | 0.0058929 | 0.005893 | 0.97031 | -0.57312 | 0.97039 | -0.57158 | 1.6189
94 | 0.0014755 | 0.00036956 | -0.0014755 | -0.0003698 | 4.1414e-08 | -2.399e-07 | 0.0022627 | 0.0022628 | 0.0022628 | 0.97031 | -0.57312 | 0.97028 | -0.57371 | 0.62165
95 | -0.0055455 | -0.0013894 | 0.0055458 | 0.0013895 | 3.2017e-07 | 5.9032e-08 | 0.0085035 | 0.0085034 | 0.0085035 | 0.97039 | -0.57158 | 0.97045 | -0.57037 | 2.3361
96 | -0.0064738 | -0.0016221 | 0.0064744 | 0.0016223 | 6.6027e-07 | 2.0176e-07 | 0.0099263 | 0.0099262 | 0.0099263 | 0.97045 | -0.57037 | 0.97056 | -0.56823 | 2.727
97 | 0.0029226 | 0.00073243 | -0.0029226 | -0.00073247 | 3.8875e-08 | -3.8927e-08 | 0.0044808 | 0.0044808 | 0.0044808 | 0.97056 | -0.56823 | 0.97054 | -0.56851 | 1.231
98 | -0.009397 | -0.0023547 | 0.0093991 | 0.0023557 | 2.0342e-06 | 9.7885e-07 | 0.014407 | 0.014407 | 0.014407 | 0.97056 | -0.56823 | 0.97079 | -0.56369 | 3.958
99 | -0.00088577 | -0.000222 | 0.00088579 | 0.00022164 | 2.0559e-08 | -3.5939e-07 | 0.0013533 | 0.0013532 | 0.0013533 | 0.97393 | -0.50174 | 0.97395 | -0.50125 | 0.37179
100 | -0.0018097 | -0.00045319 | 0.0018098 | 0.00045289 | 7.9437e-08 | -2.9407e-07 | 0.0027648 | 0.0027646 | 0.0027648 | 0.97395 | -0.50125 | 0.974 | -0.50033 | 0.75955
101 | -0.014198 | -0.0035585 | 0.0142 | 0.0035594 | 1.6504e-06 | 9.4135e-07 | 0.021763 | 0.021763 | 0.021763 | 0.97079 | -0.56369 | 0.97091 | -0.56125 | 5.9789
102 | 0.062291 | 0.015812 | -0.062272 | -0.0158 | 1.914e-05 | 1.1956e-05 | 0.094117 | 0.094117 | 0.094117 | 0.9856 | -0.27471 | 0.98527 | -0.2811 | 12.9282
103 | -0.067787 | -0.017188 | 0.067827 | 0.017213 | 3.954e-05 | 2.4793e-05 | 0.10241 | 0.10241 | 0.10241 | 0.9856 | -0.27471 | 0.98623 | -0.26258 | 14.0679
104 | -0.069013 | -0.01751 | 0.069058 | 0.017538 | 4.4592e-05 | 2.798e-05 | 0.1042 | 0.1042 | 0.1042 | 0.98623 | -0.26258 | 0.98692 | -0.24915 | 14.3137
105 | 0.0056177 | 0.0014044 | -0.0056171 | -0.0014042 | 6.4311e-07 | 1.2512e-07 | 0.0086062 | 0.0086063 | 0.0086063 | 0.97117 | -0.5568 | 0.97105 | -0.55921 | 2.3644
106 | -0.0066014 | -0.0016509 | 0.0066017 | 0.001651 | 2.3324e-07 | 7.4026e-08 | 0.010113 | 0.010113 | 0.010113 | 0.97117 | -0.5568 | 0.97121 | -0.55606 | 2.7784
107 | 0.0042655 | 0.0010655 | -0.0042653 | -0.0010655 | 1.7959e-07 | -2.3777e-08 | 0.006535 | 0.0065351 | 0.0065351 | 0.97105 | -0.55921 | 0.971 | -0.5601 | 1.7954
108 | -0.0079304 | -0.001984 | 0.0079314 | 0.0019844 | 9.5306e-07 | 3.9686e-07 | 0.012149 | 0.012149 | 0.012149 | 0.97121 | -0.55606 | 0.97133 | -0.55353 | 3.3377
109 | 0.0042653 | 0.0010655 | -0.0042643 | -0.0010656 | 9.8723e-07 | -1.3044e-07 | 0.0065351 | 0.0065354 | 0.0065354 | 0.971 | -0.5601 | 0.97076 | -0.56497 | 1.7954
110 | 0.0042643 | 0.0010656 | -0.004264 | -0.0010657 | 2.6014e-07 | -3.4297e-08 | 0.0065354 | 0.0065354 | 0.0065354 | 0.97076 | -0.56497 | 0.97069 | -0.56625 | 1.7955
111 | -0.002638 | -0.00066105 | 0.0026381 | 0.00066089 | 1.1145e-07 | -1.5351e-07 | 0.0040431 | 0.004043 | 0.0040431 | 0.97086 | -0.56223 | 0.9709 | -0.56135 | 1.1107
112 | 0.0017267 | 0.00043265 | -0.0017266 | -0.00043274 | 2.0361e-08 | -8.2837e-08 | 0.0026464 | 0.0026464 | 0.0026464 | 0.97086 | -0.56223 | 0.97085 | -0.56248 | 0.72704
113 | -0.0051738 | -0.0012964 | 0.0051743 | 0.0012965 | 4.3237e-07 | 4.9911e-08 | 0.0079294 | 0.0079293 | 0.0079294 | 0.9709 | -0.56135 | 0.97099 | -0.55959 | 2.1784
114 | 0.015921 | 0.0039912 | -0.01592 | -0.0039904 | 1.2569e-06 | 7.3478e-07 | 0.024399 | 0.024399 | 0.024399 | 0.97099 | -0.55959 | 0.97091 | -0.56125 | 6.703
115 | -0.021095 | -0.0052876 | 0.021102 | 0.0052915 | 6.3129e-06 | 3.8409e-06 | 0.032328 | 0.032328 | 0.032328 | 0.97099 | -0.55959 | 0.97131 | -0.55331 | 8.8814
116 | -0.024578 | -0.0061628 | 0.024594 | 0.0061725 | 1.5615e-05 | 9.6299e-06 | 0.037654 | 0.037654 | 0.037654 | 0.97131 | -0.55331 | 0.97198 | -0.53999 | 10.3446
117 | -0.074878 | -0.018993 | 0.074926 | 0.019023 | 4.7966e-05 | 3.0193e-05 | 0.11337 | 0.11337 | 0.11337 | 0.98347 | -0.3154 | 0.98416 | -0.30208 | 15.5734
118 | 0.0043216 | 0.0010827 | -0.0043213 | -0.0010827 | 3.7487e-07 | -5.3404e-08 | 0.0065572 | 0.0065573 | 0.0065573 | 0.98069 | -0.36944 | 0.98059 | -0.37126 | 1.8014
119 | -0.074926 | -0.019023 | 0.074954 | 0.019041 | 2.8289e-05 | 1.7806e-05 | 0.11337 | 0.11337 | 0.11337 | 0.98416 | -0.30208 | 0.98456 | -0.29424 | 15.5733
120 | 0.0021299 | 0.00053355 | -0.0021298 | -0.00053379 | 9.3674e-08 | -2.4169e-07 | 0.003232 | 0.0032321 | 0.0032321 | 0.98059 | -0.37126 | 0.98055 | -0.37218 | 0.88794
121 | -0.0026309 | -0.00065869 | 0.0026311 | 0.00065848 | 1.5121e-07 | -2.1394e-07 | 0.0040191 | 0.004019 | 0.0040191 | 0.974 | -0.50033 | 0.97406 | -0.49912 | 1.1042
122 | -0.0040908 | -0.0010243 | 0.0040913 | 0.0010242 | 5.137e-07 | -1.0797e-07 | 0.0062489 | 0.0062487 | 0.0062489 | 0.97406 | -0.49912 | 0.97419 | -0.49648 | 1.7167
123 | -0.0017571 | -0.00044037 | 0.0017576 | 0.00043836 | 5.1823e-07 | -2.019e-06 | 0.0026951 | 0.0026942 | 0.0026951 | 0.97014 | -0.57721 | 0.97045 | -0.57101 | 0.74041
124 | -0.0028938 | -0.0007231 | 0.0028944 | 0.00072243 | 6.541e-07 | -6.7678e-07 | 0.0044363 | 0.0044359 | 0.0044363 | 0.97045 | -0.57101 | 0.97069 | -0.56625 | 1.2188
125 | -0.0047499 | -0.0011893 | 0.0047505 | 0.0011893 | 5.8459e-07 | 5.3006e-09 | 0.0072548 | 0.0072547 | 0.0072548 | 0.97419 | -0.49648 | 0.97432 | -0.4939 | 1.9931
126 | -0.0059213 | -0.0014827 | 0.0059213 | 0.0014827 | 1.7069e-08 | 3.9913e-09 | 0.0090427 | 0.0090427 | 0.0090427 | 0.97432 | -0.4939 | 0.97433 | -0.49384 | 2.4843
127 | -0.0068394 | -0.0017128 | 0.0068394 | 0.0017128 | 4.3994e-12 | 2.8156e-12 | 0.010445 | 0.010445 | 0.010445 | 0.97433 | -0.49384 | 0.97433 | -0.49384 | 2.8694
128 | 0.085717 | 0.021889 | -0.08563 | -0.021834 | 8.6343e-05 | 5.4549e-05 | 0.129 | 0.129 | 0.129 | 0.98983 | -0.19295 | 0.98874 | -0.21381 | 17.7203
129 | 0.083967 | 0.021418 | -0.083883 | -0.021365 | 8.3303e-05 | 5.2603e-05 | 0.1265 | 0.1265 | 0.1265 | 0.98874 | -0.21381 | 0.98767 | -0.23438 | 17.3764
130 | 0.081478 | 0.020762 | -0.081394 | -0.020709 | 8.3558e-05 | 5.2723e-05 | 0.12288 | 0.12288 | 0.12288 | 0.98767 | -0.23438 | 0.98656 | -0.25566 | 16.8786
131 | 0.079762 | 0.0203 | -0.079755 | -0.020296 | 7.2219e-06 | 4.5542e-06 | 0.12041 | 0.12041 | 0.12041 | 0.98656 | -0.25566 | 0.98647 | -0.25753 | 16.5405
132 | 0.078568 | 0.019998 | -0.078501 | -0.019956 | 6.7064e-05 | 4.2273e-05 | 0.11862 | 0.11862 | 0.11862 | 0.98647 | -0.25753 | 0.98555 | -0.27526 | 16.2946
133 | 0.07719 | 0.019627 | -0.077164 | -0.019611 | 2.5295e-05 | 1.5936e-05 | 0.11664 | 0.11664 | 0.11664 | 0.98555 | -0.27526 | 0.98519 | -0.28206 | 16.0227
134 | 0.076062 | 0.019335 | -0.076018 | -0.019307 | 4.4593e-05 | 2.8082e-05 | 0.11498 | 0.11498 | 0.11498 | 0.98519 | -0.28206 | 0.98456 | -0.29424 | 15.7941
135 | 0.0028409 | 0.0007117 | -0.0028408 | -0.00071188 | 1.3653e-07 | -1.7981e-07 | 0.0042276 | 0.0042277 | 0.0042277 | 0.99992 | -0.0015961 | 0.99986 | -0.0026052 | 1.1614
136 | 0.00076263 | 0.00019105 | -0.00076263 | -0.00019113 | 3.0924e-09 | -8.1987e-08 | 0.0011349 | 0.001135 | 0.001135 | 0.99986 | -0.0026052 | 0.99986 | -0.0026903 | 0.3118
137 | 0.0691 | 0.017565 | -0.069058 | -0.017538 | 4.2068e-05 | 2.6395e-05 | 0.1042 | 0.1042 | 0.1042 | 0.98758 | -0.2365 | 0.98692 | -0.24915 | 14.3136

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.19217 | 0.04911

## res_load
| p_mw | q_mvar
0 | 0.0021852 | 0.00054767
1 | 0.0021719 | 0.00054433
2 | 0.0012859 | 0.00032226
3 | 0.0015413 | 0.00038628
4 | 0.0014972 | 0.00037524
5 | 0.00092839 | 0.00023268
6 | 0.0012438 | 0.00031173
7 | 0.0016135 | 0.00040438
8 | 0.0012142 | 0.00030431
9 | 0.00081382 | 0.00020396
10 | 0.00096993 | 0.00024309
11 | 0.00094241 | 0.00023619
12 | 0.00076151 | 0.00019085
13 | 0.0037566 | 0.00094149
14 | 0.0031183 | 0.00078153
15 | 0.00060478 | 0.00015157
16 | 0.0016694 | 0.0004184
17 | 0.0034601 | 0.00086718
18 | 0.0027232 | 0.00068249
19 | 0.0016067 | 0.00040269
20 | 0.0013701 | 0.00034338
21 | 0.00059278 | 0.00014856
22 | 0.0027393 | 0.00068653
23 | 0.0055709 | 0.0013962
24 | 0.0021 | 0.00052631
25 | 0.00086115 | 0.00021582
26 | 0.0011725 | 0.00029385
27 | 0.0010033 | 0.00025145
28 | 0.0020443 | 0.00051234
29 | 0.0015312 | 0.00038376
30 | 0.00095506 | 0.00023936
31 | 0.00075085 | 0.00018818
32 | 0.0013456 | 0.00033723
33 | 0.0006664 | 0.00016701
34 | 0.0017756 | 0.00044501
35 | 0.0013929 | 0.00034908
36 | 0.00060933 | 0.00015271
37 | 0.0026942 | 0.00067524
38 | 0.00073065 | 0.00018312
39 | 0.00057523 | 0.00014417
40 | 0.00068792 | 0.00017241
41 | 0.00087925 | 0.00022036
42 | 0.00080187 | 0.00020097
43 | 0.0016528 | 0.00041423
44 | 0.00092292 | 0.0002313
45 | 0.0013772 | 0.00034516
46 | 0.00073761 | 0.00018486
47 | 0.00067402 | 0.00016893
48 | 0.0013495 | 0.00033821
49 | 0.0024861 | 0.00062308
50 | 0.0013874 | 0.00034771
51 | 0.002383 | 0.00059724
52 | 0.0010688 | 0.00026787
53 | 0.0027354 | 0.00068556
54 | 0.0016782 | 0.00042059
55 | 0.0014147 | 0.00035455
56 | 0.00071298 | 0.00017869
57 | 0.00092328 | 0.0002314
58 | 0.0015133 | 0.00037928
59 | 0.0014372 | 0.0003602
60 | 0.0016164 | 0.00040511
61 | 0.0014419 | 0.00036137
62 | 0.0016154 | 0.00040487
63 | 0.00206 | 0.00051628
64 | 0.0033951 | 0.00085089
65 | 0.001053 | 0.0002639
66 | 0.0023672 | 0.00059328
67 | 0.0017025 | 0.00042668
68 | 0.0014755 | 0.0003698
69 | 0.00092794 | 0.00023256
70 | 0.00088577 | 0.000222
71 | 0.00092391 | 0.00023155
72 | 0.0029226 | 0.00073247
73 | 0.0047993 | 0.0012028
74 | 0.001186 | 0.00029725
75 | 0.0015912 | 0.0003988
76 | 0.0014892 | 0.00037322
77 | 0.0030721 | 0.00076995
78 | 0.00098369 | 0.00024654
79 | 0.0013516 | 0.00033875
80 | 0.0013288 | 0.00033302
81 | 0.002575 | 0.00064536
82 | 0.0009113 | 0.00022839
83 | 0.0025358 | 0.00063552
84 | 0.0017266 | 0.00043274
85 | 0.0017198 | 0.00043102
86 | 0.0034767 | 0.00087135
87 | 0.0039215 | 0.00098281
88 | 0.0030811 | 0.00077221
89 | 0.0017596 | 0.000441
90 | 0.0024219 | 0.00060699
91 | 0.0021913 | 0.0005492
92 | 0.0014293 | 0.00035821
93 | 0.00082114 | 0.0002058
94 | 0.0014597 | 0.00036583
95 | 0.0017571 | 0.00044037
96 | 0.0011362 | 0.00028475
97 | 0.0013696 | 0.00034325
98 | 0.00065867 | 0.00016508
99 | 0.0011708 | 0.00029342
100 | 0.00091807 | 0.00023009
101 | 0.00091822 | 0.00023013
102 | 0.0024743 | 0.00062012
103 | 0.0016636 | 0.00041695
104 | 0.0024058 | 0.00060295
105 | 0.001632 | 0.00040903
106 | 0.0011866 | 0.0002974
107 | 0.0013115 | 0.00032868
108 | 0.001102 | 0.00027618
109 | 0.0010633 | 0.00026648
110 | 0.0020781 | 0.00052083
111 | 0.0014909 | 0.00037366
112 | 0.00076263 | 0.00019113
113 | 0.0021298 | 0.00053379

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1