## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-12_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_2325-12_1_2_node_74 | 0.4 | n |  | TRUE
2 | bus_LV_2325-12_1_2_node_129 | 0.4 | n |  | TRUE
3 | bus_LV_2325-12_1_2_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_2325-12_1_2_node_130 | 0.4 | n |  | TRUE
5 | bus_LV_2325-12_1_2_node_97 | 0.4 | n |  | TRUE
6 | bus_LV_2325-12_1_2_node_131 | 0.4 | n |  | TRUE
7 | bus_LV_2325-12_1_2_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2325-12_1_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2325-12_1_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2325-12_1_2_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2325-12_1_2_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_2325-12_1_2_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_2325-12_1_2_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_2325-12_1_2_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_2325-12_1_2_node_55 | 0.4 | n |  | TRUE
16 | bus_LV_2325-12_1_2_node_66 | 0.4 | n |  | TRUE
17 | bus_LV_2325-12_1_2_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_2325-12_1_2_node_59 | 0.4 | n |  | TRUE
19 | bus_LV_2325-12_1_2_node_58 | 0.4 | n |  | TRUE
20 | bus_LV_2325-12_1_2_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_2325-12_1_2_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_2325-12_1_2_node_114 | 0.4 | n |  | TRUE
23 | bus_LV_2325-12_1_2_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_2325-12_1_2_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_2325-12_1_2_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_2325-12_1_2_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_2325-12_1_2_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_2325-12_1_2_node_72 | 0.4 | n |  | TRUE
29 | bus_LV_2325-12_1_2_node_90 | 0.4 | n |  | TRUE
30 | bus_LV_2325-12_1_2_node_71 | 0.4 | n |  | TRUE
31 | bus_LV_2325-12_1_2_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_2325-12_1_2_node_84 | 0.4 | n |  | TRUE
33 | bus_LV_2325-12_1_2_node_85 | 0.4 | n |  | TRUE
34 | bus_LV_2325-12_1_2_node_86 | 0.4 | n |  | TRUE
35 | bus_LV_2325-12_1_2_node_87 | 0.4 | n |  | TRUE
36 | bus_LV_2325-12_1_2_node_88 | 0.4 | n |  | TRUE
37 | bus_LV_2325-12_1_2_node_89 | 0.4 | n |  | TRUE
38 | bus_LV_2325-12_1_2_node_122 | 0.4 | n |  | TRUE
39 | bus_LV_2325-12_1_2_node_91 | 0.4 | n |  | TRUE
40 | bus_LV_2325-12_1_2_node_121 | 0.4 | n |  | TRUE
41 | bus_LV_2325-12_1_2_node_92 | 0.4 | n |  | TRUE
42 | bus_LV_2325-12_1_2_node_93 | 0.4 | n |  | TRUE
43 | bus_LV_2325-12_1_2_node_94 | 0.4 | n |  | TRUE
44 | bus_LV_2325-12_1_2_node_95 | 0.4 | n |  | TRUE
45 | bus_LV_2325-12_1_2_node_96 | 0.4 | n |  | TRUE
46 | bus_LV_2325-12_1_2_node_127 | 0.4 | n |  | TRUE
47 | bus_LV_2325-12_1_2_node_118 | 0.4 | n |  | TRUE
48 | bus_LV_2325-12_1_2_node_119 | 0.4 | n |  | TRUE
49 | bus_LV_2325-12_1_2_node_120 | 0.4 | n |  | TRUE
50 | bus_LV_2325-12_1_2_node_123 | 0.4 | n |  | TRUE
51 | bus_LV_2325-12_1_2_node_124 | 0.4 | n |  | TRUE
52 | bus_MV_37_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-12_1_2_load_128 | 0 | 0.0005559 | 0.00013932 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-12_1_2_load_74 | 1 | 0.00098405 | 0.00024663 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-12_1_2_load_129 | 2 | 0.0015006 | 0.00037609 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-12_1_2_load_130 | 4 | 0.0021408 | 0.00053654 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-12_1_2_load_97 | 5 | 0.0026693 | 0.00066899 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-12_1_2_load_131 | 6 | 0.0078015 | 0.0019552 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-12_1_2_load_15 | 7 | 0.0058639 | 0.0014696 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-12_1_2_load_8 | 8 | 0.021699 | 0.0054384 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-12_1_2_load_13 | 11 | 0.0018708 | 0.00046886 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-12_1_2_load_14 | 12 | 0.011845 | 0.0029687 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-12_1_2_load_53 | 13 | 0.0023706 | 0.00059413 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-12_1_2_load_54 | 14 | 0.0023635 | 0.00059236 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-12_1_2_load_55 | 15 | 0.013209 | 0.0033105 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-12_1_2_load_66 | 16 | 0.00098349 | 0.00024649 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-12_1_2_load_56 | 17 | 0.0033942 | 0.00085066 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-12_1_2_load_59 | 18 | 0.0033934 | 0.00085046 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-12_1_2_load_58 | 19 | 0.0013618 | 0.0003413 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-12_1_2_load_60 | 20 | 0.0023385 | 0.00058607 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-12_1_2_load_61 | 21 | 0.00092588 | 0.00023205 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-12_1_2_load_114 | 22 | 0.0031371 | 0.00078623 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-12_1_2_load_65 | 23 | 0.00080561 | 0.00020191 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-12_1_2_load_67 | 24 | 0.0021257 | 0.00053275 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-12_1_2_load_68 | 25 | 0.0045952 | 0.0011517 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-12_1_2_load_69 | 26 | 0.0021259 | 0.0005328 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-12_1_2_load_70 | 27 | 0.00058494 | 0.0001466 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-12_1_2_load_72 | 28 | 0.00097285 | 0.00024382 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-12_1_2_load_90 | 29 | 0.00079979 | 0.00020045 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-12_1_2_load_71 | 30 | 0.0044642 | 0.0011188 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-12_1_2_load_73 | 31 | 0.001785 | 0.00044737 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-12_1_2_load_84 | 32 | 0.0048113 | 0.0012058 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-12_1_2_load_85 | 33 | 0.00036147 | 9.0593e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-12_1_2_load_87 | 35 | 0.012764 | 0.003199 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-12_1_2_load_89 | 37 | 0.0015949 | 0.00039971 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-12_1_2_load_122 | 38 | 0.0015943 | 0.00039958 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-12_1_2_load_91 | 39 | 0.00043096 | 0.00010801 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-12_1_2_load_121 | 40 | 0.0018135 | 0.00045452 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-12_1_2_load_92 | 41 | 0.0044777 | 0.0011222 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-12_1_2_load_93 | 42 | 0.0027197 | 0.00068162 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-12_1_2_load_94 | 43 | 0.0029656 | 0.00074324 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-12_1_2_load_95 | 44 | 0.001147 | 0.00028746 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-12_1_2_load_96 | 45 | 0.0037793 | 0.00094717 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-12_1_2_load_127 | 46 | 0.0030824 | 0.00077253 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-12_1_2_load_118 | 47 | 0.0013587 | 0.00034053 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-12_1_2_load_119 | 48 | 0.0052806 | 0.0013234 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-12_1_2_load_123 | 50 | 0.00030001 | 7.519e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-12_1_2_load_124 | 51 | 0.00066113 | 0.0001657 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-12_1_2_line_0 |  | 0 | 1 | 0.0057968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-12_1_2_line_1 |  | 0 | 2 | 0.0080983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-12_1_2_line_2 |  | 1 | 31 | 0.015098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-12_1_2_line_3 |  | 2 | 3 | 0.035635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-12_1_2_line_4 |  | 3 | 9 | 0.065472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-12_1_2_line_5 |  | 4 | 5 | 0.025092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-12_1_2_line_6 |  | 5 | 14 | 0.043556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-12_1_2_line_7 |  | 5 | 44 | 0.012874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-12_1_2_line_8 |  | 6 | 7 | 0.012803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-12_1_2_line_9 |  | 7 | 12 | 0.0086407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-12_1_2_line_10 |  | 8 | 9 | 0.063913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-12_1_2_line_11 |  | 8 | 10 | 0.02872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-12_1_2_line_12 |  | 10 | 11 | 0.024918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-12_1_2_line_13 |  | 10 | 12 | 0.048593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-12_1_2_line_14 |  | 13 | 14 | 0.017278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-12_1_2_line_15 |  | 13 | 15 | 0.0048368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-12_1_2_line_16 |  | 14 | 16 | 0.061939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-12_1_2_line_17 |  | 15 | 17 | 0.025775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-12_1_2_line_18 |  | 16 | 25 | 0.0052981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-12_1_2_line_19 |  | 16 | 23 | 0.035235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-12_1_2_line_20 |  | 17 | 18 | 1.488e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-12_1_2_line_21 |  | 18 | 19 | 0.023773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-12_1_2_line_22 |  | 19 | 20 | 0.013124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-12_1_2_line_23 |  | 20 | 21 | 0.015608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-12_1_2_line_24 |  | 21 | 22 | 0.0078783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-12_1_2_line_25 |  | 23 | 24 | 0.02144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-12_1_2_line_26 |  | 24 | 26 | 0.00016946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-12_1_2_line_27 |  | 25 | 27 | 0.018754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-12_1_2_line_28 |  | 26 | 28 | 0.034567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-12_1_2_line_29 |  | 27 | 29 | 0.034946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-12_1_2_line_30 |  | 28 | 30 | 0.0013641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-12_1_2_line_31 |  | 29 | 39 | 0.0049428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-12_1_2_line_32 |  | 30 | 31 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-12_1_2_line_33 |  | 32 | 33 | 0.070605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-12_1_2_line_34 |  | 32 | 34 | 0.078335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-12_1_2_line_35 |  | 33 | 35 | 0.019411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-12_1_2_line_36 |  | 34 | 36 | 0.031218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-12_1_2_line_37 |  | 36 | 37 | 0.03201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-12_1_2_line_38 |  | 37 | 38 | 0.021621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-12_1_2_line_39 |  | 38 | 49 | 0.034832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-12_1_2_line_40 |  | 39 | 40 | 0.0004864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-12_1_2_line_41 |  | 40 | 48 | 0.002969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-12_1_2_line_42 |  | 41 | 42 | 0.012382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-12_1_2_line_43 |  | 41 | 43 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-12_1_2_line_44 |  | 42 | 44 | 0.020329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-12_1_2_line_45 |  | 43 | 45 | 0.021908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-12_1_2_line_46 |  | 45 | 46 | 0.0040836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2325-12_1_2_line_47 |  | 47 | 48 | 0.0059612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2325-12_1_2_line_48 |  | 47 | 49 | 0.027673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2325-12_1_2_line_49 |  | 49 | 50 | 0.013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-12_1_2_line_50 |  | 50 | 51 | 0.0045007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-12_1_2_trafo_65 | 0.63 MVA 20/0.4 kV | 52 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2559011.2045 | 1153060.1046 | 2559015.7227 | 1153063.7363
1 | 2559004.0025 | 1153056.7588 | 2559008.6794 | 1153058.075 | 2559011.2045 | 1153060.1046
2 | 2559015.7227 | 1153063.7363 | 2559027.4908 | 1153073.1954
3 | 2558969.4938 | 1153047.9039 | 2558988.0074 | 1153052.2575 | 2559004.0025 | 1153056.7588
4 | 2558947.9113 | 1153090.7177 | 2558937.2348 | 1153089.0676 | 2558940.9921 | 1153079.7483 | 2558950.2217 | 1153062.7987 | 2558956.2296 | 1153058.311 | 2558962.588 | 1153056.8445 | 2558969.4938 | 1153047.9039
5 | 2559177.7115 | 1153058.7656 | 2559184.1798 | 1153083.0091
6 | 2559138.2657 | 1153077.2354 | 2559177.7115 | 1153058.7656
7 | 2559177.7115 | 1153058.7656 | 2559174.3926 | 1153046.3265
8 | 2559002.5636 | 1153191.1214 | 2559007.1195 | 1153203.0869
9 | 2559002.5636 | 1153191.1214 | 2558999.489 | 1153183.0462 | 2558999.489 | 1153183.0462
10 | 2558947.9113 | 1153090.7177 | 2558984.2682 | 1153117.0385 | 2559000.5476 | 1153126.891
11 | 2559025.1179 | 1153141.7613 | 2559000.5476 | 1153126.891
12 | 2559025.1179 | 1153141.7613 | 2559046.4344 | 1153154.6655
13 | 2559025.1179 | 1153141.7613 | 2558999.489 | 1153183.0462
14 | 2559138.2657 | 1153077.2354 | 2559129.1755 | 1153062.5422
15 | 2559129.1755 | 1153062.5422 | 2559126.6307 | 1153058.4289
16 | 2559119.5246 | 1153136.2711 | 2559138.2657 | 1153077.2354
17 | 2559126.6307 | 1153058.4289 | 2559115.1851 | 1153039.9288 | 2559114.4124 | 1153035.9829
18 | 2559119.5246 | 1153136.2711 | 2559124.2147 | 1153138.7355
19 | 2559088.6578 | 1153119.2871 | 2559107.4731 | 1153129.9386 | 2559119.5246 | 1153136.2711
20 | 2559114.4124 | 1153035.9829 | 2559114.4122 | 1153035.9815
21 | 2559114.4122 | 1153035.9815 | 2559112.0849 | 1153024.0973 | 2559107.5356 | 1153013.3584
22 | 2559107.5356 | 1153013.3584 | 2559106.4546 | 1153010.8066 | 2559101.7022 | 1153001.6089
23 | 2559094.5375 | 1152987.7424 | 2559101.7022 | 1153001.6089
24 | 2559090.921 | 1152980.7431 | 2559094.5375 | 1152987.7424
25 | 2559088.6578 | 1153119.2871 | 2559085.7214 | 1153117.6248 | 2559070.8545 | 1153107.3619
26 | 2559070.8545 | 1153107.3619 | 2559070.715 | 1153107.2656
27 | 2559124.2147 | 1153138.7355 | 2559132.4528 | 1153143.0642 | 2559140.1793 | 1153148.5007
28 | 2559043.4586 | 1153086.0302 | 2559064.7836 | 1153103.1711 | 2559070.715 | 1153107.2656
29 | 2559169.4692 | 1153167.5118 | 2559155.1113 | 1153159.0072 | 2559140.1793 | 1153148.5007
30 | 2559043.4586 | 1153086.0302 | 2559042.3954 | 1153085.1756
31 | 2559169.4692 | 1153167.5118 | 2559173.722 | 1153170.0309
32 | 2559042.3954 | 1153085.1756 | 2559027.4908 | 1153073.1954
33 | 2559206.2431 | 1153234.6296 | 2559141.2441 | 1153207.0567
34 | 2559279.5641 | 1153262.2041 | 2559206.919 | 1153234.9163 | 2559206.2431 | 1153234.6296
35 | 2559123.3742 | 1153199.4762 | 2559141.2441 | 1153207.0567
36 | 2559279.5641 | 1153262.2041 | 2559281.1327 | 1153231.0331
37 | 2559281.1327 | 1153231.0331 | 2559275.3724 | 1153221.1115 | 2559256.1417 | 1153213.9025
38 | 2559236.2224 | 1153205.5114 | 2559250.7881 | 1153211.8957 | 2559256.1417 | 1153213.9025
39 | 2559205.6853 | 1153188.8455 | 2559228.3095 | 1153202.0431 | 2559236.2224 | 1153205.5114
40 | 2559174.1405 | 1153170.2787 | 2559173.722 | 1153170.0309
41 | 2559176.695 | 1153171.7919 | 2559174.1405 | 1153170.2787
42 | 2559165.96 | 1153014.721 | 2559169.1519 | 1153026.6842
43 | 2559165.96 | 1153014.721 | 2559162.0216 | 1152999.9596
44 | 2559174.3926 | 1153046.3265 | 2559169.1519 | 1153026.6842
45 | 2559154.7611 | 1152979.3454 | 2559159.513 | 1152990.5576 | 2559162.0216 | 1152999.9596
46 | 2559154.7611 | 1152979.3454 | 2559153.1676 | 1152975.5856
47 | 2559176.695 | 1153171.7919 | 2559180.68 | 1153174.1523 | 2559181.8264 | 1153174.8259
48 | 2559205.6853 | 1153188.8455 | 2559181.8264 | 1153174.8259
49 | 2559205.6853 | 1153188.8455 | 2559207.2947 | 1153186.3222 | 2559212.378 | 1153176.9958
50 | 2559214.532 | 1153173.044 | 2559212.378 | 1153176.9958

## bus_geodata
| x | y | coords
0 | 2559011.2045 | 1153060.1046
1 | 2559015.7227 | 1153063.7363
2 | 2559004.0025 | 1153056.7588
3 | 2558969.4938 | 1153047.9039
4 | 2559184.1798 | 1153083.0091
5 | 2559177.7115 | 1153058.7656
6 | 2559007.1195 | 1153203.0869
7 | 2559002.5636 | 1153191.1214
8 | 2559000.5476 | 1153126.891
9 | 2558947.9113 | 1153090.7177
10 | 2559025.1179 | 1153141.7613
11 | 2559046.4344 | 1153154.6655
12 | 2558999.489 | 1153183.0462
13 | 2559129.1755 | 1153062.5422
14 | 2559138.2657 | 1153077.2354
15 | 2559126.6307 | 1153058.4289
16 | 2559119.5246 | 1153136.2711
17 | 2559114.4124 | 1153035.9829
18 | 2559114.4122 | 1153035.9815
19 | 2559107.5356 | 1153013.3584
20 | 2559101.7022 | 1153001.6089
21 | 2559094.5375 | 1152987.7424
22 | 2559090.921 | 1152980.7431
23 | 2559088.6578 | 1153119.2871
24 | 2559070.8545 | 1153107.3619
25 | 2559124.2147 | 1153138.7355
26 | 2559070.715 | 1153107.2656
27 | 2559140.1793 | 1153148.5007
28 | 2559043.4586 | 1153086.0302
29 | 2559169.4692 | 1153167.5118
30 | 2559042.3954 | 1153085.1756
31 | 2559027.4908 | 1153073.1954
32 | 2559206.2431 | 1153234.6296
33 | 2559141.2441 | 1153207.0567
34 | 2559279.5641 | 1153262.2041
35 | 2559123.3742 | 1153199.4762
36 | 2559281.1327 | 1153231.0331
37 | 2559256.1417 | 1153213.9025
38 | 2559236.2224 | 1153205.5114
39 | 2559173.722 | 1153170.0309
40 | 2559174.1405 | 1153170.2787
41 | 2559165.96 | 1153014.721
42 | 2559169.1519 | 1153026.6842
43 | 2559162.0216 | 1152999.9596
44 | 2559174.3926 | 1153046.3265
45 | 2559154.7611 | 1152979.3454
46 | 2559153.1676 | 1152975.5856
47 | 2559181.8264 | 1153174.8259
48 | 2559176.695 | 1153171.7919
49 | 2559205.6853 | 1153188.8455
50 | 2559212.378 | 1153176.9958
51 | 2559214.532 | 1153173.044
52 | 2559205.6853 | 1153188.8455

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99484 | -0.098464 | 0.0005559 | 0.00013932
1 | 0.99511 | -0.093244 | 0.00098405 | 0.00024663
2 | 0.99446 | -0.10568 | 0.0015006 | 0.00037609
3 | 0.99285 | -0.13656 | 0 | 0
4 | 0.99289 | -0.13664 | 0.0021408 | 0.00053654
5 | 0.99294 | -0.13569 | 0.0026693 | 0.00066899
6 | 0.98494 | -0.28976 | 0.0078015 | 0.0019552
7 | 0.98503 | -0.28796 | 0.0058639 | 0.0014696
8 | 0.98701 | -0.24952 | 0.021699 | 0.0054384
9 | 0.98989 | -0.19356 | 0 | 0
10 | 0.98628 | -0.26361 | 0 | 0
11 | 0.98624 | -0.26444 | 0.0018708 | 0.00046886
12 | 0.98514 | -0.28584 | 0.011845 | 0.0029687
13 | 0.99338 | -0.1272 | 0.0023706 | 0.00059413
14 | 0.99385 | -0.11801 | 0.0023635 | 0.00059236
15 | 0.99326 | -0.12957 | 0.013209 | 0.0033105
16 | 0.99699 | -0.057554 | 0.00098349 | 0.00024649
17 | 0.99291 | -0.1362 | 0.0033942 | 0.00085066
18 | 0.99291 | -0.1362 | 0.0033934 | 0.00085046
19 | 0.99275 | -0.13946 | 0.0013618 | 0.0003413
20 | 0.99267 | -0.14095 | 0.0023385 | 0.00058607
21 | 0.99261 | -0.14207 | 0.00092588 | 0.00023205
22 | 0.99259 | -0.14251 | 0.0031371 | 0.00078623
23 | 1 | 0 | -0.15996 | -0.040167
24 | 0.99875 | -0.023799 | 0.0021257 | 0.00053275
25 | 0.99681 | -0.060989 | 0.0045952 | 0.0011517
26 | 0.99874 | -0.023981 | 0.0021259 | 0.0005328
27 | 0.99626 | -0.071642 | 0.00058494 | 0.0001466
28 | 0.99685 | -0.0599 | 0.00097285 | 0.00024382
29 | 0.99524 | -0.091166 | 0.00079979 | 0.00020045
30 | 0.99678 | -0.061296 | 0.0044642 | 0.0011188
31 | 0.99583 | -0.0794 | 0.001785 | 0.00044737
32 | 0.99094 | -0.17429 | 0.0048113 | 0.0012058
33 | 0.99009 | -0.19075 | 0.00036147 | 9.0593e-05
34 | 0.99223 | -0.14937 | 0 | 0
35 | 0.98986 | -0.19516 | 0.012764 | 0.003199
36 | 0.99274 | -0.13946 | 0 | 0
37 | 0.99327 | -0.12931 | 0.0015949 | 0.00039971
38 | 0.99365 | -0.12185 | 0.0015943 | 0.00039958
39 | 0.9951 | -0.093862 | 0.00043096 | 0.00010801
40 | 0.99509 | -0.094123 | 0.0018135 | 0.00045452
41 | 0.99225 | -0.14909 | 0.0044777 | 0.0011222
42 | 0.99241 | -0.14595 | 0.0027197 | 0.00068162
43 | 0.99211 | -0.15174 | 0.0029656 | 0.00074324
44 | 0.99273 | -0.13983 | 0.001147 | 0.00028746
45 | 0.99197 | -0.15441 | 0.0037793 | 0.00094717
46 | 0.99196 | -0.15463 | 0.0030824 | 0.00077253
47 | 0.99489 | -0.098087 | 0.0013587 | 0.00034053
48 | 0.99501 | -0.095625 | 0.0052806 | 0.0013234
49 | 0.99433 | -0.10886 | 0 | 0
50 | 0.99431 | -0.10909 | 0.00030001 | 7.519e-05
51 | 0.99431 | -0.10914 | 0.00066113 | 0.0001657
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.051542 | -0.013071 | 0.051555 | 0.01308 | 1.2938e-05 | 8.2051e-06 | 0.077148 | 0.077148 | 0.077148 | 0.99484 | -0.098464 | 0.99511 | -0.093244 | 21.1945
1 | 0.050986 | 0.012932 | -0.050968 | -0.012921 | 1.7687e-05 | 1.1215e-05 | 0.076317 | 0.076317 | 0.076317 | 0.99484 | -0.098464 | 0.99446 | -0.10568 | 20.9661
2 | -0.052539 | -0.013326 | 0.052574 | 0.013349 | 3.4996e-05 | 2.2201e-05 | 0.07862 | 0.078619 | 0.07862 | 0.99511 | -0.093244 | 0.99583 | -0.0794 | 21.5988
3 | 0.049468 | 0.012545 | -0.049395 | -0.012498 | 7.3318e-05 | 4.6462e-05 | 0.074071 | 0.074071 | 0.074071 | 0.99446 | -0.10568 | 0.99285 | -0.13656 | 20.3493
4 | 0.049395 | 0.012498 | -0.04926 | -0.012413 | 0.00013471 | 8.5369e-05 | 0.074071 | 0.074072 | 0.074072 | 0.99285 | -0.13656 | 0.98989 | -0.19356 | 20.3494
5 | -0.0021408 | -0.00053654 | 0.0021409 | 0.00053628 | 9.6854e-08 | -2.6255e-07 | 0.0032084 | 0.0032083 | 0.0032084 | 0.99289 | -0.13664 | 0.99294 | -0.13569 | 0.88142
6 | -0.022995 | -0.0057666 | 0.023014 | 0.0057785 | 1.9397e-05 | 1.185e-05 | 0.034461 | 0.034461 | 0.034461 | 0.99294 | -0.13569 | 0.99385 | -0.11801 | 9.4673
7 | 0.018184 | 0.0045613 | -0.018181 | -0.0045592 | 3.5857e-06 | 2.1283e-06 | 0.027253 | 0.027253 | 0.027253 | 0.99294 | -0.13569 | 0.99273 | -0.13983 | 7.487
8 | -0.0078015 | -0.0019552 | 0.0078022 | 0.0019555 | 6.6697e-07 | 2.6389e-07 | 0.011786 | 0.011786 | 0.011786 | 0.98494 | -0.28976 | 0.98503 | -0.28796 | 3.238
9 | -0.013666 | -0.0034251 | 0.013667 | 0.0034259 | 1.381e-06 | 7.7381e-07 | 0.020644 | 0.020644 | 0.020644 | 0.98503 | -0.28796 | 0.98514 | -0.28584 | 5.6715
10 | -0.049128 | -0.01233 | 0.04926 | 0.012413 | 0.0001315 | 8.3341e-05 | 0.074072 | 0.074072 | 0.074072 | 0.98701 | -0.24952 | 0.98989 | -0.19356 | 20.3495
11 | 0.027429 | 0.0068913 | -0.027411 | -0.0068799 | 1.8422e-05 | 1.1423e-05 | 0.041358 | 0.041358 | 0.041358 | 0.98701 | -0.24952 | 0.98628 | -0.26361 | 11.3621
12 | 0.0018708 | 0.00046859 | -0.0018708 | -0.00046886 | 7.4442e-08 | -2.7035e-07 | 0.0028225 | 0.0028226 | 0.0028226 | 0.98628 | -0.26361 | 0.98624 | -0.26444 | 0.77543
13 | 0.02554 | 0.0064113 | -0.025513 | -0.0063946 | 2.706e-05 | 1.6699e-05 | 0.038536 | 0.038536 | 0.038536 | 0.98628 | -0.26361 | 0.98514 | -0.28584 | 10.5868
14 | -0.03014 | -0.0075564 | 0.030153 | 0.0075646 | 1.3207e-05 | 8.2288e-06 | 0.045149 | 0.045149 | 0.045149 | 0.99338 | -0.1272 | 0.99385 | -0.11801 | 12.4035
15 | 0.027769 | 0.0069623 | -0.027766 | -0.0069603 | 3.1386e-06 | 1.9461e-06 | 0.041598 | 0.041598 | 0.041598 | 0.99338 | -0.1272 | 0.99326 | -0.12957 | 11.428
16 | -0.055531 | -0.013935 | 0.055691 | 0.014037 | 0.00016058 | 0.00010197 | 0.083148 | 0.083148 | 0.083148 | 0.99385 | -0.11801 | 0.99699 | -0.057554 | 22.8429
17 | 0.014557 | 0.0036498 | -0.014553 | -0.0036472 | 4.5974e-06 | 2.6088e-06 | 0.021809 | 0.021809 | 0.021809 | 0.99326 | -0.12957 | 0.99291 | -0.1362 | 5.9915
18 | 0.037096 | 0.0093482 | -0.03709 | -0.0093444 | 6.0942e-06 | 3.8312e-06 | 0.055384 | 0.055384 | 0.055384 | 0.99699 | -0.057554 | 0.99681 | -0.060989 | 15.2153
19 | -0.093771 | -0.023632 | 0.09403 | 0.023797 | 0.00025897 | 0.00016528 | 0.14 | 0.14 | 0.14 | 0.99699 | -0.057554 | 1 | 0 | 38.4614
20 | 0.011159 | 0.0027966 | -0.011159 | -0.0027966 | 1.5604e-10 | 9.9867e-11 | 0.016723 | 0.016723 | 0.016723 | 0.99291 | -0.1362 | 0.99291 | -0.1362 | 4.5941
21 | 0.0077651 | 0.0019461 | -0.0077639 | -0.0019456 | 1.2073e-06 | 4.6523e-07 | 0.011637 | 0.011637 | 0.011637 | 0.99291 | -0.1362 | 0.99275 | -0.13946 | 3.197
22 | 0.0064022 | 0.0016043 | -0.0064017 | -0.0016042 | 4.532e-07 | 1.2037e-07 | 0.0095961 | 0.0095961 | 0.0095961 | 0.99275 | -0.13946 | 0.99267 | -0.14095 | 2.6363
23 | 0.0040632 | 0.0010182 | -0.004063 | -0.0010182 | 2.1713e-07 | -6.2798e-08 | 0.0060908 | 0.0060908 | 0.0060908 | 0.99267 | -0.14095 | 0.99261 | -0.14207 | 1.6733
24 | 0.0031372 | 0.00078617 | -0.0031371 | -0.00078623 | 6.5342e-08 | -6.0015e-08 | 0.0047029 | 0.0047029 | 0.0047029 | 0.99261 | -0.14207 | 0.99259 | -0.14251 | 1.292
25 | 0.064277 | 0.01637 | -0.064203 | -0.016323 | 7.369e-05 | 4.6881e-05 | 0.095737 | 0.095737 | 0.095737 | 1 | 0 | 0.99875 | -0.023799 | 26.3014
26 | 0.062078 | 0.01579 | -0.062077 | -0.01579 | 5.4456e-07 | 3.463e-07 | 0.09257 | 0.09257 | 0.09257 | 0.99875 | -0.023799 | 0.99874 | -0.023981 | 25.4314
27 | 0.032495 | 0.0081927 | -0.032478 | -0.0081823 | 1.6559e-05 | 1.0353e-05 | 0.048524 | 0.048524 | 0.048524 | 0.99681 | -0.060989 | 0.99626 | -0.071642 | 13.3309
28 | 0.059951 | 0.015257 | -0.059847 | -0.015191 | 0.00010361 | 6.5859e-05 | 0.089403 | 0.089403 | 0.089403 | 0.99874 | -0.023981 | 0.99685 | -0.0599 | 24.5613
29 | 0.031893 | 0.0080357 | -0.031863 | -0.0080172 | 2.9755e-05 | 1.8589e-05 | 0.047651 | 0.047651 | 0.047651 | 0.99626 | -0.071642 | 0.99524 | -0.091166 | 13.0909
30 | 0.058875 | 0.014947 | -0.058871 | -0.014945 | 3.9571e-06 | 2.5147e-06 | 0.087951 | 0.087951 | 0.087951 | 0.99685 | -0.0599 | 0.99678 | -0.061296 | 24.1623
31 | 0.031064 | 0.0078167 | -0.03106 | -0.0078142 | 4.0001e-06 | 2.4959e-06 | 0.046455 | 0.046455 | 0.046455 | 0.99524 | -0.091166 | 0.9951 | -0.093862 | 12.7624
32 | 0.054406 | 0.013826 | -0.054359 | -0.013796 | 4.7382e-05 | 3.0076e-05 | 0.081287 | 0.081287 | 0.081287 | 0.99678 | -0.061296 | 0.99583 | -0.0794 | 22.3315
33 | 0.013139 | 0.0032968 | -0.013128 | -0.0032911 | 1.0308e-05 | 5.6882e-06 | 0.019731 | 0.019731 | 0.019731 | 0.99094 | -0.17429 | 0.99009 | -0.19075 | 5.4206
34 | -0.01795 | -0.0045026 | 0.017971 | 0.0045153 | 2.1344e-05 | 1.265e-05 | 0.026956 | 0.026955 | 0.026956 | 0.99094 | -0.17429 | 0.99223 | -0.14937 | 7.4054
35 | 0.012767 | 0.0032005 | -0.012764 | -0.003199 | 2.68e-06 | 1.4656e-06 | 0.019188 | 0.019188 | 0.019188 | 0.99009 | -0.19075 | 0.98986 | -0.19516 | 5.2714
36 | -0.017971 | -0.0045153 | 0.01798 | 0.0045203 | 8.5059e-06 | 5.0403e-06 | 0.026955 | 0.026955 | 0.026955 | 0.99223 | -0.14937 | 0.99274 | -0.13946 | 7.4053
37 | -0.01798 | -0.0045203 | 0.017989 | 0.0045255 | 8.7216e-06 | 5.1677e-06 | 0.026955 | 0.026955 | 0.026955 | 0.99274 | -0.13946 | 0.99327 | -0.12931 | 7.4052
38 | -0.019583 | -0.0049252 | 0.01959 | 0.0049294 | 6.9814e-06 | 4.1882e-06 | 0.029344 | 0.029344 | 0.029344 | 0.99327 | -0.12931 | 0.99365 | -0.12185 | 8.0616
39 | -0.021185 | -0.0053289 | 0.021198 | 0.0053369 | 1.3152e-05 | 7.9658e-06 | 0.031732 | 0.031731 | 0.031732 | 0.99365 | -0.12185 | 0.99433 | -0.10886 | 8.7175
40 | 0.030629 | 0.0077062 | -0.030628 | -0.007706 | 3.8279e-07 | 2.3866e-07 | 0.045811 | 0.045811 | 0.045811 | 0.9951 | -0.093862 | 0.99509 | -0.094123 | 12.5853
41 | 0.028815 | 0.0072515 | -0.028813 | -0.0072502 | 2.0681e-06 | 1.285e-06 | 0.043099 | 0.043099 | 0.043099 | 0.99509 | -0.094123 | 0.99501 | -0.095625 | 11.8403
42 | -0.014307 | -0.003586 | 0.014309 | 0.0035872 | 2.1374e-06 | 1.208e-06 | 0.021456 | 0.021456 | 0.021456 | 0.99225 | -0.14909 | 0.99241 | -0.14595 | 5.8944
43 | 0.0098294 | 0.0024638 | -0.0098282 | -0.0024632 | 1.2449e-06 | 5.9941e-07 | 0.014741 | 0.014741 | 0.014741 | 0.99225 | -0.14909 | 0.99211 | -0.15174 | 4.0497
44 | -0.017029 | -0.0042688 | 0.017034 | 0.0042717 | 4.9702e-06 | 2.9182e-06 | 0.025533 | 0.025533 | 0.025533 | 0.99241 | -0.14595 | 0.99273 | -0.13983 | 7.0147
45 | 0.0068626 | 0.0017199 | -0.0068617 | -0.0017197 | 8.704e-07 | 2.7419e-07 | 0.010293 | 0.010293 | 0.010293 | 0.99211 | -0.15174 | 0.99197 | -0.15441 | 2.8277
46 | 0.0030825 | 0.0007725 | -0.0030824 | -0.00077253 | 3.2741e-08 | -3.1763e-08 | 0.0046239 | 0.0046239 | 0.0046239 | 0.99197 | -0.15441 | 0.99196 | -0.15463 | 1.2703
47 | -0.023529 | -0.005925 | 0.023532 | 0.0059267 | 2.7701e-06 | 1.6955e-06 | 0.035202 | 0.035202 | 0.035202 | 0.99489 | -0.098087 | 0.99501 | -0.095625 | 9.6708
48 | 0.022171 | 0.0055845 | -0.022159 | -0.0055776 | 1.1417e-05 | 6.948e-06 | 0.03317 | 0.03317 | 0.03317 | 0.99489 | -0.098087 | 0.99433 | -0.10886 | 9.1126
49 | 0.00096116 | 0.00024066 | -0.00096115 | -0.00024083 | 1.0562e-08 | -1.6983e-07 | 0.0014383 | 0.0014384 | 0.0014384 | 0.99433 | -0.10886 | 0.99431 | -0.10909 | 0.39515
50 | 0.00066113 | 0.00016564 | -0.00066113 | -0.0001657 | 1.6521e-09 | -5.7318e-08 | 0.00098938 | 0.00098941 | 0.00098941 | 0.99431 | -0.10909 | 0.99431 | -0.10914 | 0.27181

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16076 | 0.040369

## res_load
| p_mw | q_mvar
0 | 0.0005559 | 0.00013932
1 | 0.00098405 | 0.00024663
2 | 0.0015006 | 0.00037609
3 | 0.0021408 | 0.00053654
4 | 0.0026693 | 0.00066899
5 | 0.0078015 | 0.0019552
6 | 0.0058639 | 0.0014696
7 | 0.021699 | 0.0054384
8 | 0.0018708 | 0.00046886
9 | 0.011845 | 0.0029687
10 | 0.0023706 | 0.00059413
11 | 0.0023635 | 0.00059236
12 | 0.013209 | 0.0033105
13 | 0.00098349 | 0.00024649
14 | 0.0033942 | 0.00085066
15 | 0.0033934 | 0.00085046
16 | 0.0013618 | 0.0003413
17 | 0.0023385 | 0.00058607
18 | 0.00092588 | 0.00023205
19 | 0.0031371 | 0.00078623
20 | 0.00080561 | 0.00020191
21 | 0.0021257 | 0.00053275
22 | 0.0045952 | 0.0011517
23 | 0.0021259 | 0.0005328
24 | 0.00058494 | 0.0001466
25 | 0.00097285 | 0.00024382
26 | 0.00079979 | 0.00020045
27 | 0.0044642 | 0.0011188
28 | 0.001785 | 0.00044737
29 | 0.0048113 | 0.0012058
30 | 0.00036147 | 9.0593e-05
31 | 0.012764 | 0.003199
32 | 0.0015949 | 0.00039971
33 | 0.0015943 | 0.00039958
34 | 0.00043096 | 0.00010801
35 | 0.0018135 | 0.00045452
36 | 0.0044777 | 0.0011222
37 | 0.0027197 | 0.00068162
38 | 0.0029656 | 0.00074324
39 | 0.001147 | 0.00028746
40 | 0.0037793 | 0.00094717
41 | 0.0030824 | 0.00077253
42 | 0.0013587 | 0.00034053
43 | 0.0052806 | 0.0013234
44 | 0.00030001 | 7.519e-05
45 | 0.00066113 | 0.0001657

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1