## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-13_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-13_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-13_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2325-13_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2325-13_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2325-13_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2325-13_0_4_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_2325-13_0_4_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_2325-13_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_2325-13_0_4_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_2325-13_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_2325-13_0_4_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_2325-13_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2325-13_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2325-13_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2325-13_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2325-13_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2325-13_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2325-13_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_2325-13_0_4_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_2325-13_0_4_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_2325-13_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_2325-13_0_4_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_2325-13_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2325-13_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_2325-13_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2325-13_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2325-13_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2325-13_0_4_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_2325-13_0_4_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_2325-13_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2325-13_0_4_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_2325-13_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2325-13_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2325-13_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_2325-13_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_2325-13_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_2325-13_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2325-13_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2325-13_0_4_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_2325-13_0_4_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_2325-13_0_4_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_2325-13_0_4_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_2325-13_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_MV_37_0_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-13_0_4_load_0 | 0 | 0.0030307 | 0.00075956 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-13_0_4_load_1 | 1 | 0.0014652 | 0.00036721 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-13_0_4_load_2 | 2 | 0.0024061 | 0.00060301 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-13_0_4_load_4 | 4 | 0.0023822 | 0.00059704 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-13_0_4_load_5 | 5 | 0.0015488 | 0.00038817 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-13_0_4_load_26 | 7 | 0.0024226 | 0.00060716 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-13_0_4_load_25 | 10 | 0.00073538 | 0.0001843 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-13_0_4_load_22 | 11 | 0.080893 | 0.020274 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-13_0_4_load_6 | 12 | 0.0068216 | 0.0017096 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-13_0_4_load_7 | 13 | 0.009966 | 0.0024977 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-13_0_4_load_8 | 14 | 0.0043684 | 0.0010948 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-13_0_4_load_9 | 15 | 0.0049528 | 0.0012413 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-13_0_4_load_10 | 16 | 0.010745 | 0.002693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-13_0_4_load_19 | 18 | 0.0042404 | 0.0010627 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-13_0_4_load_37 | 19 | 0.0077027 | 0.0019305 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-13_0_4_load_35 | 20 | 0.0072747 | 0.0018232 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-13_0_4_load_21 | 21 | 0.0016007 | 0.00040119 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-13_0_4_load_40 | 22 | 0.0023504 | 0.00058907 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-13_0_4_load_13 | 23 | 0.0070511 | 0.0017672 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-13_0_4_load_14 | 24 | 0.0031671 | 0.00079376 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-13_0_4_load_17 | 26 | 0.0061281 | 0.0015358 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-13_0_4_load_18 | 27 | 0.0049471 | 0.0012398 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-13_0_4_load_44 | 28 | 0.0045898 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-13_0_4_load_41 | 29 | 0.022538 | 0.0056487 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-13_0_4_load_27 | 30 | 0.00094352 | 0.00023647 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-13_0_4_load_45 | 31 | 0.00096585 | 0.00024207 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-13_0_4_load_28 | 32 | 0.015924 | 0.003991 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-13_0_4_load_29 | 33 | 0.0925 | 0.023183 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-13_0_4_load_31 | 35 | 0.012738 | 0.0031924 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-13_0_4_load_33 | 37 | 0.0059356 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-13_0_4_load_34 | 38 | 0.0025471 | 0.00063836 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-13_0_4_load_43 | 39 | 0.010763 | 0.0026974 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-13_0_4_load_38 | 40 | 0.0060173 | 0.0015081 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-13_0_4_load_42 | 41 | 0.0051133 | 0.0012815 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-13_0_4_load_39 | 43 | 0.009516 | 0.0023849 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-13_0_4_line_0 |  | 0 | 1 | 0.0093532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-13_0_4_line_1 |  | 0 | 2 | 0.015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-13_0_4_line_2 |  | 2 | 3 | 0.0035131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-13_0_4_line_3 |  | 3 | 4 | 0.011287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-13_0_4_line_4 |  | 3 | 5 | 0.023199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-13_0_4_line_5 |  | 4 | 6 | 0.043328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-13_0_4_line_6 |  | 5 | 7 | 0.022757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-13_0_4_line_7 |  | 6 | 8 | 0.029173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-13_0_4_line_8 |  | 7 | 9 | 0.034353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-13_0_4_line_9 |  | 8 | 18 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-13_0_4_line_10 |  | 8 | 15 | 0.005167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-13_0_4_line_11 |  | 9 | 10 | 0.03397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-13_0_4_line_12 |  | 9 | 11 | 0.010844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-13_0_4_line_13 |  | 10 | 30 | 0.032465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-13_0_4_line_14 |  | 12 | 13 | 0.0082251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-13_0_4_line_15 |  | 12 | 14 | 0.0035617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-13_0_4_line_16 |  | 13 | 15 | 0.035841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-13_0_4_line_17 |  | 14 | 16 | 0.019466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-13_0_4_line_18 |  | 16 | 17 | 0.0049681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_2325-13_0_4_line_19 |  | 17 | 19 | 0.0060546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2325-13_0_4_line_20 |  | 17 | 20 | 0.0048329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-13_0_4_line_21 |  | 18 | 21 | 0.026922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-13_0_4_line_22 |  | 19 | 22 | 0.0025952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2325-13_0_4_line_23 |  | 22 | 41 | 0.0063217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2325-13_0_4_line_24 |  | 23 | 24 | 0.015279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-13_0_4_line_25 |  | 23 | 25 | 0.0048285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-13_0_4_line_26 |  | 25 | 26 | 0.01607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-13_0_4_line_27 |  | 26 | 27 | 0.0071301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-13_0_4_line_28 |  | 27 | 28 | 0.005899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-13_0_4_line_29 |  | 28 | 29 | 0.0063903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-13_0_4_line_30 |  | 29 | 43 | 0.0013898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-13_0_4_line_31 |  | 30 | 31 | 0.022935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-13_0_4_line_32 |  | 32 | 33 | 0.0090543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-13_0_4_line_33 |  | 32 | 34 | 0.015204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-13_0_4_line_34 |  | 33 | 35 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_2325-13_0_4_line_35 |  | 34 | 36 | 0.01287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-13_0_4_line_36 |  | 35 | 37 | 0.0018843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_2325-13_0_4_line_37 |  | 36 | 38 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-13_0_4_line_38 |  | 37 | 39 | 0.0054923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2325-13_0_4_line_39 |  | 38 | 40 | 0.0072209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-13_0_4_line_40 |  | 39 | 41 | 0.0038884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2325-13_0_4_line_41 |  | 40 | 42 | 0.0073768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-13_0_4_line_42 |  | 42 | 43 | 0.029311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-13_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 44 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2558988.0074 | 1153052.2575 | 2558997.0109 | 1153054.7912
1 | 2558972.9137 | 1153048.7081 | 2558988.0074 | 1153052.2575 | 2558988.0074 | 1153052.2575
2 | 2558969.4938 | 1153047.9039 | 2558972.9137 | 1153048.7081
3 | 2558969.4938 | 1153047.9039 | 2558962.588 | 1153056.8445
4 | 2558969.4938 | 1153047.9039 | 2558963.851 | 1153045.1744 | 2558949.0863 | 1153036.8883
5 | 2558937.2348 | 1153089.0676 | 2558940.9921 | 1153079.7483 | 2558950.2217 | 1153062.7987 | 2558956.2296 | 1153058.311 | 2558962.588 | 1153056.8445
6 | 2558949.0863 | 1153036.8883 | 2558939.6423 | 1153031.5884 | 2558930.3283 | 1153024.1376
7 | 2558937.2348 | 1153089.0676 | 2558933.2932 | 1153090.5175 | 2558911.0052 | 1153101.9313
8 | 2558904.0836 | 1153002.0497 | 2558910.0794 | 1153008.1229 | 2558913.5036 | 1153010.6786 | 2558930.3283 | 1153024.1376
9 | 2558911.0052 | 1153101.9313 | 2558911.0138 | 1153108.8015 | 2558914.7692 | 1153119.1892
10 | 2558911.0052 | 1153101.9313 | 2558908.096 | 1153099.5167 | 2558907.4276 | 1153098.3021
11 | 2558904.0836 | 1153002.0497 | 2558918.1489 | 1152987.5905 | 2558929.9779 | 1152980.4872
12 | 2558904.0836 | 1153002.0497 | 2558893.2468 | 1153001.6569
13 | 2558929.9779 | 1152980.4872 | 2558954.4768 | 1152965.7755 | 2558957.3235 | 1152963.1264
14 | 2558878.3682 | 1153110.2144 | 2558878.3682 | 1153110.2144 | 2558880.8642 | 1153102.3773
15 | 2558876.0367 | 1153112.907 | 2558878.3682 | 1153110.2144
16 | 2558880.8642 | 1153102.3773 | 2558881.26 | 1153101.1344 | 2558900.5057 | 1153089.141 | 2558903.1469 | 1153090.5237 | 2558907.4276 | 1153098.3021
17 | 2558858.5196 | 1153118.8652 | 2558860.68 | 1153118.8066 | 2558867.3528 | 1153118.4496 | 2558873.1003 | 1153116.2981 | 2558876.0367 | 1153112.907
18 | 2558853.5533 | 1153119 | 2558858.5196 | 1153118.8652
19 | 2558853.5533 | 1153119 | 2558853.8118 | 1153113.0618 | 2558853.7503 | 1153112.9696
20 | 2558853.5533 | 1153119 | 2558848.9226 | 1153120.3834
21 | 2558914.7692 | 1153119.1892 | 2558917.3721 | 1153126.3892 | 2558917.0471 | 1153129.3485 | 2558911.879 | 1153137.6882 | 2558912.4104 | 1153144.1437
22 | 2558852.3101 | 1153110.8107 | 2558853.7503 | 1153112.9696
23 | 2558848.8019 | 1153105.5517 | 2558852.3101 | 1153110.8107
24 | 2558870.6771 | 1153188.3005 | 2558874.8026 | 1153197.9283 | 2558876.4685 | 1153202.435
25 | 2558868.7753 | 1153183.8623 | 2558870.6771 | 1153188.3005
26 | 2558868.7753 | 1153183.8623 | 2558863.8366 | 1153173.0239 | 2558861.7064 | 1153169.4516
27 | 2558858.0547 | 1153163.3276 | 2558861.7064 | 1153169.4516
28 | 2558858.0547 | 1153163.3276 | 2558857.3865 | 1153162.207 | 2558854.81 | 1153158.4032
29 | 2558851.2262 | 1153153.1123 | 2558854.81 | 1153158.4032
30 | 2558851.2262 | 1153153.1123 | 2558850.4468 | 1153151.9617
31 | 2558974.1137 | 1152947.502 | 2558957.3235 | 1152963.1264
32 | 2558834.4928 | 1153084.1015 | 2558827.9435 | 1153087.9373 | 2558826.6147 | 1153088.5526
33 | 2558813.2498 | 1153095.7197 | 2558818.3676 | 1153092.3718 | 2558826.6147 | 1153088.5526
34 | 2558834.4928 | 1153084.1015 | 2558834.4928 | 1153084.1015 | 2558842.5505 | 1153096.1805
35 | 2558820.3135 | 1153106.488 | 2558813.2498 | 1153095.7197
36 | 2558843.5962 | 1153097.748 | 2558842.5505 | 1153096.1805
37 | 2558820.3135 | 1153106.488 | 2558825.9057 | 1153115.5664
38 | 2558843.5962 | 1153097.748 | 2558846.6441 | 1153102.317
39 | 2558825.9057 | 1153115.5664 | 2558829.6928 | 1153121.7145
40 | 2558848.8019 | 1153105.5517 | 2558846.6441 | 1153102.317
41 | 2558834.009 | 1153127.6939 | 2558830.1056 | 1153122.3846 | 2558829.6928 | 1153121.7145
42 | 2558834.009 | 1153127.6939 | 2558850.4468 | 1153151.9617

## bus_geodata
| x | y | coords
0 | 2558988.0074 | 1153052.2575
1 | 2558997.0109 | 1153054.7912
2 | 2558972.9137 | 1153048.7081
3 | 2558969.4938 | 1153047.9039
4 | 2558962.588 | 1153056.8445
5 | 2558949.0863 | 1153036.8883
6 | 2558937.2348 | 1153089.0676
7 | 2558930.3283 | 1153024.1376
8 | 2558911.0052 | 1153101.9313
9 | 2558904.0836 | 1153002.0497
10 | 2558929.9779 | 1152980.4872
11 | 2558893.2468 | 1153001.6569
12 | 2558878.3682 | 1153110.2144
13 | 2558880.8642 | 1153102.3773
14 | 2558876.0367 | 1153112.907
15 | 2558907.4276 | 1153098.3021
16 | 2558858.5196 | 1153118.8652
17 | 2558853.5533 | 1153119
18 | 2558914.7692 | 1153119.1892
19 | 2558853.7503 | 1153112.9696
20 | 2558848.9226 | 1153120.3834
21 | 2558912.4104 | 1153144.1437
22 | 2558852.3101 | 1153110.8107
23 | 2558870.6771 | 1153188.3005
24 | 2558876.4685 | 1153202.435
25 | 2558868.7753 | 1153183.8623
26 | 2558861.7064 | 1153169.4516
27 | 2558858.0547 | 1153163.3276
28 | 2558854.81 | 1153158.4032
29 | 2558851.2262 | 1153153.1123
30 | 2558957.3235 | 1152963.1264
31 | 2558974.1137 | 1152947.502
32 | 2558826.6147 | 1153088.5526
33 | 2558834.4928 | 1153084.1015
34 | 2558813.2498 | 1153095.7197
35 | 2558842.5505 | 1153096.1805
36 | 2558820.3135 | 1153106.488
37 | 2558843.5962 | 1153097.748
38 | 2558825.9057 | 1153115.5664
39 | 2558846.6441 | 1153102.317
40 | 2558829.6928 | 1153121.7145
41 | 2558848.8019 | 1153105.5517
42 | 2558834.009 | 1153127.6939
43 | 2558850.4468 | 1153151.9617
44 | 2558853.5533 | 1153119

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98244 | -0.33575 | 0.0030307 | 0.00075956
1 | 0.98243 | -0.336 | 0.0014652 | 0.00036721
2 | 0.9825 | -0.33449 | 0.0024061 | 0.00060301
3 | 0.98252 | -0.33406 | 0 | 0
4 | 0.98352 | -0.31483 | 0.0023822 | 0.00059704
5 | 0.98064 | -0.37078 | 0.0015488 | 0.00038817
6 | 0.98741 | -0.23956 | 0 | 0
7 | 0.97882 | -0.40631 | 0.0024226 | 0.00060716
8 | 0.99004 | -0.18921 | 0 | 0
9 | 0.97615 | -0.45866 | 0 | 0
10 | 0.97607 | -0.4603 | 0.00073538 | 0.0001843
11 | 0.97533 | -0.47472 | 0.080893 | 0.020274
12 | 0.99501 | -0.094484 | 0.0068216 | 0.0017096
13 | 0.99411 | -0.11152 | 0.009966 | 0.0024977
14 | 0.99542 | -0.086688 | 0.0043684 | 0.0010948
15 | 0.99053 | -0.17978 | 0.0049528 | 0.0012413
16 | 0.99774 | -0.042702 | 0.010745 | 0.002693
17 | 0.99806 | -0.036637 | 0 | 0
18 | 0.98994 | -0.19107 | 0.0042404 | 0.0010627
19 | 0.99847 | -0.028866 | 0.0077027 | 0.0019305
20 | 0.99803 | -0.037252 | 0.0072747 | 0.0018232
21 | 0.9899 | -0.19184 | 0.0016007 | 0.00040119
22 | 0.99866 | -0.025362 | 0.0023504 | 0.00058907
23 | 0.99282 | -0.13814 | 0.0070511 | 0.0017672
24 | 0.99278 | -0.13899 | 0.0031671 | 0.00079376
25 | 0.99287 | -0.13726 | 0 | 0
26 | 0.99302 | -0.13436 | 0.0061281 | 0.0015358
27 | 0.99312 | -0.1323 | 0.0049471 | 0.0012398
28 | 0.99324 | -0.13008 | 0.0045898 | 0.0011503
29 | 0.99339 | -0.12716 | 0.022538 | 0.0056487
30 | 0.97601 | -0.46144 | 0.00094352 | 0.00023647
31 | 0.97599 | -0.46184 | 0.00096585 | 0.00024207
32 | 0.99816 | -0.035208 | 0.015924 | 0.003991
33 | 0.99884 | -0.022161 | 0.0925 | 0.023183
34 | 0.99724 | -0.052914 | 0 | 0
35 | 1 | 0 | -0.35814 | -0.090482
36 | 0.99646 | -0.067927 | 0 | 0
37 | 0.99984 | -0.0029339 | 0.0059356 | 0.0014876
38 | 0.99581 | -0.080382 | 0.0025471 | 0.00063836
39 | 0.99941 | -0.011207 | 0.010763 | 0.0026974
40 | 0.99539 | -0.088503 | 0.0060173 | 0.0015081
41 | 0.99912 | -0.016702 | 0.0051133 | 0.0012815
42 | 0.995 | -0.096025 | 0 | 0
43 | 0.99345 | -0.12597 | 0.009516 | 0.0023849
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0014652 | 0.00036711 | -0.0014652 | -0.00036721 | 1.7274e-08 | -1.0738e-07 | 0.0022192 | 0.0022192 | 0.0022192 | 0.98244 | -0.33575 | 0.98243 | -0.336 | 0.60968
1 | -0.0044959 | -0.0011267 | 0.0044961 | 0.0011266 | 2.6961e-07 | -2.3799e-08 | 0.0068095 | 0.0068094 | 0.0068095 | 0.98244 | -0.33575 | 0.9825 | -0.33449 | 1.8707
2 | -0.0069022 | -0.0017297 | 0.0069023 | 0.0017297 | 1.4396e-07 | 4.7642e-08 | 0.010453 | 0.010453 | 0.010453 | 0.9825 | -0.33449 | 0.98252 | -0.33406 | 2.8718
3 | -0.094985 | -0.024026 | 0.095073 | 0.024082 | 8.7685e-05 | 5.5976e-05 | 0.14393 | 0.14393 | 0.14393 | 0.98252 | -0.33406 | 0.98352 | -0.31483 | 39.5419
4 | 0.088083 | 0.022297 | -0.087928 | -0.022198 | 0.000155 | 9.8907e-05 | 0.13348 | 0.13348 | 0.13348 | 0.98252 | -0.33406 | 0.98064 | -0.37078 | 36.6701
5 | -0.097455 | -0.024679 | 0.097809 | 0.024905 | 0.00035367 | 0.0002258 | 0.14754 | 0.14754 | 0.14754 | 0.98352 | -0.31483 | 0.98741 | -0.23956 | 40.532
6 | 0.086379 | 0.021809 | -0.086232 | -0.021716 | 0.00014674 | 9.3626e-05 | 0.13113 | 0.13113 | 0.13113 | 0.98064 | -0.37078 | 0.97882 | -0.40631 | 36.0245
7 | -0.097809 | -0.024905 | 0.098047 | 0.025057 | 0.00023813 | 0.00015203 | 0.14754 | 0.14754 | 0.14754 | 0.98741 | -0.23956 | 0.99004 | -0.18921 | 40.532
8 | 0.08381 | 0.021109 | -0.0836 | -0.020975 | 0.00020924 | 0.00013348 | 0.12745 | 0.12745 | 0.12745 | 0.97882 | -0.40631 | 0.97615 | -0.45866 | 35.0128
9 | 0.0058417 | 0.0014637 | -0.0058412 | -0.0014636 | 5.179e-07 | 1.0109e-07 | 0.0087798 | 0.0087799 | 0.0087799 | 0.99004 | -0.18921 | 0.98994 | -0.19107 | 2.4121
10 | -0.10389 | -0.026521 | 0.10394 | 0.026551 | 4.7346e-05 | 3.0235e-05 | 0.15632 | 0.15632 | 0.15632 | 0.99004 | -0.18921 | 0.99053 | -0.17978 | 42.944
11 | 0.0026451 | 0.00066193 | -0.0026449 | -0.00066222 | 2.0707e-07 | -2.9209e-07 | 0.0040317 | 0.0040319 | 0.0040319 | 0.97615 | -0.45866 | 0.97607 | -0.4603 | 1.1077
12 | 0.080955 | 0.020313 | -0.080893 | -0.020274 | 6.1937e-05 | 3.9504e-05 | 0.12341 | 0.12341 | 0.12341 | 0.97615 | -0.45866 | 0.97533 | -0.47472 | 33.9051
13 | 0.0019095 | 0.00047792 | -0.0019094 | -0.00047826 | 1.0316e-07 | -3.3973e-07 | 0.0029108 | 0.002911 | 0.002911 | 0.97607 | -0.4603 | 0.97601 | -0.46144 | 0.79971
14 | 0.11931 | 0.030583 | -0.11921 | -0.03052 | 9.8467e-05 | 6.2912e-05 | 0.17867 | 0.17867 | 0.17867 | 0.99501 | -0.094484 | 0.99411 | -0.11152 | 49.086
15 | -0.12614 | -0.032293 | 0.12618 | 0.032323 | 4.7647e-05 | 3.0448e-05 | 0.18887 | 0.18887 | 0.18887 | 0.99501 | -0.094484 | 0.99542 | -0.086688 | 51.8886
16 | 0.10925 | 0.028023 | -0.10889 | -0.027792 | 0.00036042 | 0.0002302 | 0.16376 | 0.16376 | 0.16376 | 0.99411 | -0.11152 | 0.99053 | -0.17978 | 44.988
17 | -0.13055 | -0.033418 | 0.13083 | 0.033596 | 0.00027873 | 0.00017813 | 0.1954 | 0.1954 | 0.1954 | 0.99542 | -0.086688 | 0.99774 | -0.042702 | 53.6826
18 | -0.14158 | -0.036289 | 0.14162 | 0.036316 | 4.1641e-05 | 2.652e-05 | 0.21143 | 0.21143 | 0.21143 | 0.99774 | -0.042702 | 0.99806 | -0.036637 | 29.0425
19 | -0.14889 | -0.038139 | 0.14895 | 0.038175 | 5.6088e-05 | 3.5738e-05 | 0.22228 | 0.22228 | 0.22228 | 0.99806 | -0.036637 | 0.99847 | -0.028866 | 30.5323
20 | 0.0072749 | 0.0018233 | -0.0072747 | -0.0018232 | 2.132e-07 | 7.3292e-08 | 0.010846 | 0.010846 | 0.010846 | 0.99806 | -0.036637 | 0.99803 | -0.037252 | 2.9797
21 | 0.0016008 | 0.00040088 | -0.0016007 | -0.00040119 | 5.845e-08 | -3.087e-07 | 0.0024061 | 0.0024062 | 0.0024062 | 0.98994 | -0.19107 | 0.9899 | -0.19184 | 0.66105
22 | -0.15665 | -0.040105 | 0.15668 | 0.040122 | 2.6588e-05 | 1.6949e-05 | 0.23375 | 0.23375 | 0.23375 | 0.99847 | -0.028866 | 0.99866 | -0.025362 | 32.1091
23 | -0.15903 | -0.040711 | 0.15909 | 0.040754 | 6.6723e-05 | 4.2537e-05 | 0.23726 | 0.23726 | 0.23726 | 0.99866 | -0.025362 | 0.99912 | -0.016702 | 32.5902
24 | 0.0031673 | 0.00079364 | -0.0031671 | -0.00079376 | 1.2911e-07 | -1.1494e-07 | 0.004747 | 0.004747 | 0.004747 | 0.99282 | -0.13814 | 0.99278 | -0.13899 | 1.3041
25 | -0.010218 | -0.0025608 | 0.010219 | 0.002561 | 4.2469e-07 | 2.0936e-07 | 0.015315 | 0.015315 | 0.015315 | 0.99282 | -0.13814 | 0.99287 | -0.13726 | 4.2074
26 | -0.010219 | -0.002561 | 0.01022 | 0.0025617 | 1.4134e-06 | 6.9673e-07 | 0.015315 | 0.015315 | 0.015315 | 0.99287 | -0.13726 | 0.99302 | -0.13436 | 4.2074
27 | -0.016348 | -0.0040976 | 0.01635 | 0.0040985 | 1.6047e-06 | 9.3473e-07 | 0.024498 | 0.024498 | 0.024498 | 0.99302 | -0.13436 | 0.99312 | -0.1323 | 6.7302
28 | -0.021297 | -0.0053384 | 0.021299 | 0.0053397 | 2.2525e-06 | 1.3652e-06 | 0.03191 | 0.03191 | 0.03191 | 0.99312 | -0.1323 | 0.99324 | -0.13008 | 8.7665
29 | -0.025889 | -0.00649 | 0.025893 | 0.0064923 | 3.605e-06 | 2.2245e-06 | 0.038786 | 0.038786 | 0.038786 | 0.99324 | -0.13008 | 0.99339 | -0.12716 | 10.6555
30 | -0.048431 | -0.012141 | 0.048434 | 0.012143 | 2.7429e-06 | 1.7375e-06 | 0.072547 | 0.072547 | 0.072547 | 0.99339 | -0.12716 | 0.99345 | -0.12597 | 19.9304
31 | 0.00096587 | 0.00024179 | -0.00096585 | -0.00024207 | 1.8649e-08 | -2.7469e-07 | 0.0014725 | 0.0014726 | 0.0014726 | 0.97601 | -0.46144 | 0.97599 | -0.46184 | 0.40455
32 | -0.082711 | -0.020838 | 0.082763 | 0.020871 | 5.1653e-05 | 3.2939e-05 | 0.12334 | 0.12334 | 0.12334 | 0.99816 | -0.035208 | 0.99884 | -0.022161 | 33.8846
33 | 0.066787 | 0.016847 | -0.06673 | -0.016811 | 5.6561e-05 | 3.6001e-05 | 0.099601 | 0.099601 | 0.099601 | 0.99816 | -0.035208 | 0.99724 | -0.052914 | 27.363
34 | -0.17526 | -0.044054 | 0.17545 | 0.044173 | 0.00018566 | 0.00011844 | 0.26114 | 0.26114 | 0.26114 | 0.99884 | -0.022161 | 1 | 0 | 35.871
35 | 0.06673 | 0.016811 | -0.066682 | -0.016781 | 4.7878e-05 | 3.0474e-05 | 0.099601 | 0.099601 | 0.099601 | 0.99724 | -0.052914 | 0.99646 | -0.067927 | 27.363
36 | 0.18105 | 0.046309 | -0.18102 | -0.046293 | 2.5704e-05 | 1.6401e-05 | 0.26973 | 0.26973 | 0.26973 | 1 | 0 | 0.99984 | -0.0029339 | 37.0507
37 | 0.066682 | 0.016781 | -0.066643 | -0.016756 | 3.9666e-05 | 2.5248e-05 | 0.099601 | 0.099601 | 0.099601 | 0.99646 | -0.067927 | 0.99581 | -0.080382 | 27.363
38 | 0.17508 | 0.044805 | -0.17501 | -0.044761 | 7.0096e-05 | 4.4717e-05 | 0.2609 | 0.2609 | 0.2609 | 0.99984 | -0.0029339 | 0.99941 | -0.011207 | 35.8373
39 | 0.064096 | 0.016117 | -0.064071 | -0.016102 | 2.4849e-05 | 1.581e-05 | 0.095795 | 0.095795 | 0.095795 | 0.99581 | -0.080382 | 0.99539 | -0.088503 | 26.3174
40 | 0.16425 | 0.042063 | -0.16421 | -0.042035 | 4.3716e-05 | 2.7877e-05 | 0.24487 | 0.24487 | 0.24487 | 0.99941 | -0.011207 | 0.99912 | -0.016702 | 33.6362
41 | 0.058053 | 0.014593 | -0.058033 | -0.01458 | 2.0842e-05 | 1.3243e-05 | 0.0868 | 0.0868 | 0.0868 | 0.99539 | -0.088503 | 0.995 | -0.096025 | 23.8462
42 | 0.058033 | 0.01458 | -0.05795 | -0.014528 | 8.2813e-05 | 5.262e-05 | 0.0868 | 0.0868 | 0.0868 | 0.995 | -0.096025 | 0.99345 | -0.12597 | 23.8462

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37088 | 0.093674

## res_load
| p_mw | q_mvar
0 | 0.0030307 | 0.00075956
1 | 0.0014652 | 0.00036721
2 | 0.0024061 | 0.00060301
3 | 0.0023822 | 0.00059704
4 | 0.0015488 | 0.00038817
5 | 0.0024226 | 0.00060716
6 | 0.00073538 | 0.0001843
7 | 0.080893 | 0.020274
8 | 0.0068216 | 0.0017096
9 | 0.009966 | 0.0024977
10 | 0.0043684 | 0.0010948
11 | 0.0049528 | 0.0012413
12 | 0.010745 | 0.002693
13 | 0.0042404 | 0.0010627
14 | 0.0077027 | 0.0019305
15 | 0.0072747 | 0.0018232
16 | 0.0016007 | 0.00040119
17 | 0.0023504 | 0.00058907
18 | 0.0070511 | 0.0017672
19 | 0.0031671 | 0.00079376
20 | 0.0061281 | 0.0015358
21 | 0.0049471 | 0.0012398
22 | 0.0045898 | 0.0011503
23 | 0.022538 | 0.0056487
24 | 0.00094352 | 0.00023647
25 | 0.00096585 | 0.00024207
26 | 0.015924 | 0.003991
27 | 0.0925 | 0.023183
28 | 0.012738 | 0.0031924
29 | 0.0059356 | 0.0014876
30 | 0.0025471 | 0.00063836
31 | 0.010763 | 0.0026974
32 | 0.0060173 | 0.0015081
33 | 0.0051133 | 0.0012815
34 | 0.009516 | 0.0023849

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1