## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-15_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2325-15_0_2_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_2325-15_0_2_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2325-15_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2325-15_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2325-15_0_2_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_2325-15_0_2_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2325-15_0_2_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_2325-15_0_2_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_2325-15_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2325-15_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2325-15_0_2_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2325-15_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2325-15_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2325-15_0_2_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_2325-15_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_2325-15_0_2_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_2325-15_0_2_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_2325-15_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2325-15_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_MV_0_node_1 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-15_0_2_load_0 | 0 | 0.00088203 | 0.00022106 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-15_0_2_load_15 | 7 | 0.0019985 | 0.00050087 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-15_0_2_load_20 | 9 | 0.0025619 | 0.00064206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-15_0_2_load_21 | 10 | 0.0012324 | 0.00030886 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-15_0_2_load_9 | 11 | 0.0033679 | 0.00084408 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-15_0_2_load_12 | 15 | 0.00034035 | 8.53e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-15_0_2_load_22 | 16 | 0.001451 | 0.00036364 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-15_0_2_load_13 | 18 | 0.00092353 | 0.00023146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-15_0_2_load_19 | 19 | 0.0011272 | 0.00028249 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-15_0_2_load_17 | 21 | 0.00057271 | 0.00014354 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-15_0_2_line_0 |  | 0 | 1 | 0.4793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-15_0_2_line_1 |  | 0 | 2 | 0.47245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-15_0_2_line_2 |  | 1 | 3 | 0.93942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-15_0_2_line_3 |  | 2 | 4 | 0.41196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-15_0_2_line_4 |  | 3 | 11 | 0.017364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-15_0_2_line_5 |  | 4 | 14 | 0.020951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-15_0_2_line_6 |  | 4 | 15 | 0.23974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-15_0_2_line_7 |  | 5 | 6 | 0.66759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-15_0_2_line_8 |  | 5 | 7 | 0.016894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-15_0_2_line_9 |  | 6 | 10 | 0.78794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-15_0_2_line_10 |  | 6 | 8 | 1.1184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-15_0_2_line_11 |  | 7 | 14 | 0.8252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-15_0_2_line_12 |  | 8 | 9 | 0.17349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-15_0_2_line_13 |  | 11 | 12 | 0.0050106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-15_0_2_line_14 |  | 12 | 13 | 0.057059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-15_0_2_line_15 |  | 13 | 16 | 0.006238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-15_0_2_line_16 |  | 14 | 17 | 0.1684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-15_0_2_line_17 |  | 15 | 18 | 0.1379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-15_0_2_line_18 |  | 17 | 19 | 0.16204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-15_0_2_line_19 |  | 17 | 20 | 0.058624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-15_0_2_line_20 |  | 20 | 21 | 0.12356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-15_0_2_trafo_1 | 0.63 MVA 20/0.4 kV | 22 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61 | x62 | y62 | x63 | y63 | x64 | y64 | x65 | y65 | x66 | y66 | x67 | y67 | x68 | y68 | x69 | y69 | x70 | y70 | x71 | y71 | x72 | y72 | x73 | y73 | x74 | y74 | x75 | y75 | x76 | y76 | x77 | y77 | x78 | y78 | x79 | y79 | x80 | y80 | x81 | y81 | x82 | y82 | x83 | y83 | x84 | y84 | x85 | y85 | x86 | y86
0 | 2563978.7543 | 1154231.1899 | 2564000.9428 | 1154213.8369 | 2564018.7326 | 1154193.3755 | 2564033.6877 | 1154178.634 | 2564046.1678 | 1154168.2095 | 2564055.158 | 1154159.1288 | 2564059.6523 | 1154147.4182 | 2564062.0174 | 1154123.4697 | 2564059.3765 | 1154101.352 | 2564057.5014 | 1154086.7225 | 2564059.5745 | 1154074.2037 | 2564067.04 | 1154064.165 | 2564084.716 | 1154042.515 | 2564114.6245 | 1154012.5654 | 2564156.4359 | 1153976.8531 | 2564196.4387 | 1153955.537 | 2564243.9747 | 1153936.6887 | 2564288.2518 | 1153920.6282 | 2564293.554 | 1153917.1812
1 | 2564342.5822 | 1153618.3964 | 2564338.1377 | 1153621.869 | 2564337.3494 | 1153626.0647 | 2564337.1781 | 1153629.5119 | 2564341.4615 | 1153641.537 | 2564348.3643 | 1153665.7417 | 2564352.7706 | 1153694.6079 | 2564360.3498 | 1153715.1623 | 2564377.4828 | 1153737.4275 | 2564393.6332 | 1153757.0083 | 2564412.9622 | 1153791.2667 | 2564429.8434 | 1153817.6912 | 2564432.2622 | 1153832.3065 | 2564429.3576 | 1153847.0534 | 2564422.5828 | 1153856.0092 | 2564417.6127 | 1153858.7956 | 2564413.6771 | 1153860.0862 | 2564406.1411 | 1153860.9758 | 2564393.7475 | 1153860.3378 | 2564379.5879 | 1153858.1651 | 2564363.7586 | 1153852.5673 | 2564349.5884 | 1153847.3043 | 2564340.8238 | 1153845.4221 | 2564330.9896 | 1153845.5917 | 2564321.5768 | 1153848.2489 | 2564314.8382 | 1153852.9247 | 2564310.5536 | 1153858.7531 | 2564307.7447 | 1153867.6076 | 2564308.1035 | 1153875.0426 | 2564312.4016 | 1153897.3061 | 2564313.5512 | 1153907.4378 | 2564313.5683 | 1153915.4751 | 2564312.0415 | 1153920.609 | 2564307.4386 | 1153923.2043 | 2564301.3824 | 1153922.6623 | 2564294.5336 | 1153916.5443 | 2564293.554 | 1153917.1812
2 | 2564606.9467 | 1154790.8275 | 2564609.8987 | 1154795.8349 | 2564618.8495 | 1154808.722 | 2564612.565 | 1154809.6151 | 2564605.6777 | 1154808.4551 | 2564599.6095 | 1154807.0234 | 2564590.1662 | 1154801.6653 | 2564586.7559 | 1154796.9941 | 2564575.8415 | 1154777.6153 | 2564571.2357 | 1154770.5389 | 2564568.4634 | 1154764.7968 | 2564567.1897 | 1154759.535 | 2564566.0641 | 1154739.0757 | 2564563.8713 | 1154727.5495 | 2564561.8377 | 1154722.2032 | 2564554.0184 | 1154708.7203 | 2564544.6587 | 1154692.8897 | 2564531.272 | 1154673.1699 | 2564527.7837 | 1154668.2991 | 2564520.1197 | 1154661.641 | 2564509.4627 | 1154656.0456 | 2564503.2411 | 1154653.3477 | 2564495.2994 | 1154650.3264 | 2564476.6867 | 1154644.5336 | 2564454.9295 | 1154636.247 | 2564446.4596 | 1154630.8388 | 2564442.5387 | 1154626.76 | 2564439.6009 | 1154622.8865 | 2564436.8133 | 1154618.4786 | 2564434.4635 | 1154611.5668 | 2564433.061 | 1154604.0157 | 2564431.8256 | 1154593.5955 | 2564430.5461 | 1154584.7875 | 2564429.2994 | 1154578.9363 | 2564427.4228 | 1154572.9333 | 2564422.3691 | 1154561.513 | 2564417.3334 | 1154554.4281 | 2564411.6022 | 1154547.7698 | 2564408.2234 | 1154543.2765 | 2564405.5141 | 1154539.146 | 2564402.9349 | 1154533.6696 | 2564401.2316 | 1154528.4437 | 2564399.9574 | 1154523.1263 | 2564398.8532 | 1154516.7296 | 2564397.1601 | 1154504.1666 | 2564394.38 | 1154498.4358 | 2564391.0583 | 1154493.2306 | 2564387.1908 | 1154489.1292 | 2564381.0178 | 1154485.5974 | 2564376.0796 | 1154483.3366 | 2564369.0841 | 1154480.8102 | 2564361.5631 | 1154478.9316 | 2564352.324 | 1154477.0967 | 2564343.8939 | 1154475.835 | 2564336.4442 | 1154474.3451 | 2564327.2937 | 1154471.9205 | 2564313.7107 | 1154467.1321 | 2564308.8035 | 1154464.9268 | 2564302.824 | 1154461.7051 | 2564290.8057 | 1154454.3173 | 2564276.2215 | 1154443.7209 | 2564261.239 | 1154431.9374 | 2564216.9205 | 1154405.6657 | 2564179.7577 | 1154385.6549 | 2564157.3131 | 1154372.9713 | 2564150.1246 | 1154367.7115 | 2564140.8897 | 1154361.4746 | 2564129.7562 | 1154353.3147 | 2564114.2007 | 1154345.8483 | 2564108.058 | 1154343.6061 | 2564103.1246 | 1154340.8898 | 2564098.1957 | 1154337.6398 | 2564094.1101 | 1154334.3181 | 2564083.0622 | 1154321.2553 | 2564078.9561 | 1154317.0555 | 2564067.5185 | 1154309.3867 | 2564062.5207 | 1154306.1817 | 2564056.9871 | 1154301.8793 | 2564052.6746 | 1154297.8141 | 2564044.1359 | 1154288.7384 | 2564038.4411 | 1154281.869 | 2564032.1362 | 1154275.6036 | 2564023.364 | 1154267.263 | 2564009.4269 | 1154254.7068 | 2563993.0281 | 1154241.0204 | 2563984.5786 | 1154235.3349 | 2563978.7543 | 1154231.1899
3 | 2564032.0873 | 1153360.995 | 2564041.5873 | 1153370.2317 | 2564054.6097 | 1153383.4494 | 2564073.2335 | 1153403.1813 | 2564083.5862 | 1153415.1921 | 2564095.3602 | 1153427.5169 | 2564103.9973 | 1153436.1808 | 2564110.0771 | 1153440.5911 | 2564117.4182 | 1153445.5275 | 2564151.7204 | 1153462.1422 | 2564155.3137 | 1153463.8883 | 2564169.6331 | 1153470.8175 | 2564176.8384 | 1153474.8655 | 2564181.7187 | 1153478.8384 | 2564185.9926 | 1153482.7816 | 2564189.4043 | 1153487.5192 | 2564194.956 | 1153496.0237 | 2564202.5661 | 1153508.7737 | 2564208.4043 | 1153517.7212 | 2564212.2763 | 1153522.4672 | 2564217.2292 | 1153527.0512 | 2564222.9848 | 1153531.1745 | 2564234.8573 | 1153538.2296 | 2564277.3728 | 1153559.5763 | 2564291.7569 | 1153567.1168 | 2564313.5761 | 1153578.7041 | 2564319.9782 | 1153583.1683 | 2564328 | 1153591.6806 | 2564330.9328 | 1153595.8986 | 2564333.484 | 1153600.4524 | 2564338.7788 | 1153610.9708 | 2564342.5822 | 1153618.3964
4 | 2564606.9467 | 1154790.8275 | 2564605.034 | 1154782.5568 | 2564605.1339 | 1154774.7745 | 2564605.3444 | 1154773.7033
5 | 2564032.0873 | 1153360.995 | 2564024.2596 | 1153350.4365 | 2564020.398 | 1153343.634
6 | 2564032.0873 | 1153360.995 | 2564023.8964 | 1153375.6071 | 2564021.3479 | 1153379.2242 | 2564017.4066 | 1153382.1715 | 2564012.7775 | 1153382.9996 | 2564002.1858 | 1153383.6301 | 2563996.7452 | 1153386.0417 | 2563992.3928 | 1153389.5029 | 2563989.2277 | 1153393.9352 | 2563988.1305 | 1153399.0555 | 2563988.2185 | 1153404.7579 | 2563989.6442 | 1153410.9414 | 2563996.4272 | 1153427.687 | 2564004.2441 | 1153444.1263 | 2564011.851 | 1153469.06 | 2564022.8178 | 1153495.1964 | 2564025.9666 | 1153505.9719 | 2564028.5079 | 1153519.0634 | 2564032.9857 | 1153544.216 | 2564037.1474 | 1153560.1547 | 2564039.7912 | 1153566.4426
7 | 2563278.5316 | 1153763.7486 | 2563290.9853 | 1153772.8994 | 2563310.5092 | 1153786.5648 | 2563320.0211 | 1153793.8993 | 2563327.7353 | 1153799.5773 | 2563333.1396 | 1153803.8909 | 2563338.502 | 1153808.883 | 2563342.7937 | 1153813.1701 | 2563347.3847 | 1153818.7338 | 2563355.9395 | 1153827.6639 | 2563364.0563 | 1153835.2071 | 2563369.0301 | 1153838.1338 | 2563374.7789 | 1153841.0891 | 2563380.7297 | 1153843.1872 | 2563386.1051 | 1153844.0327 | 2563392.9521 | 1153844.6579 | 2563402.371 | 1153846.8461 | 2563413.8688 | 1153851.534 | 2563424.2785 | 1153853.9051 | 2563430.7875 | 1153854.4546 | 2563444.5278 | 1153854.4932 | 2563455.2029 | 1153853.8501 | 2563460.5055 | 1153854.0735 | 2563466.4624 | 1153854.6709 | 2563476.0694 | 1153856.2689 | 2563485.1256 | 1153858.1036 | 2563495.582 | 1153860.5969 | 2563504.9636 | 1153862.9744 | 2563506.4863 | 1153854.7499 | 2563503.748 | 1153843.4719 | 2563499.4279 | 1153834.4936 | 2563492.9711 | 1153827.3959 | 2563478.296 | 1153818.7363 | 2563470.4027 | 1153812.5923 | 2563458.0592 | 1153797.5375 | 2563444.0948 | 1153774.5774 | 2563434.2437 | 1153751.837 | 2563411.9039 | 1153697.8233 | 2563403.9095 | 1153683.9316 | 2563381.901 | 1153656.6519 | 2563375.9659 | 1153648.3506 | 2563371.2596 | 1153638.9856 | 2563369.4173 | 1153633.7942 | 2563368.6559 | 1153628.4628 | 2563369.9312 | 1153619.9396 | 2563395.2129 | 1153499.5354
8 | 2563395.2129 | 1153499.5354 | 2563410.8495 | 1153505.9308
9 | 2563278.5316 | 1153763.7486 | 2563267.8645 | 1153755.7098 | 2563258.0418 | 1153748.9887 | 2563249.4477 | 1153743.7163 | 2563241.1066 | 1153739.6653 | 2563232.459 | 1153735.6829 | 2563222.598 | 1153732.764 | 2563216.9613 | 1153731.8536 | 2563212.5844 | 1153733.7258 | 2563209.626 | 1153737.9572 | 2563208.9022 | 1153745.043 | 2563209.5629 | 1153753.9435 | 2563213.5226 | 1153774.1406 | 2563220.9452 | 1153807.3454 | 2563224.2808 | 1153824.6115 | 2563226.6693 | 1153835.0466 | 2563229.9989 | 1153846.3209 | 2563233.1555 | 1153858.1743 | 2563240.1512 | 1153883.0774 | 2563242.7406 | 1153897.5245 | 2563245.5006 | 1153914.7608 | 2563247.3817 | 1153930.046 | 2563250.4707 | 1153949.6704 | 2563252.364 | 1153964.4441 | 2563254.2174 | 1153992.7583 | 2563255.9406 | 1154021.1066 | 2563256.84 | 1154033.9298 | 2563256.8407 | 1154042.8232 | 2563256.249 | 1154048.9299 | 2563255.1406 | 1154054.5841 | 2563249.9398 | 1154072.2026 | 2563245.8748 | 1154084.8784 | 2563243.089 | 1154094.7338 | 2563237.5589 | 1154116.1785 | 2563233.5 | 1154131.0999 | 2563229.065 | 1154145.9679 | 2563224.0947 | 1154159.8721 | 2563203.1424 | 1154207.1134 | 2563200.2004 | 1154215.2355 | 2563198.145 | 1154222.8298 | 2563196.4528 | 1154230.8553 | 2563194.9654 | 1154239.7467 | 2563194.4097 | 1154247.9543 | 2563192.9279 | 1154256.5011 | 2563190.9056 | 1154266.9855 | 2563189.9543 | 1154273.2278 | 2563189.6104 | 1154279.6999 | 2563188.5013 | 1154285.2317 | 2563186.5972 | 1154289.9569 | 2563182.737 | 1154295.9503 | 2563178.3279 | 1154303.7591 | 2563175.9198 | 1154310.1104 | 2563173.8924 | 1154317.2487 | 2563172.7886 | 1154324.8927 | 2563171.8413 | 1154333.036 | 2563171.1178 | 1154341.3891 | 2563170.8983 | 1154354.3748 | 2563171.4749 | 1154360.8413 | 2563172.3597 | 1154367.517 | 2563177.6482 | 1154393.0309 | 2563182.0762 | 1154417.0827 | 2563184.0425 | 1154425.5239
10 | 2563278.5316 | 1153763.7486 | 2563264.4685 | 1153782.4664 | 2563270.2865 | 1153813.0019 | 2563292.942 | 1153857.0302 | 2563341.4158 | 1153974.4605 | 2563365.8186 | 1154028.439 | 2563392.6781 | 1154096.5988 | 2563400.3578 | 1154152.0691 | 2563411.4819 | 1154205.0283 | 2563427.5929 | 1154258.1127 | 2563440.4653 | 1154316.0526 | 2563447.0818 | 1154374.6533 | 2563460.8025 | 1154422.0717 | 2563463.9619 | 1154476.0799 | 2563458.6213 | 1154522.436 | 2563467.5975 | 1154557.9328 | 2563483.382 | 1154581.5488 | 2563501.6139 | 1154595.156 | 2563511.3613 | 1154603.6233 | 2563517.1544 | 1154615.2607 | 2563521.6202 | 1154633.1537 | 2563524.4405 | 1154649.1559 | 2563528.585 | 1154658.3687 | 2563533.3186 | 1154674.9039 | 2563544.0015 | 1154684.6107 | 2563562.9109 | 1154703.7723 | 2563570.0665 | 1154716.2241 | 2563574.2273 | 1154728.1383 | 2563572.9494 | 1154742.5422 | 2563560.3249 | 1154754.1358 | 2563550.714 | 1154761.7758 | 2563541.329 | 1154768.703 | 2563537.5348 | 1154777.9974 | 2563533.6251 | 1154788.471
11 | 2564020.398 | 1153343.634 | 2563994.4016 | 1153350.9046 | 2563979.1448 | 1153355.3428 | 2563960.1293 | 1153357.3245 | 2563937.6618 | 1153355.5918 | 2563897.7232 | 1153353.6641 | 2563854.0651 | 1153354.5494 | 2563828.183 | 1153356.5618 | 2563811.9698 | 1153357.5933 | 2563802.0091 | 1153361.0773 | 2563796.1274 | 1153367.9496 | 2563789.0197 | 1153378.8758 | 2563781.3561 | 1153401.9337 | 2563770.849 | 1153417.8496 | 2563769.3535 | 1153428.1194 | 2563773.1443 | 1153435.8671 | 2563783.2025 | 1153448.5573 | 2563787.0158 | 1153460.0402 | 2563767.3093 | 1153554.6738 | 2563762.6895 | 1153564.6511 | 2563754.3017 | 1153569.3708 | 2563745.9006 | 1153573.1568 | 2563741.249 | 1153577.8428 | 2563736.6048 | 1153583.7739 | 2563731.3092 | 1153584.7397 | 2563715.0629 | 1153580.1799 | 2563672.2406 | 1153565.5091 | 2563660.3858 | 1153565.2696 | 2563652.2635 | 1153563.151 | 2563644.1318 | 1153559.465 | 2563630.3354 | 1153546.4864 | 2563602.8479 | 1153540.4387 | 2563584.4601 | 1153543.3517 | 2563565.1647 | 1153549.683 | 2563547.7431 | 1153557.5594 | 2563539.3232 | 1153558.2331 | 2563523.4063 | 1153556.1509 | 2563474.3557 | 1153543.0868 | 2563461.5213 | 1153535.7055 | 2563424.8861 | 1153511.6719 | 2563410.8495 | 1153505.9308
12 | 2563533.6251 | 1154788.471 | 2563533.8144 | 1154798.1747 | 2563535.0529 | 1154807.5942 | 2563542.2504 | 1154825.682 | 2563549.4421 | 1154842.8359 | 2563556.1388 | 1154855.5239 | 2563561.657 | 1154868.6749 | 2563568.1129 | 1154880.8864 | 2563577.3891 | 1154891.4355 | 2563590.9427 | 1154904.0708 | 2563606.1677 | 1154921.6542 | 2563613.2653 | 1154922.078 | 2563617.5346 | 1154925.3538 | 2563620.5552 | 1154929.908
13 | 2564606.3105 | 1154768.7867 | 2564605.3444 | 1154773.7033
14 | 2564606.3105 | 1154768.7867 | 2564606.6604 | 1154766.9838 | 2564609.2865 | 1154762.2548 | 2564614.3568 | 1154759.6569 | 2564619.8661 | 1154759.9802 | 2564621.1361 | 1154760.7175 | 2564624.5065 | 1154757.3293 | 2564628.153 | 1154756.5185 | 2564634.8951 | 1154757.7683 | 2564639.4826 | 1154759.1642 | 2564646.7233 | 1154760.4111 | 2564650.0152 | 1154759.3134 | 2564650.9253 | 1154758.8522 | 2564654.8262 | 1154762.1754
15 | 2564659.666 | 1154758.2227 | 2564654.8262 | 1154762.1754
16 | 2563971.5582 | 1153186.8138 | 2563981.4811 | 1153196.148 | 2563992.6569 | 1153210.9774 | 2563999.9812 | 1153229.6652 | 2564003.5409 | 1153242.3947 | 2564006.1555 | 1153256.1861 | 2564009.491 | 1153278.8887 | 2564012.1084 | 1153302.107 | 2564014.4101 | 1153322.5814 | 2564017.1264 | 1153335.4272 | 2564020.398 | 1153343.634
17 | 2564091.2818 | 1153681.9927 | 2564097.6413 | 1153675.4958 | 2564101.1832 | 1153669.9385 | 2564101.9362 | 1153666.2877 | 2564101.4226 | 1153662.4999 | 2564093.7099 | 1153650.5733 | 2564080.024 | 1153634.0467 | 2564074.5254 | 1153625.453 | 2564069.3034 | 1153613.078 | 2564062.231 | 1153599.1911 | 2564055.3116 | 1153587.7822 | 2564042.8259 | 1153571.8711 | 2564040.066 | 1153567.0963 | 2564039.7912 | 1153566.4426
18 | 2563971.5582 | 1153186.8138 | 2563968.3833 | 1153194.748 | 2563971.3035 | 1153218.5315 | 2563976.0511 | 1153238.7021 | 2563978.8321 | 1153255.9164 | 2563979.2467 | 1153273.8675 | 2563979.123 | 1153286.4857 | 2563974.6453 | 1153295.9507 | 2563965.4398 | 1153305.1328 | 2563954.1677 | 1153312.582 | 2563933.4547 | 1153324.5013
19 | 2563928.8332 | 1153146.561 | 2563941.4372 | 1153158.9805 | 2563971.5582 | 1153186.8138
20 | 2563928.8332 | 1153146.561 | 2563899.7031 | 1153195.5164 | 2563877.6135 | 1153218.4275 | 2563870.3817 | 1153221.5392 | 2563863.5855 | 1153220.5574 | 2563846.5129 | 1153210.0783

## bus_geodata
| x | y | coords
0 | 2564293.554 | 1153917.1812
1 | 2563978.7543 | 1154231.1899
2 | 2564342.5822 | 1153618.3964
3 | 2564606.9467 | 1154790.8275
4 | 2564032.0873 | 1153360.995
5 | 2563395.2129 | 1153499.5354
6 | 2563278.5316 | 1153763.7486
7 | 2563410.8495 | 1153505.9308
8 | 2563533.6251 | 1154788.471
9 | 2563620.5552 | 1154929.908
10 | 2563184.0425 | 1154425.5239
11 | 2564605.3444 | 1154773.7033
12 | 2564606.3105 | 1154768.7867
13 | 2564654.8262 | 1154762.1754
14 | 2564020.398 | 1153343.634
15 | 2564039.7912 | 1153566.4426
16 | 2564659.666 | 1154758.2227
17 | 2563971.5582 | 1153186.8138
18 | 2564091.2818 | 1153681.9927
19 | 2563933.4547 | 1153324.5013
20 | 2563928.8332 | 1153146.561
21 | 2563846.5129 | 1153210.0783
22 | 2563978.7543 | 1154231.1899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99576 | -0.082407 | 0.00088203 | 0.00022106
1 | 1 | 0 | -0.016265 | -0.0036361
2 | 0.99195 | -0.15681 | 0 | 0
3 | 0.99588 | -0.079534 | 0 | 0
4 | 0.98864 | -0.22204 | 0 | 0
5 | 0.98403 | -0.31325 | 0 | 0
6 | 0.9817 | -0.35989 | 0 | 0
7 | 0.98409 | -0.31207 | 0.0019985 | 0.00050087
8 | 0.97905 | -0.41233 | 0 | 0
9 | 0.97864 | -0.42042 | 0.0025619 | 0.00064206
10 | 0.9808 | -0.37765 | 0.0012324 | 0.00030886
11 | 0.9958 | -0.081005 | 0.0033679 | 0.00084408
12 | 0.9958 | -0.081133 | 0 | 0
13 | 0.99572 | -0.082589 | 0 | 0
14 | 0.98849 | -0.22489 | 0 | 0
15 | 0.98836 | -0.22748 | 0.00034035 | 8.53e-05
16 | 0.99571 | -0.082749 | 0.001451 | 0.00036364
17 | 0.98823 | -0.23004 | 0 | 0
18 | 0.98824 | -0.22976 | 0.00092353 | 0.00023146
19 | 0.98806 | -0.23331 | 0.0011272 | 0.00028249
20 | 0.9882 | -0.23065 | 0 | 0
21 | 0.98814 | -0.23191 | 0.00057271 | 0.00014354
22 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0097393 | -0.0024116 | 0.0097773 | 0.0024297 | 3.8013e-05 | 1.8067e-05 | 0.014544 | 0.014542 | 0.014544 | 0.99576 | -0.082407 | 1 | 0 | 3.9955
1 | 0.0088573 | 0.0021905 | -0.0088263 | -0.0021768 | 3.0995e-05 | 1.3714e-05 | 0.013226 | 0.013228 | 0.013228 | 0.99576 | -0.082407 | 0.99195 | -0.15681 | 3.634
2 | 0.0048376 | 0.0012063 | -0.0048193 | -0.0012069 | 1.8254e-05 | -5.9103e-07 | 0.0071963 | 0.0072006 | 0.0072006 | 1 | 0 | 0.99588 | -0.079534 | 1.9782
3 | 0.0088263 | 0.0021768 | -0.0087992 | -0.0021648 | 2.7034e-05 | 1.2002e-05 | 0.013228 | 0.01323 | 0.01323 | 0.99195 | -0.15681 | 0.98864 | -0.22204 | 3.6345
4 | 0.0048193 | 0.0012069 | -0.004819 | -0.0012069 | 3.3761e-07 | -9.8393e-09 | 0.0072006 | 0.0072007 | 0.0072007 | 0.99588 | -0.079534 | 0.9958 | -0.081005 | 1.9782
5 | 0.0075349 | 0.0018526 | -0.0075339 | -0.0018523 | 1.0083e-06 | 3.7667e-07 | 0.011328 | 0.011328 | 0.011328 | 0.98864 | -0.22204 | 0.98849 | -0.22489 | 3.1122
6 | 0.0012643 | 0.00031219 | -0.001264 | -0.00031506 | 3.2517e-07 | -2.8652e-06 | 0.0019013 | 0.0019024 | 0.0019024 | 0.98864 | -0.22204 | 0.98836 | -0.22748 | 0.52263
7 | 0.0038109 | 0.00092689 | -0.0038026 | -0.00093005 | 8.2893e-06 | -3.1555e-06 | 0.0057528 | 0.0057557 | 0.0057557 | 0.98403 | -0.31325 | 0.9817 | -0.35989 | 1.5812
8 | -0.0038109 | -0.00092689 | 0.0038111 | 0.00092681 | 2.0966e-07 | -8.0446e-08 | 0.0057528 | 0.0057527 | 0.0057528 | 0.98403 | -0.31325 | 0.98409 | -0.31207 | 1.5804
9 | 0.0012334 | 0.00029957 | -0.0012324 | -0.00030886 | 1.031e-06 | -9.2933e-06 | 0.0018662 | 0.0018697 | 0.0018697 | 0.9817 | -0.35989 | 0.9808 | -0.37765 | 0.51366
10 | 0.0025692 | 0.00063048 | -0.0025628 | -0.00064051 | 6.3528e-06 | -1.0036e-05 | 0.0038895 | 0.0038945 | 0.0038945 | 0.9817 | -0.35989 | 0.97905 | -0.41233 | 1.0699
11 | -0.0058096 | -0.0014277 | 0.0058334 | 0.0014324 | 2.3815e-05 | 4.7104e-06 | 0.0087745 | 0.0087708 | 0.0087745 | 0.98409 | -0.31207 | 0.98849 | -0.22489 | 2.4106
12 | 0.0025628 | 0.00064051 | -0.0025619 | -0.00064206 | 9.8695e-07 | -1.5491e-06 | 0.0038945 | 0.0038953 | 0.0038953 | 0.97905 | -0.41233 | 0.97864 | -0.42042 | 1.0701
13 | 0.0014511 | 0.00036283 | -0.0014511 | -0.00036289 | 8.8318e-09 | -5.9532e-08 | 0.002168 | 0.002168 | 0.002168 | 0.9958 | -0.081005 | 0.9958 | -0.081133 | 0.59562
14 | 0.0014511 | 0.00036289 | -0.001451 | -0.00036357 | 1.0059e-07 | -6.7787e-07 | 0.002168 | 0.0021683 | 0.0021683 | 0.9958 | -0.081133 | 0.99572 | -0.082589 | 0.59569
15 | 0.001451 | 0.00036357 | -0.001451 | -0.00036364 | 1.0998e-08 | -7.41e-08 | 0.0021683 | 0.0021683 | 0.0021683 | 0.99572 | -0.082589 | 0.99571 | -0.082749 | 0.5957
16 | 0.0017005 | 0.00041987 | -0.0017001 | -0.00042176 | 4.1321e-07 | -1.8937e-06 | 0.0025576 | 0.0025584 | 0.0025584 | 0.98849 | -0.22489 | 0.98823 | -0.23004 | 0.70285
17 | 0.00092363 | 0.00022976 | -0.00092353 | -0.00023146 | 9.9954e-08 | -1.7031e-06 | 0.00139 | 0.0013906 | 0.0013906 | 0.98836 | -0.22748 | 0.98824 | -0.22976 | 0.38203
18 | 0.0011273 | 0.00028053 | -0.0011272 | -0.00028249 | 1.7502e-07 | -1.9638e-06 | 0.0016967 | 0.0016975 | 0.0016975 | 0.98823 | -0.23004 | 0.98806 | -0.23331 | 0.46634
19 | 0.00057276 | 0.00014123 | -0.00057275 | -0.00014197 | 1.6326e-08 | -7.4064e-07 | 0.00086162 | 0.00086188 | 0.00086188 | 0.98823 | -0.23004 | 0.9882 | -0.23065 | 0.23678
20 | 0.00057275 | 0.00014197 | -0.00057271 | -0.00014354 | 3.4443e-08 | -1.5609e-06 | 0.00086188 | 0.00086244 | 0.00086244 | 0.9882 | -0.23065 | 0.98814 | -0.23191 | 0.23693

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.016265 | 0.0036361

## res_load
| p_mw | q_mvar
0 | 0.00088203 | 0.00022106
1 | 0.0019985 | 0.00050087
2 | 0.0025619 | 0.00064206
3 | 0.0012324 | 0.00030886
4 | 0.0033679 | 0.00084408
5 | 0.00034035 | 8.53e-05
6 | 0.001451 | 0.00036364
7 | 0.00092353 | 0.00023146
8 | 0.0011272 | 0.00028249
9 | 0.00057271 | 0.00014354

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1