## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-19_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-19_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-19_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2325-19_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2325-19_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2325-19_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2325-19_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2325-19_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2325-19_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2325-19_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2325-19_0_4_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2325-19_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_2325-19_0_4_node_68 | 0.4 | n |  | TRUE
13 | bus_LV_2325-19_0_4_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_2325-19_0_4_node_59 | 0.4 | n |  | TRUE
15 | bus_LV_2325-19_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2325-19_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_2325-19_0_4_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_2325-19_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2325-19_0_4_node_49 | 0.4 | n |  | TRUE
20 | bus_LV_2325-19_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_2325-19_0_4_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_2325-19_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2325-19_0_4_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_2325-19_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_2325-19_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_2325-19_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2325-19_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2325-19_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2325-19_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2325-19_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2325-19_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2325-19_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2325-19_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2325-19_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_2325-19_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_2325-19_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_2325-19_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_2325-19_0_4_node_51 | 0.4 | n |  | TRUE
39 | bus_LV_2325-19_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_2325-19_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2325-19_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2325-19_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2325-19_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2325-19_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_2325-19_0_4_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_2325-19_0_4_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_2325-19_0_4_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_2325-19_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_2325-19_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_2325-19_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_2325-19_0_4_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2325-19_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2325-19_0_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_2325-19_0_4_node_69 | 0.4 | n |  | TRUE
55 | bus_LV_2325-19_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_2325-19_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_2325-19_0_4_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_2325-19_0_4_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_2325-19_0_4_node_60 | 0.4 | n |  | TRUE
60 | bus_LV_2325-19_0_4_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_2325-19_0_4_node_62 | 0.4 | n |  | TRUE
62 | bus_LV_2325-19_0_4_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2325-19_0_4_node_64 | 0.4 | n |  | TRUE
64 | bus_LV_2325-19_0_4_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_2325-19_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_2325-19_0_4_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_2325-19_0_4_node_71 | 0.4 | n |  | TRUE
68 | bus_MV_37_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-19_0_4_load_0 | 0 | 0.027711 | 0.006945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-19_0_4_load_3 | 3 | 0.025469 | 0.0063831 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-19_0_4_load_4 | 4 | 0.063573 | 0.015933 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-19_0_4_load_8 | 8 | 0.097849 | 0.024523 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-19_0_4_load_9 | 9 | 0.06013 | 0.01507 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-19_0_4_load_27 | 10 | 0.021057 | 0.0052775 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-19_0_4_load_13 | 11 | 0.0046181 | 0.0011574 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-19_0_4_load_68 | 12 | 0.012783 | 0.0032037 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-19_0_4_load_59 | 14 | 0.0067799 | 0.0016992 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-19_0_4_load_16 | 15 | 0.0078893 | 0.0019772 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-19_0_4_load_11 | 18 | 0.0073853 | 0.0018509 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-19_0_4_load_45 | 20 | 0.0093118 | 0.0023338 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-19_0_4_load_57 | 21 | 0.0017682 | 0.00044315 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-19_0_4_load_17 | 22 | 0.0031382 | 0.00078652 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-19_0_4_load_10 | 24 | 0.011462 | 0.0028726 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-19_0_4_load_12 | 25 | 0.009156 | 0.0022947 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-19_0_4_load_14 | 26 | 0.0090967 | 0.0022798 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-19_0_4_load_25 | 29 | 0.007677 | 0.001924 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-19_0_4_load_18 | 30 | 0.0039286 | 0.00098459 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-19_0_4_load_19 | 31 | 0.0021112 | 0.00052911 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-19_0_4_load_20 | 32 | 0.0028369 | 0.00071099 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-19_0_4_load_21 | 33 | 0.0017351 | 0.00043485 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-19_0_4_load_22 | 34 | 0.0034477 | 0.00086407 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-19_0_4_load_23 | 35 | 0.0019416 | 0.00048661 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-19_0_4_load_24 | 36 | 0.0052146 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-19_0_4_load_41 | 37 | 0.0011548 | 0.00028943 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-19_0_4_load_51 | 38 | 0.0024715 | 0.00061941 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-19_0_4_load_42 | 39 | 0.0021575 | 0.00054073 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-19_0_4_load_29 | 40 | 0.0064644 | 0.0016201 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-19_0_4_load_30 | 41 | 0.023939 | 0.0059997 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-19_0_4_load_36 | 44 | 0.035471 | 0.0088898 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-19_0_4_load_40 | 45 | 0.017777 | 0.0044553 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-19_0_4_load_52 | 47 | 0.0017882 | 0.00044816 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-19_0_4_load_43 | 48 | 0.001957 | 0.00049047 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-19_0_4_load_44 | 49 | 0.0020795 | 0.00052117 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-19_0_4_load_50 | 50 | 0.0083119 | 0.0020832 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-19_0_4_load_48 | 51 | 0.0031168 | 0.00078116 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-19_0_4_load_46 | 52 | 0.0060493 | 0.0015161 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-19_0_4_load_70 | 53 | 0.000609 | 0.00015263 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-19_0_4_load_69 | 54 | 0.00060918 | 0.00015268 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-19_0_4_load_54 | 55 | 0.0031497 | 0.00078938 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-19_0_4_load_55 | 56 | 0.0017687 | 0.00044327 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-19_0_4_load_60 | 59 | 0.0047642 | 0.001194 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-19_0_4_load_61 | 60 | 0.0033518 | 0.00084005 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-19_0_4_load_62 | 61 | 0.00042165 | 0.00010568 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-19_0_4_load_63 | 62 | 0.00088014 | 0.00022058 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-19_0_4_load_64 | 63 | 0.00042165 | 0.00010568 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-19_0_4_load_65 | 64 | 0.00042153 | 0.00010565 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-19_0_4_load_66 | 65 | 0.0005908 | 0.00014807 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-19_0_4_load_67 | 66 | 0.00042162 | 0.00010567 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-19_0_4_load_71 | 67 | 0.00060901 | 0.00015263 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-19_0_4_line_0 |  | 0 | 1 | 0.057861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2325-19_0_4_line_1 |  | 0 | 2 | 0.03747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-19_0_4_line_2 |  | 1 | 3 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-19_0_4_line_3 |  | 1 | 4 | 0.015638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2325-19_0_4_line_4 |  | 1 | 5 | 0.065109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-19_0_4_line_5 |  | 2 | 6 | 0.055389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-19_0_4_line_6 |  | 2 | 7 | 0.10507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-19_0_4_line_7 |  | 3 | 8 | 0.0064116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-19_0_4_line_8 |  | 4 | 9 | 0.025204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-19_0_4_line_9 |  | 5 | 10 | 0.002031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-19_0_4_line_10 |  | 5 | 11 | 0.020392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-19_0_4_line_11 |  | 6 | 12 | 0.0498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-19_0_4_line_12 |  | 7 | 13 | 0.17854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-19_0_4_line_13 |  | 7 | 14 | 0.098255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-19_0_4_line_14 |  | 8 | 15 | 0.029908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-19_0_4_line_15 |  | 9 | 16 | 0.02998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-19_0_4_line_16 |  | 10 | 17 | 0.046657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-19_0_4_line_17 |  | 11 | 18 | 0.048962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-19_0_4_line_18 |  | 13 | 19 | 0.095477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-19_0_4_line_19 |  | 13 | 20 | 0.027594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-19_0_4_line_20 |  | 14 | 21 | 0.065447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-19_0_4_line_21 |  | 15 | 22 | 0.0016795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-19_0_4_line_22 |  | 16 | 23 | 0.004586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-19_0_4_line_23 |  | 17 | 40 | 0.013664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-19_0_4_line_24 |  | 17 | 41 | 0.042122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-19_0_4_line_25 |  | 18 | 24 | 0.017211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-19_0_4_line_26 |  | 19 | 53 | 0.12678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-19_0_4_line_27 |  | 20 | 52 | 0.042928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-19_0_4_line_28 |  | 21 | 56 | 1.3235e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-19_0_4_line_29 |  | 22 | 30 | 0.037722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-19_0_4_line_30 |  | 23 | 44 | 0.0090106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-19_0_4_line_31 |  | 24 | 25 | 0.0094991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-19_0_4_line_32 |  | 25 | 26 | 0.027837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-19_0_4_line_33 |  | 26 | 27 | 0.11342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-19_0_4_line_34 |  | 27 | 28 | 0.067517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-19_0_4_line_35 |  | 28 | 29 | 0.093982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-19_0_4_line_36 |  | 31 | 32 | 0.0081886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-19_0_4_line_37 |  | 31 | 33 | 0.015907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-19_0_4_line_38 |  | 32 | 34 | 0.020858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-19_0_4_line_39 |  | 33 | 35 | 0.013902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-19_0_4_line_40 |  | 34 | 36 | 0.019768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-19_0_4_line_41 |  | 35 | 37 | 0.017791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-19_0_4_line_42 |  | 36 | 38 | 0.047546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-19_0_4_line_43 |  | 37 | 39 | 0.0053256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-19_0_4_line_44 |  | 39 | 48 | 0.026828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-19_0_4_line_45 |  | 42 | 43 | 0.015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-19_0_4_line_46 |  | 42 | 44 | 0.010108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2325-19_0_4_line_47 |  | 43 | 46 | 0.041259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2325-19_0_4_line_48 |  | 43 | 45 | 0.0097811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2325-19_0_4_line_49 |  | 46 | 47 | 0.046273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-19_0_4_line_50 |  | 48 | 49 | 0.0038726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2325-19_0_4_line_51 |  | 49 | 50 | 0.029638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2325-19_0_4_line_52 |  | 50 | 51 | 0.00011935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2325-19_0_4_line_53 |  | 51 | 52 | 0.0097506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2325-19_0_4_line_54 |  | 53 | 54 | 0.0056898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2325-19_0_4_line_55 |  | 54 | 66 | 0.015924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2325-19_0_4_line_56 |  | 55 | 56 | 0.023041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2325-19_0_4_line_57 |  | 55 | 57 | 0.14275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2325-19_0_4_line_58 |  | 57 | 58 | 0.13352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2325-19_0_4_line_59 |  | 58 | 59 | 0.10495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2325-19_0_4_line_60 |  | 60 | 61 | 0.0029308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2325-19_0_4_line_61 |  | 60 | 62 | 0.0049952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2325-19_0_4_line_62 |  | 61 | 63 | 0.0057521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2325-19_0_4_line_63 |  | 62 | 64 | 0.0040671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2325-19_0_4_line_64 |  | 63 | 65 | 0.015635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2325-19_0_4_line_65 |  | 64 | 66 | 0.0057539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-19_0_4_line_66 |  | 65 | 67 | 0.0060933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-19_0_4_trafo_0 | 0.63 MVA 20/0.4 kV | 68 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2558562.5009 | 1153055.3677 | 2558545.0104 | 1153061.447 | 2558513.9088 | 1153078.6928 | 2558510.9586 | 1153081.058
1 | 2558481.7233 | 1153104.495 | 2558510.9586 | 1153081.058
2 | 2558562.5009 | 1153055.3677 | 2558566.9546 | 1153074.6048
3 | 2558562.5009 | 1153055.3677 | 2558557.779 | 1153040.4593
4 | 2558562.5009 | 1153055.3677 | 2558581.1371 | 1153054.0941 | 2558601.7302 | 1153053.9743 | 2558615.9017 | 1153052.8317 | 2558627.3674 | 1153050.9517
5 | 2558481.7233 | 1153104.495 | 2558480.4423 | 1153124.5142 | 2558479.9533 | 1153139.2473 | 2558492.3595 | 1153138.0388 | 2558495.9537 | 1153130.7546
6 | 2558386.9786 | 1153145.2826 | 2558401.8402 | 1153143.0007 | 2558412.0367 | 1153141.8073 | 2558413.5155 | 1153141.508 | 2558420.3315 | 1153139.671 | 2558426.6267 | 1153137.971 | 2558437.5285 | 1153133.371 | 2558450.5449 | 1153126.1106 | 2558481.7233 | 1153104.495
7 | 2558568.4007 | 1153080.8512 | 2558568.4007 | 1153080.8512 | 2558566.9546 | 1153074.6048
8 | 2558557.779 | 1153040.4593 | 2558553.7072 | 1153029.7041 | 2558547.8664 | 1153017.3076
9 | 2558627.3674 | 1153050.9517 | 2558629.296 | 1153050.3153
10 | 2558627.3674 | 1153050.9517 | 2558632.8583 | 1153070.5907
11 | 2558495.9537 | 1153130.7546 | 2558545.7473 | 1153129.9427
12 | 2558274.9995 | 1153128.2394 | 2558282.8168 | 1153130.275 | 2558286.1653 | 1153117.4785 | 2558286.3772 | 1153111.5295 | 2558293.8135 | 1153106.2085 | 2558299.0872 | 1153103.2593 | 2558330.0492 | 1153088.1145 | 2558332.0524 | 1153087.0889 | 2558340.1805 | 1153104.0524 | 2558341.4847 | 1153105.1328 | 2558343.0164 | 1153105.8336 | 2558344.5687 | 1153106.1786 | 2558346.4322 | 1153106.0323 | 2558364.6837 | 1153096.8789 | 2558366.4415 | 1153100.3129 | 2558381.4706 | 1153134.3596 | 2558386.9786 | 1153145.2826
13 | 2558386.9786 | 1153145.2826 | 2558392.4255 | 1153157.3622 | 2558394.3548 | 1153165.5975 | 2558395.0106 | 1153170.5622 | 2558396.3528 | 1153183.7708 | 2558397.3653 | 1153194.8027 | 2558397.2603 | 1153201.7959 | 2558396.6926 | 1153210.66 | 2558395.0851 | 1153225.601 | 2558391.1542 | 1153241.3989
14 | 2558568.4007 | 1153080.8512 | 2558568.0868 | 1153108.7566 | 2558567.9388 | 1153110.7521
15 | 2558538.5329 | 1152988.9768 | 2558540.3498 | 1152996.5236 | 2558542.6964 | 1153006.3347 | 2558547.8664 | 1153017.3076
16 | 2558669.8249 | 1153028.0811 | 2558660.1188 | 1153035.8963 | 2558642.6093 | 1153045.922 | 2558629.296 | 1153050.3153
17 | 2558645.3792 | 1153117.221 | 2558645.3228 | 1153109.0246 | 2558642.1412 | 1153090.4703 | 2558632.8583 | 1153070.5907
18 | 2558191.8494 | 1153084.0836 | 2558203.188 | 1153093.7541 | 2558210.4258 | 1153099.6068 | 2558218.9545 | 1153105.7284 | 2558227.6559 | 1153111.3041 | 2558242.2911 | 1153118.3838 | 2558261.2093 | 1153124.6111 | 2558274.9995 | 1153128.2394
19 | 2558274.9995 | 1153128.2394 | 2558272.7728 | 1153143.4738 | 2558273.4293 | 1153155.6539
20 | 2558370.8771 | 1153303.6066 | 2558384.2747 | 1153263.2952 | 2558389.6209 | 1153247.5612 | 2558391.1542 | 1153241.3989
21 | 2558567.8146 | 1153112.427 | 2558567.9388 | 1153110.7521
22 | 2558537.7575 | 1152984.4576 | 2558538.5329 | 1152988.9768
23 | 2558669.8249 | 1153028.0811 | 2558662.9608 | 1153016.2667
24 | 2558669.8249 | 1153028.0811 | 2558683.8688 | 1153048.5283 | 2558683.028 | 1153059.0284 | 2558682.668 | 1153065.801
25 | 2558646.1068 | 1153134.3667 | 2558645.4764 | 1153131.335 | 2558645.3792 | 1153117.221
26 | 2558191.8494 | 1153084.0836 | 2558189.1724 | 1153085.3029 | 2558182.9699 | 1153084.8903 | 2558125.0243 | 1153052.9108 | 2558112.8786 | 1153050.7721 | 2558097.2642 | 1153056.2505 | 2558074.8418 | 1153053.8109
27 | 2558273.4293 | 1153155.6539 | 2558273.7594 | 1153161.7763 | 2558278.6216 | 1153198.2504
28 | 2558370.8767 | 1153303.6079 | 2558370.8771 | 1153303.6066
29 | 2558563.7677 | 1153149.8433 | 2558565.5738 | 1153142.6469 | 2558567.8146 | 1153112.427
30 | 2558537.7575 | 1152984.4576 | 2558541.2298 | 1152982.8439 | 2558543.9736 | 1152980.168 | 2558544.578 | 1152978.9619
31 | 2558646.1068 | 1153134.3667 | 2558648.0407 | 1153143.6669
32 | 2558654.0698 | 1153170.834 | 2558652.4914 | 1153165.0707 | 2558648.0407 | 1153143.6669
33 | 2558684.9619 | 1153279.8729 | 2558677.206 | 1153258.8376 | 2558668.165 | 1153226.1275 | 2558659.7874 | 1153191.7119 | 2558654.0698 | 1153170.834
34 | 2558684.9619 | 1153279.8729 | 2558673.4402 | 1153283.5762 | 2558662.0257 | 1153287.2455 | 2558638.8427 | 1153295.5427 | 2558622.7126 | 1153305.2032
35 | 2558622.7126 | 1153305.2032 | 2558617.3257 | 1153287.2755 | 2558611.2524 | 1153266.6179 | 2558611.1821 | 1153256.4242 | 2558612.0962 | 1153246.5573 | 2558611.3422 | 1153231.7771 | 2558610.2709 | 1153219.9562 | 2558603.3383 | 1153219.3481
36 | 2558310.8335 | 1153315.5401 | 2558314.3825 | 1153322.9197
37 | 2558303.9393 | 1153301.2049 | 2558310.8335 | 1153315.5401
38 | 2558314.3825 | 1153322.9197 | 2558315.0388 | 1153324.2843 | 2558318.4963 | 1153343.3162
39 | 2558303.9393 | 1153301.2049 | 2558297.9143 | 1153288.6768
40 | 2558318.4963 | 1153343.3162 | 2558320.1762 | 1153352.5632 | 2558311.2603 | 1153357.858
41 | 2558290.2036 | 1153272.6439 | 2558297.9143 | 1153288.6768
42 | 2558266.8107 | 1153373.0331 | 2558296.4052 | 1153366.6799 | 2558311.2603 | 1153357.858
43 | 2558287.8989 | 1153267.8435 | 2558287.9004 | 1153267.8548 | 2558290.2036 | 1153272.6439
44 | 2558284.3539 | 1153241.2508 | 2558287.8989 | 1153267.8435
45 | 2558532.371 | 1152962.2278 | 2558536.3678 | 1152962.1112 | 2558540.1516 | 1152963.3636 | 2558543.2838 | 1152965.8321 | 2558545.379 | 1152969.2305
46 | 2558545.379 | 1152969.2305 | 2558546.172 | 1152972.9603 | 2558545.6841 | 1152976.7545 | 2558544.578 | 1152978.9619
47 | 2558523.3627 | 1152922.1916 | 2558526.2027 | 1152932.3328 | 2558532.2369 | 1152953.9133 | 2558532.371 | 1152962.2278
48 | 2558532.371 | 1152962.2278 | 2558527.9037 | 1152964.2152 | 2558524.6681 | 1152967.8839
49 | 2558523.3627 | 1152922.1916 | 2558513.4144 | 1152919.3922 | 2558495.7404 | 1152915.6123 | 2558478.7525 | 1152910.0843
50 | 2558283.8422 | 1153237.4122 | 2558284.3539 | 1153241.2508
51 | 2558279.9258 | 1153208.0338 | 2558283.8422 | 1153237.4122
52 | 2558279.9258 | 1153208.0338 | 2558279.9101 | 1153207.9155
53 | 2558279.9101 | 1153207.9155 | 2558278.6216 | 1153198.2504
54 | 2558069.1854 | 1153053.1954 | 2558074.8418 | 1153053.8109
55 | 2558069.1854 | 1153053.1954 | 2558061.6428 | 1153052.3748 | 2558053.3565 | 1153051.4589
56 | 2558364.5411 | 1153325.7537 | 2558368.9951 | 1153309.2692 | 2558370.8767 | 1153303.6079
57 | 2558350.2207 | 1153467.4806 | 2558350.3965 | 1153462.9659 | 2558353.0295 | 1153412.2772 | 2558355.842 | 1153373.082 | 2558357.6062 | 1153359.7407 | 2558360.0696 | 1153344.3379 | 2558362.1579 | 1153334.574 | 2558364.5411 | 1153325.7537
58 | 2558350.2207 | 1153467.4806 | 2558345.3638 | 1153470.7492 | 2558308.1991 | 1153503.9019 | 2558286.0198 | 1153518.4299 | 2558241.6425 | 1153544.7629
59 | 2558241.6425 | 1153544.7629 | 2558228.0721 | 1153546.1246 | 2558176.6923 | 1153540.7682 | 2558165.0043 | 1153538.1038 | 2558149.8954 | 1153532.2838 | 2558143.2529 | 1153522.6029
60 | 2558038.63 | 1153049.8312 | 2558035.7169 | 1153049.5092
61 | 2558038.63 | 1153049.8312 | 2558043.595 | 1153050.38
62 | 2558035.7169 | 1153049.5092 | 2558029.9997 | 1153048.8773
63 | 2558043.595 | 1153050.38 | 2558047.6375 | 1153050.8268
64 | 2558029.9997 | 1153048.8773 | 2558014.4593 | 1153047.1597
65 | 2558047.6375 | 1153050.8268 | 2558053.3565 | 1153051.4589
66 | 2558008.4029 | 1153046.4903 | 2558014.4593 | 1153047.1597

## bus_geodata
| x | y | coords
0 | 2558510.9586 | 1153081.058
1 | 2558562.5009 | 1153055.3677
2 | 2558481.7233 | 1153104.495
3 | 2558566.9546 | 1153074.6048
4 | 2558557.779 | 1153040.4593
5 | 2558627.3674 | 1153050.9517
6 | 2558495.9537 | 1153130.7546
7 | 2558386.9786 | 1153145.2826
8 | 2558568.4007 | 1153080.8512
9 | 2558547.8664 | 1153017.3076
10 | 2558629.296 | 1153050.3153
11 | 2558632.8583 | 1153070.5907
12 | 2558545.7473 | 1153129.9427
13 | 2558274.9995 | 1153128.2394
14 | 2558391.1542 | 1153241.3989
15 | 2558567.9388 | 1153110.7521
16 | 2558538.5329 | 1152988.9768
17 | 2558669.8249 | 1153028.0811
18 | 2558645.3792 | 1153117.221
19 | 2558191.8494 | 1153084.0836
20 | 2558273.4293 | 1153155.6539
21 | 2558370.8771 | 1153303.6066
22 | 2558567.8146 | 1153112.427
23 | 2558537.7575 | 1152984.4576
24 | 2558646.1068 | 1153134.3667
25 | 2558648.0407 | 1153143.6669
26 | 2558654.0698 | 1153170.834
27 | 2558684.9619 | 1153279.8729
28 | 2558622.7126 | 1153305.2032
29 | 2558603.3383 | 1153219.3481
30 | 2558563.7677 | 1153149.8433
31 | 2558310.8335 | 1153315.5401
32 | 2558314.3825 | 1153322.9197
33 | 2558303.9393 | 1153301.2049
34 | 2558318.4963 | 1153343.3162
35 | 2558297.9143 | 1153288.6768
36 | 2558311.2603 | 1153357.858
37 | 2558290.2036 | 1153272.6439
38 | 2558266.8107 | 1153373.0331
39 | 2558287.8989 | 1153267.8435
40 | 2558662.9608 | 1153016.2667
41 | 2558682.668 | 1153065.801
42 | 2558545.379 | 1152969.2305
43 | 2558532.371 | 1152962.2278
44 | 2558544.578 | 1152978.962
45 | 2558524.6681 | 1152967.8838
46 | 2558523.3627 | 1152922.1916
47 | 2558478.7525 | 1152910.0843
48 | 2558284.3539 | 1153241.2508
49 | 2558283.8422 | 1153237.4122
50 | 2558279.9258 | 1153208.0338
51 | 2558279.9101 | 1153207.9155
52 | 2558278.6216 | 1153198.2504
53 | 2558074.8418 | 1153053.8109
54 | 2558069.1854 | 1153053.1954
55 | 2558364.5411 | 1153325.7537
56 | 2558370.8767 | 1153303.6079
57 | 2558350.2207 | 1153467.4806
58 | 2558241.6425 | 1153544.7629
59 | 2558143.2529 | 1153522.6029
60 | 2558038.63 | 1153049.8312
61 | 2558035.7169 | 1153049.5092
62 | 2558043.595 | 1153050.38
63 | 2558029.9997 | 1153048.8773
64 | 2558047.6375 | 1153050.8268
65 | 2558014.4593 | 1153047.1597
66 | 2558053.3565 | 1153051.4589
67 | 2558008.4029 | 1153046.4903
68 | 2558481.7233 | 1153104.495

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.51922 | -0.13219
1 | 0.9926 | -0.14153 | 0 | 0
2 | 0.99676 | -0.061129 | 0 | 0
3 | 0.9901 | -0.18995 | 0.025469 | 0.0063831
4 | 0.99132 | -0.16629 | 0.063573 | 0.015933
5 | 0.98654 | -0.25843 | 0 | 0
6 | 0.99612 | -0.07356 | 0 | 0
7 | 0.98891 | -0.2107 | 0 | 0
8 | 0.98943 | -0.20282 | 0.097849 | 0.024523
9 | 0.98865 | -0.21791 | 0.06013 | 0.01507
10 | 0.98645 | -0.2603 | 0.021057 | 0.0052775
11 | 0.98561 | -0.27649 | 0.0046181 | 0.0011574
12 | 0.99554 | -0.084749 | 0.012783 | 0.0032037
13 | 0.97856 | -0.41089 | 0 | 0
14 | 0.98726 | -0.24271 | 0.0067799 | 0.0016992
15 | 0.98902 | -0.21079 | 0.0078893 | 0.0019772
16 | 0.98713 | -0.24738 | 0 | 0
17 | 0.98514 | -0.28575 | 0 | 0
18 | 0.98359 | -0.31591 | 0.0073853 | 0.0018509
19 | 0.97782 | -0.4254 | 0 | 0
20 | 0.97718 | -0.438 | 0.0093118 | 0.0023338
21 | 0.98657 | -0.25613 | 0.0017682 | 0.00044315
22 | 0.98901 | -0.211 | 0.0031382 | 0.00078652
23 | 0.9869 | -0.2519 | 0 | 0
24 | 0.983 | -0.32752 | 0.011462 | 0.0028726
25 | 0.98277 | -0.33196 | 0.009156 | 0.0022947
26 | 0.98234 | -0.3404 | 0.0090967 | 0.0022798
27 | 0.98153 | -0.35615 | 0 | 0
28 | 0.98105 | -0.36554 | 0 | 0
29 | 0.98039 | -0.37862 | 0.007677 | 0.001924
30 | 0.98888 | -0.21364 | 0.0039286 | 0.00098459
31 | 0.97272 | -0.52566 | 0.0021112 | 0.00052911
32 | 0.97262 | -0.52777 | 0.0028369 | 0.00071099
33 | 0.97296 | -0.52095 | 0.0017351 | 0.00043485
34 | 0.9724 | -0.53205 | 0.0034477 | 0.00086407
35 | 0.97319 | -0.51639 | 0.0019416 | 0.00048661
36 | 0.97226 | -0.53485 | 0.0052146 | 0.0013069
37 | 0.97352 | -0.50992 | 0.0011548 | 0.00028943
38 | 0.97215 | -0.53702 | 0.0024715 | 0.00061941
39 | 0.97363 | -0.50787 | 0.0021575 | 0.00054073
40 | 0.98506 | -0.28733 | 0.0064644 | 0.0016201
41 | 0.98421 | -0.30387 | 0.023939 | 0.0059997
42 | 0.98626 | -0.26432 | 0 | 0
43 | 0.98598 | -0.26991 | 0 | 0
44 | 0.98645 | -0.26077 | 0.035471 | 0.0088898
45 | 0.98582 | -0.27302 | 0.017777 | 0.0044553
46 | 0.98591 | -0.27123 | 0 | 0
47 | 0.98583 | -0.27272 | 0.0017882 | 0.00044816
48 | 0.9742 | -0.49649 | 0.001957 | 0.00049047
49 | 0.97429 | -0.49471 | 0.0020795 | 0.00052117
50 | 0.97504 | -0.47997 | 0.0083119 | 0.0020832
51 | 0.97504 | -0.47989 | 0.0031168 | 0.00078116
52 | 0.97539 | -0.47301 | 0.0060493 | 0.0015161
53 | 0.97684 | -0.44469 | 0.000609 | 0.00015263
54 | 0.9768 | -0.4455 | 0.00060918 | 0.00015268
55 | 0.9864 | -0.25941 | 0.0031497 | 0.00078938
56 | 0.98657 | -0.25613 | 0.0017687 | 0.00044327
57 | 0.98578 | -0.27162 | 0 | 0
58 | 0.98519 | -0.28305 | 0 | 0
59 | 0.98473 | -0.29204 | 0.0047642 | 0.001194
60 | 0.97661 | -0.44923 | 0.0033518 | 0.00084005
61 | 0.97661 | -0.44934 | 0.00042165 | 0.00010568
62 | 0.97664 | -0.44874 | 0.00088014 | 0.00022058
63 | 0.9766 | -0.44951 | 0.00042165 | 0.00010568
64 | 0.97666 | -0.44827 | 0.00042153 | 0.00010565
65 | 0.97658 | -0.44985 | 0.0005908 | 0.00014807
66 | 0.9767 | -0.44757 | 0.00042162 | 0.00010567
67 | 0.97658 | -0.44992 | 0.00060901 | 0.00015263
68 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.42256 | 0.10771 | -0.41969 | -0.10588 | 0.0028653 | 0.0018315 | 0.62941 | 0.62941 | 0.62941 | 1 | 0 | 0.9926 | -0.14153 | 57.6383
1 | 0.09501 | 0.024478 | -0.094728 | -0.024298 | 0.00028179 | 0.00017985 | 0.14161 | 0.14161 | 0.14161 | 1 | 0 | 0.99676 | -0.061129 | 38.9047
2 | 0.13867 | 0.034907 | -0.13835 | -0.034702 | 0.00032016 | 0.00020465 | 0.20794 | 0.20794 | 0.20794 | 0.9926 | -0.14153 | 0.9901 | -0.18995 | 57.1253
3 | 0.17936 | 0.045191 | -0.17915 | -0.045055 | 0.00021212 | 0.00013535 | 0.26897 | 0.26897 | 0.26897 | 0.9926 | -0.14153 | 0.99132 | -0.16629 | 36.9459
4 | 0.10166 | 0.025785 | -0.10109 | -0.025422 | 0.00056789 | 0.00036262 | 0.15251 | 0.15251 | 0.15251 | 0.9926 | -0.14153 | 0.98654 | -0.25843 | 41.8982
5 | 0.012797 | 0.0032115 | -0.01279 | -0.0032074 | 7.5821e-06 | 4.1311e-06 | 0.019106 | 0.019106 | 0.019106 | 0.99676 | -0.061129 | 0.99612 | -0.07356 | 5.2489
6 | 0.081931 | 0.021087 | -0.081339 | -0.02071 | 0.00059132 | 0.00037708 | 0.12251 | 0.12251 | 0.12251 | 0.99676 | -0.061129 | 0.98891 | -0.2107 | 33.6561
7 | 0.11288 | 0.028319 | -0.11281 | -0.028275 | 6.9207e-05 | 4.421e-05 | 0.16966 | 0.16966 | 0.16966 | 0.9901 | -0.18995 | 0.98943 | -0.20282 | 46.6096
8 | 0.11557 | 0.029122 | -0.11529 | -0.028941 | 0.00028464 | 0.00018184 | 0.17354 | 0.17354 | 0.17354 | 0.99132 | -0.16629 | 0.98865 | -0.21791 | 47.6756
9 | 0.051523 | 0.012936 | -0.051519 | -0.012933 | 4.6007e-06 | 2.9185e-06 | 0.077722 | 0.077722 | 0.077722 | 0.98654 | -0.25843 | 0.98645 | -0.2603 | 21.3521
10 | 0.049569 | 0.012486 | -0.049526 | -0.012459 | 4.2772e-05 | 2.7114e-05 | 0.074788 | 0.074788 | 0.074788 | 0.98654 | -0.25843 | 0.98561 | -0.27649 | 20.5461
11 | 0.01279 | 0.0032074 | -0.012783 | -0.0032037 | 6.8173e-06 | 3.7152e-06 | 0.019106 | 0.019106 | 0.019106 | 0.99612 | -0.07356 | 0.99554 | -0.084749 | 5.249
12 | 0.063065 | 0.01612 | -0.062461 | -0.015735 | 0.00060433 | 0.0003845 | 0.095007 | 0.095008 | 0.095008 | 0.98891 | -0.2107 | 0.97856 | -0.41089 | 26.1011
13 | 0.018274 | 0.0045898 | -0.018247 | -0.0045733 | 2.7868e-05 | 1.6577e-05 | 0.027501 | 0.027502 | 0.027502 | 0.98891 | -0.2107 | 0.98726 | -0.24271 | 7.5554
14 | 0.014962 | 0.0037515 | -0.014957 | -0.0037482 | 5.6792e-06 | 3.2507e-06 | 0.022503 | 0.022503 | 0.022503 | 0.98943 | -0.20282 | 0.98902 | -0.21079 | 6.1821
15 | 0.05516 | 0.01387 | -0.055082 | -0.013821 | 7.7519e-05 | 4.9229e-05 | 0.083037 | 0.083037 | 0.083037 | 0.98865 | -0.21791 | 0.98713 | -0.24738 | 22.8124
16 | 0.030462 | 0.0076557 | -0.030425 | -0.0076327 | 3.6955e-05 | 2.3056e-05 | 0.045958 | 0.045958 | 0.045958 | 0.98645 | -0.2603 | 0.98514 | -0.28575 | 12.6258
17 | 0.044908 | 0.011301 | -0.044824 | -0.011248 | 8.4441e-05 | 5.3419e-05 | 0.067816 | 0.067816 | 0.067816 | 0.98561 | -0.27649 | 0.98359 | -0.31591 | 18.6308
18 | 0.0083514 | 0.0020953 | -0.0083456 | -0.0020928 | 5.7751e-06 | 2.4975e-06 | 0.0127 | 0.0127 | 0.0127 | 0.97856 | -0.41089 | 0.97782 | -0.4254 | 3.4891
19 | 0.054109 | 0.01364 | -0.054039 | -0.013595 | 7.0102e-05 | 4.4519e-05 | 0.082308 | 0.082308 | 0.082308 | 0.97856 | -0.41089 | 0.97718 | -0.438 | 22.6121
20 | 0.011467 | 0.0028741 | -0.011459 | -0.0028702 | 7.331e-06 | 3.8556e-06 | 0.017283 | 0.017283 | 0.017283 | 0.98726 | -0.24271 | 0.98657 | -0.25613 | 4.7481
21 | 0.0070674 | 0.001771 | -0.0070673 | -0.0017709 | 7.1207e-08 | 2.402e-08 | 0.010633 | 0.010633 | 0.010633 | 0.98902 | -0.21079 | 0.98901 | -0.211 | 2.9212
22 | 0.055082 | 0.013821 | -0.05507 | -0.013814 | 1.1858e-05 | 7.5305e-06 | 0.083037 | 0.083037 | 0.083037 | 0.98713 | -0.24738 | 0.9869 | -0.2519 | 22.8124
23 | 0.0064649 | 0.0016203 | -0.0064644 | -0.0016201 | 4.8859e-07 | 1.3874e-07 | 0.0097649 | 0.009765 | 0.009765 | 0.98514 | -0.28575 | 0.98506 | -0.28733 | 2.6827
24 | 0.02396 | 0.0060124 | -0.023939 | -0.0059997 | 2.0691e-05 | 1.2707e-05 | 0.036193 | 0.036193 | 0.036193 | 0.98514 | -0.28575 | 0.98421 | -0.30387 | 9.9432
25 | 0.037438 | 0.009397 | -0.037418 | -0.009384 | 2.0708e-05 | 1.3035e-05 | 0.056643 | 0.056643 | 0.056643 | 0.98359 | -0.31591 | 0.983 | -0.32752 | 15.5613
26 | 0.0083456 | 0.0020928 | -0.008338 | -0.0020894 | 7.6689e-06 | 3.3194e-06 | 0.0127 | 0.012701 | 0.012701 | 0.97782 | -0.4254 | 0.97684 | -0.44469 | 3.4893
27 | 0.044727 | 0.011262 | -0.044653 | -0.011214 | 7.4718e-05 | 4.7283e-05 | 0.068128 | 0.068128 | 0.068128 | 0.97718 | -0.438 | 0.97539 | -0.47301 | 18.7166
28 | 0.0096912 | 0.0024271 | -0.0096912 | -0.0024271 | 1.0603e-10 | 6.7858e-11 | 0.014616 | 0.014616 | 0.014616 | 0.98657 | -0.25613 | 0.98657 | -0.25613 | 4.0155
29 | 0.0039291 | 0.00098442 | -0.0039286 | -0.00098459 | 4.9433e-07 | -1.6764e-07 | 0.0059114 | 0.0059115 | 0.0059115 | 0.98901 | -0.211 | 0.98888 | -0.21364 | 1.624
30 | 0.05507 | 0.013814 | -0.055047 | -0.013799 | 2.3299e-05 | 1.4796e-05 | 0.083037 | 0.083037 | 0.083037 | 0.9869 | -0.2519 | 0.98645 | -0.26077 | 22.8125
31 | 0.025956 | 0.0065114 | -0.02595 | -0.006508 | 5.4998e-06 | 3.3995e-06 | 0.039293 | 0.039293 | 0.039293 | 0.983 | -0.32752 | 0.98277 | -0.33196 | 10.7948
32 | 0.016794 | 0.0042133 | -0.016788 | -0.0042094 | 6.7507e-06 | 3.9679e-06 | 0.02543 | 0.02543 | 0.02543 | 0.98277 | -0.33196 | 0.98234 | -0.3404 | 6.9863
33 | 0.007691 | 0.0019295 | -0.0076852 | -0.0019272 | 5.7738e-06 | 2.2604e-06 | 0.011651 | 0.011651 | 0.011651 | 0.98234 | -0.3404 | 0.98153 | -0.35615 | 3.2009
34 | 0.0076852 | 0.0019272 | -0.0076817 | -0.0019259 | 3.4372e-06 | 1.3468e-06 | 0.011651 | 0.011652 | 0.011652 | 0.98153 | -0.35615 | 0.98105 | -0.36554 | 3.201
35 | 0.0076817 | 0.0019259 | -0.007677 | -0.001924 | 4.7848e-06 | 1.8763e-06 | 0.011652 | 0.011652 | 0.011652 | 0.98105 | -0.36554 | 0.98039 | -0.37862 | 3.2011
36 | 0.013976 | 0.0035034 | -0.013974 | -0.0035026 | 1.4036e-06 | 7.9664e-07 | 0.021379 | 0.021379 | 0.021379 | 0.97272 | -0.52566 | 0.97262 | -0.52777 | 5.8735
37 | -0.016087 | -0.0040325 | 0.01609 | 0.0040346 | 3.6124e-06 | 2.1145e-06 | 0.024609 | 0.024609 | 0.024609 | 0.97272 | -0.52566 | 0.97296 | -0.52095 | 6.7607
38 | 0.011137 | 0.0027916 | -0.011135 | -0.0027904 | 2.2709e-06 | 1.1946e-06 | 0.017039 | 0.017039 | 0.017039 | 0.97262 | -0.52777 | 0.9724 | -0.53205 | 4.6811
39 | -0.017826 | -0.0044694 | 0.017829 | 0.0044717 | 3.8746e-06 | 2.307e-06 | 0.027262 | 0.027262 | 0.027262 | 0.97296 | -0.52095 | 0.97319 | -0.51639 | 7.4897
40 | 0.0076874 | 0.0019263 | -0.0076864 | -0.0019259 | 1.0258e-06 | 4.1133e-07 | 0.011764 | 0.011764 | 0.011764 | 0.9724 | -0.53205 | 0.97226 | -0.53485 | 3.2318
41 | -0.019771 | -0.0049583 | 0.019777 | 0.004962 | 6.0972e-06 | 3.6811e-06 | 0.030231 | 0.030231 | 0.030231 | 0.97319 | -0.51639 | 0.97352 | -0.50992 | 8.3052
42 | 0.0024717 | 0.00061898 | -0.0024715 | -0.00061941 | 2.5514e-07 | -4.2628e-07 | 0.0037827 | 0.003783 | 0.003783 | 0.97226 | -0.53485 | 0.97215 | -0.53702 | 1.0393
43 | -0.020932 | -0.0052515 | 0.020934 | 0.0052527 | 2.0445e-06 | 1.2423e-06 | 0.031996 | 0.031996 | 0.031996 | 0.97352 | -0.50992 | 0.97363 | -0.50787 | 8.7901
44 | -0.023091 | -0.0057934 | 0.023104 | 0.0058011 | 1.2532e-05 | 7.6864e-06 | 0.035294 | 0.035293 | 0.035294 | 0.97363 | -0.50787 | 0.9742 | -0.49649 | 9.696
45 | 0.019573 | 0.0049072 | -0.019568 | -0.0049041 | 5.2107e-06 | 3.1316e-06 | 0.029531 | 0.029531 | 0.029531 | 0.98626 | -0.26432 | 0.98598 | -0.26991 | 8.113
46 | -0.019573 | -0.0049072 | 0.019576 | 0.0049092 | 3.3056e-06 | 1.9866e-06 | 0.029531 | 0.029531 | 0.029531 | 0.98626 | -0.26432 | 0.98645 | -0.26077 | 8.113
47 | 0.0017884 | 0.00044719 | -0.0017883 | -0.00044765 | 1.1269e-07 | -4.5406e-07 | 0.0026987 | 0.0026988 | 0.0026988 | 0.98598 | -0.26991 | 0.98591 | -0.27123 | 0.74144
48 | 0.01778 | 0.0044569 | -0.017777 | -0.0044553 | 2.6409e-06 | 1.5655e-06 | 0.026833 | 0.026833 | 0.026833 | 0.98598 | -0.26991 | 0.98582 | -0.27302 | 7.3717
49 | 0.0017883 | 0.00044765 | -0.0017882 | -0.00044816 | 1.264e-07 | -5.0914e-07 | 0.0026988 | 0.002699 | 0.002699 | 0.98591 | -0.27123 | 0.98583 | -0.27272 | 0.7415
50 | -0.025061 | -0.0062916 | 0.025063 | 0.0062929 | 2.1283e-06 | 1.3139e-06 | 0.038283 | 0.038283 | 0.038283 | 0.9742 | -0.49649 | 0.97429 | -0.49471 | 10.5172
51 | -0.027143 | -0.0068141 | 0.027162 | 0.0068259 | 1.9103e-05 | 1.1857e-05 | 0.041458 | 0.041458 | 0.041458 | 0.97429 | -0.49471 | 0.97504 | -0.47997 | 11.3897
52 | -0.035474 | -0.0089091 | 0.035474 | 0.0089092 | 1.312e-07 | 8.2479e-08 | 0.054143 | 0.054143 | 0.054143 | 0.97504 | -0.47997 | 0.97504 | -0.47989 | 14.8745
53 | -0.038591 | -0.0096903 | 0.038603 | 0.0096983 | 1.2685e-05 | 7.9967e-06 | 0.0589 | 0.0589 | 0.0589 | 0.97504 | -0.47989 | 0.97539 | -0.47301 | 16.1813
54 | 0.007729 | 0.0019368 | -0.0077287 | -0.0019367 | 2.9575e-07 | 1.1806e-07 | 0.011773 | 0.011773 | 0.011773 | 0.97684 | -0.44469 | 0.9768 | -0.4455 | 3.2345
55 | 0.0071195 | 0.001784 | -0.0071188 | -0.0017838 | 7.0238e-07 | 2.5022e-07 | 0.010845 | 0.010845 | 0.010845 | 0.9768 | -0.4455 | 0.9767 | -0.44757 | 2.9795
56 | -0.0079213 | -0.0019833 | 0.0079225 | 0.0019838 | 1.2336e-06 | 4.9535e-07 | 0.011949 | 0.011949 | 0.011949 | 0.9864 | -0.25941 | 0.98657 | -0.25613 | 3.2826
57 | 0.0047716 | 0.0011939 | -0.0047688 | -0.0011939 | 2.7733e-06 | -4.6126e-08 | 0.0071974 | 0.007198 | 0.007198 | 0.9864 | -0.25941 | 0.98578 | -0.27162 | 1.9775
58 | 0.0047688 | 0.0011939 | -0.0047662 | -0.001194 | 2.5945e-06 | -4.0765e-08 | 0.007198 | 0.0071986 | 0.0071986 | 0.98578 | -0.27162 | 0.98519 | -0.28305 | 1.9776
59 | 0.0047662 | 0.001194 | -0.0047642 | -0.001194 | 2.0395e-06 | -3.0426e-08 | 0.0071986 | 0.0071991 | 0.0071991 | 0.98519 | -0.28305 | 0.98473 | -0.29204 | 1.9778
60 | 0.0020432 | 0.0005117 | -0.0020432 | -0.00051173 | 1.065e-08 | -2.9856e-08 | 0.0031129 | 0.003113 | 0.003113 | 0.97661 | -0.44923 | 0.97661 | -0.44934 | 0.85521
61 | -0.005395 | -0.0013518 | 0.0053951 | 0.0013518 | 1.2657e-07 | 1.8498e-08 | 0.00822 | 0.00822 | 0.00822 | 0.97661 | -0.44923 | 0.97664 | -0.44874 | 2.2582
62 | 0.0016215 | 0.00040606 | -0.0016215 | -0.00040612 | 1.3165e-08 | -6.3547e-08 | 0.0024705 | 0.0024705 | 0.0024705 | 0.97661 | -0.44934 | 0.9766 | -0.44951 | 0.67871
63 | -0.0062753 | -0.0015724 | 0.0062754 | 0.0015724 | 1.3942e-07 | 3.8333e-08 | 0.0095609 | 0.0095609 | 0.0095609 | 0.97664 | -0.44874 | 0.97666 | -0.44827 | 2.6266
64 | 0.0011998 | 0.00030044 | -0.0011998 | -0.00030063 | 1.9594e-08 | -1.8309e-07 | 0.0018281 | 0.0018281 | 0.0018281 | 0.9766 | -0.44951 | 0.97658 | -0.44985 | 0.50223
65 | -0.0066969 | -0.001678 | 0.0066972 | 0.0016781 | 2.2463e-07 | 7.1753e-08 | 0.010203 | 0.010203 | 0.010203 | 0.97666 | -0.44827 | 0.9767 | -0.44757 | 2.8031
66 | 0.00060901 | 0.00015256 | -0.00060901 | -0.00015263 | 1.9675e-09 | -7.4979e-08 | 0.00092792 | 0.00092795 | 0.00092795 | 0.97658 | -0.44985 | 0.97658 | -0.44992 | 0.25493

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.54693 | 0.13914

## res_load
| p_mw | q_mvar
0 | 0.027711 | 0.006945
1 | 0.025469 | 0.0063831
2 | 0.063573 | 0.015933
3 | 0.097849 | 0.024523
4 | 0.06013 | 0.01507
5 | 0.021057 | 0.0052775
6 | 0.0046181 | 0.0011574
7 | 0.012783 | 0.0032037
8 | 0.0067799 | 0.0016992
9 | 0.0078893 | 0.0019772
10 | 0.0073853 | 0.0018509
11 | 0.0093118 | 0.0023338
12 | 0.0017682 | 0.00044315
13 | 0.0031382 | 0.00078652
14 | 0.011462 | 0.0028726
15 | 0.009156 | 0.0022947
16 | 0.0090967 | 0.0022798
17 | 0.007677 | 0.001924
18 | 0.0039286 | 0.00098459
19 | 0.0021112 | 0.00052911
20 | 0.0028369 | 0.00071099
21 | 0.0017351 | 0.00043485
22 | 0.0034477 | 0.00086407
23 | 0.0019416 | 0.00048661
24 | 0.0052146 | 0.0013069
25 | 0.0011548 | 0.00028943
26 | 0.0024715 | 0.00061941
27 | 0.0021575 | 0.00054073
28 | 0.0064644 | 0.0016201
29 | 0.023939 | 0.0059997
30 | 0.035471 | 0.0088898
31 | 0.017777 | 0.0044553
32 | 0.0017882 | 0.00044816
33 | 0.001957 | 0.00049047
34 | 0.0020795 | 0.00052117
35 | 0.0083119 | 0.0020832
36 | 0.0031168 | 0.00078116
37 | 0.0060493 | 0.0015161
38 | 0.000609 | 0.00015263
39 | 0.00060918 | 0.00015268
40 | 0.0031497 | 0.00078938
41 | 0.0017687 | 0.00044327
42 | 0.0047642 | 0.001194
43 | 0.0033518 | 0.00084005
44 | 0.00042165 | 0.00010568
45 | 0.00088014 | 0.00022058
46 | 0.00042165 | 0.00010568
47 | 0.00042153 | 0.00010565
48 | 0.0005908 | 0.00014807
49 | 0.00042162 | 0.00010567
50 | 0.00060901 | 0.00015263

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1