## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-2_1_2_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_2325-2_1_2_node_8 | 0.4 | n |  | TRUE
2 | bus_LV_2325-2_1_2_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_2325-2_1_2_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_2325-2_1_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_2325-2_1_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_2325-2_1_2_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2325-2_1_2_node_43 | 0.4 | n |  | TRUE
8 | bus_LV_2325-2_1_2_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_2325-2_1_2_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_2325-2_1_2_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_2325-2_1_2_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_2325-2_1_2_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_2325-2_1_2_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_2325-2_1_2_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2325-2_1_2_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_2325-2_1_2_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_2325-2_1_2_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_2325-2_1_2_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_2325-2_1_2_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_2325-2_1_2_node_226 | 0.4 | n |  | TRUE
21 | bus_LV_2325-2_1_2_node_153 | 0.4 | n |  | TRUE
22 | bus_LV_2325-2_1_2_node_269 | 0.4 | n |  | TRUE
23 | bus_LV_2325-2_1_2_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_2325-2_1_2_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_2325-2_1_2_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_2325-2_1_2_node_160 | 0.4 | n |  | TRUE
27 | bus_LV_2325-2_1_2_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_2325-2_1_2_node_47 | 0.4 | n |  | TRUE
29 | bus_LV_2325-2_1_2_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_2325-2_1_2_node_51 | 0.4 | n |  | TRUE
31 | bus_LV_2325-2_1_2_node_49 | 0.4 | n |  | TRUE
32 | bus_LV_2325-2_1_2_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_2325-2_1_2_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_2325-2_1_2_node_162 | 0.4 | n |  | TRUE
35 | bus_LV_2325-2_1_2_node_87 | 0.4 | n |  | TRUE
36 | bus_LV_2325-2_1_2_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_2325-2_1_2_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_2325-2_1_2_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_2325-2_1_2_node_65 | 0.4 | n |  | TRUE
40 | bus_LV_2325-2_1_2_node_66 | 0.4 | n |  | TRUE
41 | bus_LV_2325-2_1_2_node_67 | 0.4 | n |  | TRUE
42 | bus_LV_2325-2_1_2_node_68 | 0.4 | n |  | TRUE
43 | bus_LV_2325-2_1_2_node_69 | 0.4 | n |  | TRUE
44 | bus_LV_2325-2_1_2_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_2325-2_1_2_node_71 | 0.4 | n |  | TRUE
46 | bus_LV_2325-2_1_2_node_157 | 0.4 | n |  | TRUE
47 | bus_LV_2325-2_1_2_node_271 | 0.4 | n |  | TRUE
48 | bus_LV_2325-2_1_2_node_250 | 0.4 | n |  | TRUE
49 | bus_LV_2325-2_1_2_node_95 | 0.4 | n |  | TRUE
50 | bus_LV_2325-2_1_2_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_2325-2_1_2_node_97 | 0.4 | n |  | TRUE
52 | bus_LV_2325-2_1_2_node_98 | 0.4 | n |  | TRUE
53 | bus_LV_2325-2_1_2_node_99 | 0.4 | n |  | TRUE
54 | bus_LV_2325-2_1_2_node_100 | 0.4 | n |  | TRUE
55 | bus_LV_2325-2_1_2_node_101 | 0.4 | n |  | TRUE
56 | bus_LV_2325-2_1_2_node_102 | 0.4 | n |  | TRUE
57 | bus_LV_2325-2_1_2_node_180 | 0.4 | n |  | TRUE
58 | bus_LV_2325-2_1_2_node_198 | 0.4 | n |  | TRUE
59 | bus_LV_2325-2_1_2_node_107 | 0.4 | n |  | TRUE
60 | bus_LV_2325-2_1_2_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_2325-2_1_2_node_109 | 0.4 | n |  | TRUE
62 | bus_LV_2325-2_1_2_node_110 | 0.4 | n |  | TRUE
63 | bus_LV_2325-2_1_2_node_111 | 0.4 | n |  | TRUE
64 | bus_LV_2325-2_1_2_node_112 | 0.4 | n |  | TRUE
65 | bus_LV_2325-2_1_2_node_113 | 0.4 | n |  | TRUE
66 | bus_LV_2325-2_1_2_node_251 | 0.4 | n |  | TRUE
67 | bus_LV_2325-2_1_2_node_161 | 0.4 | n |  | TRUE
68 | bus_LV_2325-2_1_2_node_142 | 0.4 | n |  | TRUE
69 | bus_LV_2325-2_1_2_node_120 | 0.4 | n |  | TRUE
70 | bus_LV_2325-2_1_2_node_121 | 0.4 | n |  | TRUE
71 | bus_LV_2325-2_1_2_node_122 | 0.4 | n |  | TRUE
72 | bus_LV_2325-2_1_2_node_123 | 0.4 | n |  | TRUE
73 | bus_LV_2325-2_1_2_node_124 | 0.4 | n |  | TRUE
74 | bus_LV_2325-2_1_2_node_126 | 0.4 | n |  | TRUE
75 | bus_LV_2325-2_1_2_node_127 | 0.4 | n |  | TRUE
76 | bus_LV_2325-2_1_2_node_125 | 0.4 | n |  | TRUE
77 | bus_LV_2325-2_1_2_node_234 | 0.4 | n |  | TRUE
78 | bus_LV_2325-2_1_2_node_128 | 0.4 | n |  | TRUE
79 | bus_LV_2325-2_1_2_node_129 | 0.4 | n |  | TRUE
80 | bus_LV_2325-2_1_2_node_130 | 0.4 | n |  | TRUE
81 | bus_LV_2325-2_1_2_node_131 | 0.4 | n |  | TRUE
82 | bus_LV_2325-2_1_2_node_132 | 0.4 | n |  | TRUE
83 | bus_LV_2325-2_1_2_node_176 | 0.4 | n |  | TRUE
84 | bus_LV_2325-2_1_2_node_224 | 0.4 | n |  | TRUE
85 | bus_LV_2325-2_1_2_node_140 | 0.4 | n |  | TRUE
86 | bus_LV_2325-2_1_2_node_141 | 0.4 | n |  | TRUE
87 | bus_LV_2325-2_1_2_node_211 | 0.4 | n |  | TRUE
88 | bus_LV_2325-2_1_2_node_154 | 0.4 | n |  | TRUE
89 | bus_LV_2325-2_1_2_node_155 | 0.4 | n |  | TRUE
90 | bus_LV_2325-2_1_2_node_156 | 0.4 | n |  | TRUE
91 | bus_LV_2325-2_1_2_node_158 | 0.4 | n |  | TRUE
92 | bus_LV_2325-2_1_2_node_159 | 0.4 | n |  | TRUE
93 | bus_LV_2325-2_1_2_node_179 | 0.4 | n |  | TRUE
94 | bus_LV_2325-2_1_2_node_175 | 0.4 | n |  | TRUE
95 | bus_LV_2325-2_1_2_node_163 | 0.4 | n |  | TRUE
96 | bus_LV_2325-2_1_2_node_164 | 0.4 | n |  | TRUE
97 | bus_LV_2325-2_1_2_node_177 | 0.4 | n |  | TRUE
98 | bus_LV_2325-2_1_2_node_178 | 0.4 | n |  | TRUE
99 | bus_LV_2325-2_1_2_node_233 | 0.4 | n |  | TRUE
100 | bus_LV_2325-2_1_2_node_181 | 0.4 | n |  | TRUE
101 | bus_LV_2325-2_1_2_node_182 | 0.4 | n |  | TRUE
102 | bus_LV_2325-2_1_2_node_183 | 0.4 | n |  | TRUE
103 | bus_LV_2325-2_1_2_node_186 | 0.4 | n |  | TRUE
104 | bus_LV_2325-2_1_2_node_232 | 0.4 | n |  | TRUE
105 | bus_LV_2325-2_1_2_node_199 | 0.4 | n |  | TRUE
106 | bus_LV_2325-2_1_2_node_200 | 0.4 | n |  | TRUE
107 | bus_LV_2325-2_1_2_node_208 | 0.4 | n |  | TRUE
108 | bus_LV_2325-2_1_2_node_209 | 0.4 | n |  | TRUE
109 | bus_LV_2325-2_1_2_node_212 | 0.4 | n |  | TRUE
110 | bus_LV_2325-2_1_2_node_213 | 0.4 | n |  | TRUE
111 | bus_LV_2325-2_1_2_node_214 | 0.4 | n |  | TRUE
112 | bus_LV_2325-2_1_2_node_248 | 0.4 | n |  | TRUE
113 | bus_LV_2325-2_1_2_node_223 | 0.4 | n |  | TRUE
114 | bus_LV_2325-2_1_2_node_225 | 0.4 | n |  | TRUE
115 | bus_LV_2325-2_1_2_node_227 | 0.4 | n |  | TRUE
116 | bus_LV_2325-2_1_2_node_249 | 0.4 | n |  | TRUE
117 | bus_LV_2325-2_1_2_node_268 | 0.4 | n |  | TRUE
118 | bus_LV_2325-2_1_2_node_252 | 0.4 | n |  | TRUE
119 | bus_LV_2325-2_1_2_node_266 | 0.4 | n |  | TRUE
120 | bus_LV_2325-2_1_2_node_267 | 0.4 | n |  | TRUE
121 | bus_LV_2325-2_1_2_node_270 | 0.4 | n |  | TRUE
122 | bus_LV_2325-2_1_2_node_272 | 0.4 | n |  | TRUE
123 | bus_MV_37_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-2_1_2_load_7 | 0 | 0.0073159 | 0.0018335 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-2_1_2_load_8 | 1 | 0.0074856 | 0.0018761 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-2_1_2_load_9 | 2 | 0.0033558 | 0.00084104 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-2_1_2_load_11 | 4 | 0.0095497 | 0.0023934 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-2_1_2_load_13 | 6 | 0.0039117 | 0.00098038 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-2_1_2_load_43 | 7 | 0.011343 | 0.0028429 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-2_1_2_load_32 | 8 | 0.0036156 | 0.00090616 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-2_1_2_load_30 | 9 | 0.0021708 | 0.00054405 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-2_1_2_load_20 | 10 | 0.00054881 | 0.00013755 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-2_1_2_load_21 | 11 | 9.3825e-05 | 2.3515e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-2_1_2_load_24 | 14 | 0.00047303 | 0.00011855 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-2_1_2_load_25 | 15 | 0.00011482 | 2.8776e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-2_1_2_load_28 | 16 | 0.00037883 | 9.4944e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-2_1_2_load_52 | 17 | 0.00062258 | 0.00015603 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-2_1_2_load_29 | 18 | 0.00038134 | 9.5572e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-2_1_2_load_226 | 20 | 0.0010648 | 0.00026687 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-2_1_2_load_153 | 21 | 0.0013034 | 0.00032667 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-2_1_2_load_42 | 23 | 0.000623 | 0.00015614 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-2_1_2_load_44 | 24 | 0.0015528 | 0.00038916 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-2_1_2_load_160 | 26 | 0.0042949 | 0.0010764 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-2_1_2_load_46 | 27 | 0.00029684 | 7.4395e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-2_1_2_load_48 | 29 | 0.00037555 | 9.4123e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-2_1_2_load_49 | 31 | 0.00011627 | 2.9139e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-2_1_2_load_50 | 32 | 0.00068179 | 0.00017087 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-2_1_2_load_53 | 33 | 0.00016965 | 4.2517e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-2_1_2_load_162 | 34 | 0.0006809 | 0.00017065 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-2_1_2_load_87 | 35 | 0.00033123 | 8.3014e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-2_1_2_load_62 | 36 | 0.0054452 | 0.0013647 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-2_1_2_load_63 | 37 | 0.0010474 | 0.00026251 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-2_1_2_load_65 | 39 | 0.0014344 | 0.00035949 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-2_1_2_load_68 | 42 | 0.0013627 | 0.00034152 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-2_1_2_load_69 | 43 | 0.0016873 | 0.00042288 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-2_1_2_load_70 | 44 | 0.0010739 | 0.00026913 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-2_1_2_load_71 | 45 | 0.002149 | 0.00053859 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-2_1_2_load_271 | 47 | 0.0010595 | 0.00026555 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-2_1_2_load_250 | 48 | 0.00018391 | 4.6092e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-2_1_2_load_95 | 49 | 0.002078 | 0.00052079 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-2_1_2_load_97 | 51 | 0.0010972 | 0.00027499 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-2_1_2_load_98 | 52 | 0.001489 | 0.00037317 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-2_1_2_load_99 | 53 | 0.00075191 | 0.00018845 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-2_1_2_load_100 | 54 | 0.0010341 | 0.00025917 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-2_1_2_load_101 | 55 | 0.00058933 | 0.0001477 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-2_1_2_load_102 | 56 | 0.00055089 | 0.00013807 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-2_1_2_load_180 | 57 | 0.0013098 | 0.00032827 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-2_1_2_load_198 | 58 | 0.00076025 | 0.00019054 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-2_1_2_load_107 | 59 | 0.00017847 | 4.4729e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-2_1_2_load_108 | 60 | 0.00026027 | 6.5229e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-2_1_2_load_110 | 62 | 7.9656e-05 | 1.9964e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-2_1_2_load_111 | 63 | 0.00043283 | 0.00010848 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-2_1_2_load_112 | 64 | 0.00024923 | 6.2463e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-2_1_2_load_113 | 65 | 0.00026803 | 6.7175e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2325-2_1_2_load_251 | 66 | 0.00016806 | 4.212e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2325-2_1_2_load_142 | 68 | 0.00022398 | 5.6135e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2325-2_1_2_load_120 | 69 | 0.00062243 | 0.000156 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2325-2_1_2_load_121 | 70 | 0.001578 | 0.00039549 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2325-2_1_2_load_123 | 72 | 0.00062401 | 0.00015639 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2325-2_1_2_load_126 | 74 | 0.0019475 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2325-2_1_2_load_125 | 76 | 0.00075775 | 0.00018991 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2325-2_1_2_load_234 | 77 | 0.0011111 | 0.00027846 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2325-2_1_2_load_128 | 78 | 0.0014563 | 0.00036498 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2325-2_1_2_load_129 | 79 | 0.0028657 | 0.00071821 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2325-2_1_2_load_131 | 81 | 0.0028527 | 0.00071496 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2325-2_1_2_load_132 | 82 | 0.0024522 | 0.00061457 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2325-2_1_2_load_176 | 83 | 0.00098347 | 0.00024648 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2325-2_1_2_load_224 | 84 | 0.0022376 | 0.0005608 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2325-2_1_2_load_140 | 85 | 7.7397e-05 | 1.9398e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2325-2_1_2_load_141 | 86 | 7.082e-05 | 1.7749e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2325-2_1_2_load_211 | 87 | 0.00083464 | 0.00020918 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2325-2_1_2_load_154 | 88 | 0.0020379 | 0.00051074 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2325-2_1_2_load_155 | 89 | 0.010104 | 0.0025324 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2325-2_1_2_load_158 | 91 | 0.0034408 | 0.00086235 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2325-2_1_2_load_159 | 92 | 0.0015935 | 0.00039937 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2325-2_1_2_load_179 | 93 | 0.0010828 | 0.00027137 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2325-2_1_2_load_175 | 94 | 0.0023587 | 0.00059115 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2325-2_1_2_load_164 | 96 | 0.00012251 | 3.0704e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2325-2_1_2_load_177 | 97 | 0.003629 | 0.00090952 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2325-2_1_2_load_178 | 98 | 0.0010044 | 0.00025173 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2325-2_1_2_load_233 | 99 | 0.00098099 | 0.00024586 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2325-2_1_2_load_181 | 100 | 0.0010323 | 0.00025871 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2325-2_1_2_load_182 | 101 | 0.0011369 | 0.00028492 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2325-2_1_2_load_186 | 103 | 0.00079391 | 0.00019897 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2325-2_1_2_load_232 | 104 | 0.0034465 | 0.00086379 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2325-2_1_2_load_199 | 105 | 0.0010905 | 0.00027332 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2325-2_1_2_load_200 | 106 | 0.0010902 | 0.00027324 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2325-2_1_2_load_208 | 107 | 0.0013519 | 0.00033882 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2325-2_1_2_load_209 | 108 | 0.0012297 | 0.00030819 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2325-2_1_2_load_212 | 109 | 0.0010969 | 0.00027491 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2325-2_1_2_load_213 | 110 | 0.00087022 | 0.0002181 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2325-2_1_2_load_214 | 111 | 0.0023015 | 0.00057681 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2325-2_1_2_load_248 | 112 | 0.00021016 | 5.2672e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2325-2_1_2_load_223 | 113 | 0.0010155 | 0.00025452 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2325-2_1_2_load_225 | 114 | 0.0013626 | 0.00034151 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2325-2_1_2_load_227 | 115 | 0.0013386 | 0.00033549 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2325-2_1_2_load_249 | 116 | 0.0013126 | 0.00032898 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2325-2_1_2_load_268 | 117 | 0.00073243 | 0.00018356 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2325-2_1_2_load_252 | 118 | 0.00078709 | 0.00019726 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2325-2_1_2_load_266 | 119 | 0.00054618 | 0.00013689 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2325-2_1_2_load_267 | 120 | 0.0020067 | 0.00050293 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2325-2_1_2_load_270 | 121 | 0.0015948 | 0.00039968 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2325-2_1_2_load_272 | 122 | 0.0016615 | 0.00041642 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 115 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-2_1_2_line_0 |  | 0 | 1 | 0.021237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-2_1_2_line_1 |  | 0 | 2 | 0.0057219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-2_1_2_line_2 |  | 1 | 3 | 0.0039308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-2_1_2_line_3 |  | 2 | 4 | 0.02469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-2_1_2_line_4 |  | 3 | 5 | 0.1008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-2_1_2_line_5 |  | 3 | 6 | 0.016601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-2_1_2_line_6 |  | 4 | 7 | 0.0067627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-2_1_2_line_7 |  | 5 | 8 | 0.01745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-2_1_2_line_8 |  | 6 | 9 | 0.058238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-2_1_2_line_9 |  | 7 | 23 | 0.032752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-2_1_2_line_10 |  | 8 | 22 | 0.013761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-2_1_2_line_11 |  | 9 | 19 | 0.012054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-2_1_2_line_12 |  | 9 | 20 | 0.075408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2325-2_1_2_line_13 |  | 10 | 11 | 0.0025004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-2_1_2_line_14 |  | 10 | 12 | 0.043978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-2_1_2_line_15 |  | 12 | 13 | 0.073849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-2_1_2_line_16 |  | 12 | 14 | 0.023936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-2_1_2_line_17 |  | 12 | 15 | 0.028168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-2_1_2_line_18 |  | 13 | 16 | 0.11726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-2_1_2_line_19 |  | 13 | 17 | 0.13235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-2_1_2_line_20 |  | 14 | 18 | 0.12686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-2_1_2_line_21 |  | 17 | 33 | 0.048558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-2_1_2_line_22 |  | 17 | 27 | 0.13659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-2_1_2_line_23 |  | 19 | 21 | 0.0064728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-2_1_2_line_24 |  | 20 | 115 | 0.0047476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2325-2_1_2_line_25 |  | 20 | 114 | 0.0041055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-2_1_2_line_26 |  | 21 | 87 | 0.0089439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-2_1_2_line_27 |  | 22 | 121 | 0.011841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-2_1_2_line_28 |  | 23 | 24 | 0.034922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-2_1_2_line_29 |  | 24 | 25 | 0.022778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-2_1_2_line_30 |  | 25 | 26 | 0.018845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-2_1_2_line_31 |  | 26 | 46 | 0.017559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-2_1_2_line_32 |  | 27 | 28 | 0.055415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-2_1_2_line_33 |  | 28 | 29 | 0.023499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-2_1_2_line_34 |  | 29 | 30 | 0.010542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-2_1_2_line_35 |  | 30 | 35 | 0.044686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-2_1_2_line_36 |  | 31 | 32 | 0.0097797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-2_1_2_line_37 |  | 31 | 33 | 0.15381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-2_1_2_line_38 |  | 32 | 34 | 7.466e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-2_1_2_line_39 |  | 34 | 95 | 0.11395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-2_1_2_line_40 |  | 35 | 48 | 0.012863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-2_1_2_line_41 |  | 36 | 37 | 0.022572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-2_1_2_line_42 |  | 36 | 38 | 0.045622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-2_1_2_line_43 |  | 37 | 39 | 0.0012108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-2_1_2_line_44 |  | 38 | 40 | 0.008424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-2_1_2_line_45 |  | 38 | 41 | 0.093255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-2_1_2_line_46 |  | 39 | 42 | 0.022663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2325-2_1_2_line_47 |  | 40 | 43 | 0.024766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2325-2_1_2_line_48 |  | 40 | 44 | 0.0092413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2325-2_1_2_line_49 |  | 41 | 45 | 0.043686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-2_1_2_line_50 |  | 42 | 46 | 0.049873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2325-2_1_2_line_51 |  | 44 | 47 | 0.02199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2325-2_1_2_line_52 |  | 46 | 89 | 0.0086704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2325-2_1_2_line_53 |  | 47 | 122 | 0.0022019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2325-2_1_2_line_54 |  | 48 | 64 | 0.13129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2325-2_1_2_line_55 |  | 49 | 50 | 0.013017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2325-2_1_2_line_56 |  | 49 | 51 | 0.012499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2325-2_1_2_line_57 |  | 50 | 52 | 0.016187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2325-2_1_2_line_58 |  | 50 | 53 | 0.013417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2325-2_1_2_line_59 |  | 51 | 54 | 0.039121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2325-2_1_2_line_60 |  | 52 | 55 | 0.019561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2325-2_1_2_line_61 |  | 53 | 56 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2325-2_1_2_line_62 |  | 54 | 57 | 0.018136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2325-2_1_2_line_63 |  | 56 | 58 | 0.017576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2325-2_1_2_line_64 |  | 57 | 93 | 0.0060752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2325-2_1_2_line_65 |  | 58 | 105 | 0.019893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-2_1_2_line_66 |  | 59 | 60 | 0.032064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2325-2_1_2_line_67 |  | 59 | 61 | 0.039723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2325-2_1_2_line_68 |  | 60 | 62 | 0.0079712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2325-2_1_2_line_69 |  | 61 | 63 | 0.029429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2325-2_1_2_line_70 |  | 62 | 64 | 0.078863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2325-2_1_2_line_71 |  | 63 | 65 | 0.046006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2325-2_1_2_line_72 |  | 63 | 66 | 0.080348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2325-2_1_2_line_73 |  | 64 | 67 | 0.11028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2325-2_1_2_line_74 |  | 65 | 68 | 0.020881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2325-2_1_2_line_75 |  | 66 | 118 | 0.01849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2325-2_1_2_line_76 |  | 66 | 119 | 0.1096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2325-2_1_2_line_77 |  | 67 | 94 | 0.046275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2325-2_1_2_line_78 |  | 67 | 75 | 0.011022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2325-2_1_2_line_79 |  | 68 | 86 | 0.0023302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2325-2_1_2_line_80 |  | 69 | 70 | 0.0047281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2325-2_1_2_line_81 |  | 69 | 71 | 0.017298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2325-2_1_2_line_82 |  | 70 | 72 | 0.012826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2325-2_1_2_line_83 |  | 71 | 73 | 0.020998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2325-2_1_2_line_84 |  | 72 | 74 | 0.034925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2325-2_1_2_line_85 |  | 73 | 75 | 0.11456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2325-2_1_2_line_86 |  | 74 | 78 | 0.013959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2325-2_1_2_line_87 |  | 76 | 77 | 0.048251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2325-2_1_2_line_88 |  | 77 | 109 | 4.2272e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2325-2_1_2_line_89 |  | 78 | 79 | 0.0031572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2325-2_1_2_line_90 |  | 79 | 80 | 0.022602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2325-2_1_2_line_91 |  | 80 | 81 | 0.038821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2325-2_1_2_line_92 |  | 80 | 82 | 0.012871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2325-2_1_2_line_93 |  | 81 | 83 | 0.02302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2325-2_1_2_line_94 |  | 82 | 84 | 0.00055606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2325-2_1_2_line_95 |  | 83 | 97 | 0.017149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2325-2_1_2_line_96 |  | 84 | 113 | 0.077026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2325-2_1_2_line_97 |  | 85 | 86 | 0.0046457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2325-2_1_2_line_98 |  | 87 | 109 | 0.0055841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2325-2_1_2_line_99 |  | 88 | 89 | 0.0014928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2325-2_1_2_line_100 |  | 88 | 90 | 0.021893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2325-2_1_2_line_101 |  | 90 | 91 | 0.045326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2325-2_1_2_line_102 |  | 90 | 92 | 0.096545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2325-2_1_2_line_103 |  | 92 | 93 | 0.0249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2325-2_1_2_line_104 |  | 95 | 96 | 0.11607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2325-2_1_2_line_105 |  | 97 | 98 | 0.010343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2325-2_1_2_line_106 |  | 98 | 99 | 0.036684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2325-2_1_2_line_107 |  | 99 | 104 | 0.049282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2325-2_1_2_line_108 |  | 100 | 101 | 0.060988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2325-2_1_2_line_109 |  | 101 | 102 | 0.010574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2325-2_1_2_line_110 |  | 102 | 103 | 0.018678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2325-2_1_2_line_111 |  | 103 | 104 | 0.058762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2325-2_1_2_line_112 |  | 105 | 106 | 1.1194e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2325-2_1_2_line_113 |  | 106 | 107 | 0.013451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2325-2_1_2_line_114 |  | 107 | 108 | 0.0038874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2325-2_1_2_line_115 |  | 110 | 111 | 0.027694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2325-2_1_2_line_116 |  | 111 | 112 | 0.024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2325-2_1_2_line_117 |  | 112 | 116 | 0.02501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2325-2_1_2_line_118 |  | 113 | 114 | 0.0038666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2325-2_1_2_line_119 |  | 116 | 117 | 0.11106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2325-2_1_2_line_120 |  | 117 | 120 | 0.00053953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2325-2_1_2_line_121 |  | 119 | 120 | 0.015647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-2_1_2_trafo_227 | 0.63 MVA 20/0.4 kV | 123 | 115 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2559255.8914 | 1153368.3004 | 2559276.5906 | 1153363.5511
1 | 2559250.3144 | 1153369.58 | 2559255.8914 | 1153368.3004
2 | 2559280.4219 | 1153362.672 | 2559276.5906 | 1153363.5511
3 | 2559250.3144 | 1153369.58 | 2559230.5444 | 1153374.1162 | 2559226.1791 | 1153374.7187
4 | 2559279.5641 | 1153262.2041 | 2559278.0971 | 1153353.6165 | 2559280.4219 | 1153362.672
5 | 2559280.4219 | 1153362.672 | 2559296.4979 | 1153358.5287
6 | 2559219.48 | 1153375.6433 | 2559226.1791 | 1153374.7187
7 | 2559279.5641 | 1153262.2041 | 2559280.4411 | 1153244.7765
8 | 2559296.4979 | 1153358.5287 | 2559322.8148 | 1153351.7459 | 2559337.409 | 1153351.925 | 2559353.4991 | 1153355.4231
9 | 2559219.48 | 1153375.6433 | 2559197.8445 | 1153378.6294 | 2559189.2335 | 1153379.3883 | 2559187.0475 | 1153379.9874
10 | 2559281.1327 | 1153231.0331 | 2559280.4411 | 1153244.7765
11 | 2559365.278 | 1153357.9839 | 2559353.4991 | 1153355.4231
12 | 2559383.7315 | 1153424.5054 | 2559353.4991 | 1153355.4231
13 | 2560132.8265 | 1153421.1193 | 2560134.4663 | 1153419.2316
14 | 2560111.0391 | 1153458.5595 | 2560119.5692 | 1153436.3804 | 2560132.8265 | 1153421.1193
15 | 2560111.0391 | 1153458.5595 | 2560105.376 | 1153458.4081 | 2560097.212 | 1153459.474 | 2560089.8361 | 1153462.5134 | 2560082.3338 | 1153467.3102 | 2560076.7469 | 1153471.694 | 2560071.3205 | 1153478.3001 | 2560055.4505 | 1153500.806
16 | 2560111.0391 | 1153458.5595 | 2560092.9853 | 1153442.8433
17 | 2560111.0391 | 1153458.5595 | 2560118.6224 | 1153462.4778 | 2560135.1753 | 1153473.0332
18 | 2560055.4505 | 1153500.806 | 2560051.2344 | 1153484.0588 | 2560046.3094 | 1153461.0798 | 2560036.4628 | 1153447.9497 | 2560013.488 | 1153435.8408 | 2560001.7889 | 1153426.8141 | 2559998.1017 | 1153413.4763 | 2559998.1799 | 1153407.9818
19 | 2560055.4505 | 1153500.806 | 2559946.8159 | 1153576.4006
20 | 2560021.1954 | 1153350.0142 | 2560025.6971 | 1153353.2395 | 2560040.7638 | 1153357.5526 | 2560051.7631 | 1153361.7149 | 2560058.5501 | 1153370.4854 | 2560060.3957 | 1153382.646 | 2560061.7276 | 1153396.0329 | 2560066.2324 | 1153408.8873 | 2560074.9815 | 1153420.813 | 2560086.2368 | 1153436.9687 | 2560092.9853 | 1153442.8433
21 | 2559948.0857 | 1153622.8056 | 2559952.7423 | 1153607.8002 | 2559945.2818 | 1153587.773 | 2559946.8159 | 1153576.4006
22 | 2559946.8159 | 1153576.4006 | 2559823.8615 | 1153516.9184
23 | 2559365.278 | 1153357.9839 | 2559371.5758 | 1153359.4787
24 | 2559379.3409 | 1153426.3117 | 2559383.7315 | 1153424.5054
25 | 2559387.5282 | 1153422.9433 | 2559383.7315 | 1153424.5054
26 | 2559380.278 | 1153361.5441 | 2559371.5758 | 1153359.4787
27 | 2559281.1327 | 1153231.0331 | 2559275.3724 | 1153221.1115 | 2559275.0272 | 1153220.9821
28 | 2559187.0475 | 1153379.9874 | 2559179.8753 | 1153381.9531 | 2559171.2247 | 1153388.1707 | 2559164.0066 | 1153396.3128 | 2559161.2316 | 1153401.5777
29 | 2559151.3538 | 1153422.0898 | 2559156.6441 | 1153410.2811 | 2559161.2316 | 1153401.5777
30 | 2559151.3538 | 1153422.0898 | 2559164.4452 | 1153435.6452
31 | 2559176.6434 | 1153448.2758 | 2559164.4452 | 1153435.6452
32 | 2559838.9517 | 1153463.5971 | 2559823.8615 | 1153516.9184
33 | 2559838.9517 | 1153463.5971 | 2559840.2486 | 1153440.1338
34 | 2559839.9292 | 1153429.651 | 2559840.5874 | 1153434.0044 | 2559840.2486 | 1153440.1338
35 | 2559839.9292 | 1153429.651 | 2559824.8191 | 1153437.2004 | 2559816.3334 | 1153439.4805 | 2559800.2108 | 1153435.5753 | 2559797.9386 | 1153434.7439
36 | 2559832.6402 | 1153731.29 | 2559832.3136 | 1153730.5671 | 2559830.3599 | 1153721.7956
37 | 2559830.3599 | 1153721.7956 | 2559948.0857 | 1153622.8056
38 | 2559832.6402 | 1153731.29 | 2559832.6406 | 1153731.2907
39 | 2559852.0509 | 1153840.3136 | 2559853.9857 | 1153835.954 | 2559854.6835 | 1153832.4587 | 2559855.6847 | 1153805.4937 | 2559852.3889 | 1153774.989 | 2559832.6406 | 1153731.2907
40 | 2559785.859 | 1153430.3242 | 2559797.9386 | 1153434.7439
41 | 2559201.3536 | 1153538.9866 | 2559201.6812 | 1153530.0143 | 2559201.157 | 1153516.4306
42 | 2559199.689 | 1153584.578 | 2559201.3536 | 1153538.9866
43 | 2559201.157 | 1153516.4306 | 2559201.1103 | 1153515.2206
44 | 2559199.689 | 1153584.578 | 2559208.0917 | 1153583.6983
45 | 2559199.689 | 1153584.578 | 2559197.1224 | 1153655.1094 | 2559196.3249 | 1153677.7486
46 | 2559198.1635 | 1153492.8755 | 2559200.6197 | 1153502.5074 | 2559201.1103 | 1153515.2206
47 | 2559208.0917 | 1153583.6983 | 2559216.2725 | 1153560.3196
48 | 2559208.0917 | 1153583.6983 | 2559210.8659 | 1153592.2838 | 2559210.8659 | 1153592.5025
49 | 2559196.3249 | 1153677.7486 | 2559217.4604 | 1153679.8617 | 2559239.5474 | 1153675.2206
50 | 2559176.6434 | 1153448.2758 | 2559194.9286 | 1153480.1901 | 2559198.1635 | 1153492.8755
51 | 2559210.8659 | 1153592.5025 | 2559210.8631 | 1153606.5467 | 2559210.4283 | 1153614.4807
52 | 2559176.6434 | 1153448.2758 | 2559183.3319 | 1153453.793
53 | 2559210.4283 | 1153614.4807 | 2559210.3078 | 1153616.6792
54 | 2559677.4765 | 1153356.2354 | 2559785.859 | 1153430.3242
55 | 2559298.5651 | 1153621.5484 | 2559286.6953 | 1153626.8918
56 | 2559286.6953 | 1153626.8918 | 2559275.2976 | 1153632.0226
57 | 2559298.5651 | 1153621.5484 | 2559307.4809 | 1153627.3243 | 2559309.9073 | 1153632.3306
58 | 2559298.5651 | 1153621.5484 | 2559310.9612 | 1153616.4159
59 | 2559259.7605 | 1153596.7304 | 2559267.8223 | 1153622.5796 | 2559275.2976 | 1153632.0226 | 2559275.2976 | 1153632.0226
60 | 2559322.7506 | 1153641.4349 | 2559315.005 | 1153642.848 | 2559309.9073 | 1153632.3306
61 | 2559310.9612 | 1153616.4159 | 2559325.3423 | 1153610.4614
62 | 2559259.7605 | 1153596.7304 | 2559254.3608 | 1153579.4168
63 | 2559317.8908 | 1153594.5434 | 2559325.3423 | 1153610.4614 | 2559325.3423 | 1153610.4614
64 | 2559252.552 | 1153573.6171 | 2559254.3608 | 1153579.4168
65 | 2559317.8908 | 1153594.5434 | 2559313.7586 | 1153585.716 | 2559310.109 | 1153576.2492
66 | 2559760.5095 | 1153299.3711 | 2559748.6266 | 1153300.0624 | 2559728.4714 | 1153299.5763
67 | 2559798.449 | 1153289.3233 | 2559787.1626 | 1153295.0462 | 2559769.1425 | 1153298.8688 | 2559760.5095 | 1153299.3711
68 | 2559728.4714 | 1153299.5763 | 2559720.5026 | 1153299.3841
69 | 2559798.449 | 1153289.3233 | 2559810.067 | 1153280.4299 | 2559822.9771 | 1153273.1972
70 | 2559677.4765 | 1153356.2354 | 2559680.2923 | 1153347.6117 | 2559683.211 | 1153334.3742 | 2559684.3863 | 1153324.3056 | 2559690.3279 | 1153313.3379 | 2559703.0068 | 1153304.7818 | 2559720.1339 | 1153299.3752 | 2559720.5026 | 1153299.3841
71 | 2559866.7108 | 1153264.389 | 2559858.8544 | 1153261.7386 | 2559839.3524 | 1153267.7164 | 2559825.049 | 1153272.0365 | 2559822.9771 | 1153273.1972
72 | 2559822.9771 | 1153273.1972 | 2559770.2599 | 1153212.5616
73 | 2559622.3149 | 1153449.6422 | 2559630.5234 | 1153444.9513 | 2559639.4745 | 1153434.3079 | 2559647.6902 | 1153419.2673 | 2559675.0974 | 1153363.5213 | 2559677.4765 | 1153356.2354
74 | 2559866.7108 | 1153264.389 | 2559872.7808 | 1153266.4368 | 2559885.7444 | 1153272.8757 | 2559885.7444 | 1153272.8757
75 | 2559783.7944 | 1153199.9645 | 2559770.2599 | 1153212.5616 | 2559770.2599 | 1153212.5616
76 | 2559770.2599 | 1153212.5616 | 2559687.151 | 1153141.119
77 | 2559622.3149 | 1153449.6422 | 2559640.8879 | 1153481.3559 | 2559650.3837 | 1153480.6356
78 | 2559612.723 | 1153455.1206 | 2559622.3149 | 1153449.6422
79 | 2559887.3038 | 1153274.6072 | 2559885.7444 | 1153272.8757
80 | 2559509.3943 | 1153448.5906 | 2559512.1802 | 1153444.7704
81 | 2559518.4631 | 1153429.2751 | 2559518.3241 | 1153432.5444 | 2559516.9688 | 1153438.6456 | 2559513.3701 | 1153443.1388 | 2559512.1802 | 1153444.7704
82 | 2559509.3943 | 1153448.5906 | 2559509.3943 | 1153448.5906 | 2559502.3846 | 1153452.4176 | 2559497.9419 | 1153454.3364
83 | 2559519.3729 | 1153408.3027 | 2559518.4631 | 1153429.2751
84 | 2559465.8792 | 1153468.1844 | 2559497.9419 | 1153454.3364
85 | 2559519.3729 | 1153408.3027 | 2559540.1661 | 1153407.3288 | 2559552.7635 | 1153407.2328 | 2559567.3874 | 1153409.5689 | 2559581.4003 | 1153415.7333 | 2559591.0341 | 1153422.1718 | 2559597.2919 | 1153428.5886 | 2559602.4727 | 1153436.8691 | 2559612.723 | 1153455.1206
86 | 2559453.064 | 1153473.7193 | 2559465.8792 | 1153468.1844
87 | 2559419.9306 | 1153396.8567 | 2559385.7153 | 1153362.8346
88 | 2559385.7112 | 1153362.8337 | 2559385.7153 | 1153362.8346
89 | 2559450.1656 | 1153474.9711 | 2559453.064 | 1153473.7193
90 | 2559433.3774 | 1153489.5467 | 2559439.462 | 1153481.6682 | 2559448.6509 | 1153475.6253 | 2559450.1656 | 1153474.9711
91 | 2559433.3774 | 1153489.5467 | 2559430.4522 | 1153500.5943 | 2559431.4599 | 1153512.338 | 2559437.1885 | 1153526.8546
92 | 2559433.3774 | 1153489.5467 | 2559427.0005 | 1153482.5528 | 2559426.168 | 1153479.2498
93 | 2559445.6385 | 1153548.2674 | 2559437.1885 | 1153526.8546
94 | 2559426.0321 | 1153478.7106 | 2559426.168 | 1153479.2498
95 | 2559451.9336 | 1153564.2197 | 2559445.6385 | 1153548.2674
96 | 2559426.0321 | 1153478.7106 | 2559421.143 | 1153459.3138 | 2559414.2399 | 1153442.5852 | 2559400.7664 | 1153417.4967 | 2559391.1039 | 1153421.4721
97 | 2559887.3038 | 1153274.6072 | 2559890.4128 | 1153278.0593
98 | 2559380.278 | 1153361.5441 | 2559385.7112 | 1153362.8337
99 | 2559183.3319 | 1153453.793 | 2559184.4834 | 1153454.7429
100 | 2559201.3718 | 1153468.6738 | 2559184.4834 | 1153454.7429
101 | 2559201.3718 | 1153468.6738 | 2559207.63 | 1153467.1861 | 2559234.3685 | 1153495.5191
102 | 2559201.3718 | 1153468.6738 | 2559216.5664 | 1153492.8942 | 2559223.2394 | 1153526.5105 | 2559238.8666 | 1153535.3868 | 2559244.2168 | 1153550.1563
103 | 2559252.552 | 1153573.6171 | 2559251.5407 | 1153570.3743 | 2559244.2168 | 1153550.1563
104 | 2559852.0509 | 1153840.3136 | 2559824.7366 | 1153815.8393 | 2559795.8749 | 1153792.8984 | 2559783.3478 | 1153781.6098 | 2559772.257 | 1153769.4223 | 2559766.7352 | 1153762.0795
105 | 2559455.7304 | 1153573.8409 | 2559451.9336 | 1153564.2197
106 | 2559455.7304 | 1153573.8409 | 2559465.1496 | 1153597.7098 | 2559468.1265 | 1153608.3242
107 | 2559468.1265 | 1153608.3242 | 2559468.7501 | 1153610.5477 | 2559468.527 | 1153621.8105 | 2559467.0969 | 1153631.5919 | 2559459.311 | 1153656.2122
108 | 2559460.8821 | 1153800.5899 | 2559457.941 | 1153782.242 | 2559446.9488 | 1153741.2853
109 | 2559444.6215 | 1153730.9723 | 2559446.4273 | 1153739.3421 | 2559446.9488 | 1153741.2853
110 | 2559444.6215 | 1153730.9723 | 2559442.1664 | 1153719.6052 | 2559443.3118 | 1153712.65
111 | 2559459.311 | 1153656.2122 | 2559445.3207 | 1153700.4519 | 2559443.3118 | 1153712.65
112 | 2559310.1086 | 1153576.2481 | 2559310.109 | 1153576.2492
113 | 2559310.1086 | 1153576.2481 | 2559305.2701 | 1153563.6971
114 | 2559303.8718 | 1153560.0699 | 2559305.2701 | 1153563.6971
115 | 2559568.593 | 1153280.6459 | 2559575.2666 | 1153277.3259 | 2559593.4608 | 1153268.4574
116 | 2559593.4608 | 1153268.4574 | 2559615.3482 | 1153257.7886
117 | 2559615.3482 | 1153257.7886 | 2559633.1504 | 1153249.1111 | 2559637.5687 | 1153246.3587
118 | 2559387.5282 | 1153422.9433 | 2559391.1039 | 1153421.4721
119 | 2559637.5687 | 1153246.3587 | 2559670.9806 | 1153140.4392
120 | 2559670.9806 | 1153140.4392 | 2559671.5198 | 1153140.42 | 2559671.5198 | 1153140.42
121 | 2559687.151 | 1153141.119 | 2559671.5198 | 1153140.42

## bus_geodata
| x | y | coords
0 | 2559255.8914 | 1153368.3004
1 | 2559276.5906 | 1153363.5511
2 | 2559250.3144 | 1153369.58
3 | 2559280.4219 | 1153362.672
4 | 2559226.1791 | 1153374.7187
5 | 2559279.5641 | 1153262.2041
6 | 2559296.4979 | 1153358.5287
7 | 2559219.48 | 1153375.6433
8 | 2559280.4411 | 1153244.7765
9 | 2559353.4991 | 1153355.4231
10 | 2560132.8265 | 1153421.1193
11 | 2560134.4663 | 1153419.2316
12 | 2560111.0391 | 1153458.5595
13 | 2560055.4505 | 1153500.806
14 | 2560092.9853 | 1153442.8433
15 | 2560135.1753 | 1153473.0332
16 | 2559998.1799 | 1153407.9818
17 | 2559946.8159 | 1153576.4006
18 | 2560021.1955 | 1153350.0142
19 | 2559365.278 | 1153357.9839
20 | 2559383.7315 | 1153424.5054
21 | 2559371.5758 | 1153359.4787
22 | 2559281.1327 | 1153231.0331
23 | 2559187.0475 | 1153379.9874
24 | 2559161.2316 | 1153401.5777
25 | 2559151.3538 | 1153422.0898
26 | 2559164.4452 | 1153435.6452
27 | 2559823.8615 | 1153516.9184
28 | 2559838.9517 | 1153463.5971
29 | 2559840.2486 | 1153440.1338
30 | 2559839.9292 | 1153429.651
31 | 2559830.3599 | 1153721.7956
32 | 2559832.6402 | 1153731.29
33 | 2559948.0857 | 1153622.8056
34 | 2559832.6406 | 1153731.2907
35 | 2559797.9386 | 1153434.7439
36 | 2559201.3536 | 1153538.9866
37 | 2559201.157 | 1153516.4306
38 | 2559199.689 | 1153584.578
39 | 2559201.1103 | 1153515.2206
40 | 2559208.0917 | 1153583.6983
41 | 2559196.3249 | 1153677.7486
42 | 2559198.1635 | 1153492.8755
43 | 2559216.2725 | 1153560.3196
44 | 2559210.8659 | 1153592.5025
45 | 2559239.5474 | 1153675.2206
46 | 2559176.6434 | 1153448.2758
47 | 2559210.4283 | 1153614.4807
48 | 2559785.859 | 1153430.3242
49 | 2559286.6953 | 1153626.8918
50 | 2559298.5651 | 1153621.5484
51 | 2559275.2976 | 1153632.0226
52 | 2559309.9073 | 1153632.3306
53 | 2559310.9612 | 1153616.4159
54 | 2559259.7605 | 1153596.7304
55 | 2559322.7506 | 1153641.4349
56 | 2559325.3423 | 1153610.4614
57 | 2559254.3608 | 1153579.4168
58 | 2559317.8908 | 1153594.5434
59 | 2559760.5095 | 1153299.3711
60 | 2559728.4714 | 1153299.5763
61 | 2559798.449 | 1153289.3233
62 | 2559720.5026 | 1153299.3841
63 | 2559822.9771 | 1153273.1972
64 | 2559677.4765 | 1153356.2354
65 | 2559866.7108 | 1153264.389
66 | 2559770.2599 | 1153212.5616
67 | 2559622.3149 | 1153449.6422
68 | 2559885.7444 | 1153272.8758
69 | 2559512.1802 | 1153444.7704
70 | 2559509.3943 | 1153448.5906
71 | 2559518.4631 | 1153429.2751
72 | 2559497.9419 | 1153454.3364
73 | 2559519.3729 | 1153408.3027
74 | 2559465.8792 | 1153468.1844
75 | 2559612.723 | 1153455.1206
76 | 2559419.9306 | 1153396.8567
77 | 2559385.7153 | 1153362.8346
78 | 2559453.064 | 1153473.7193
79 | 2559450.1656 | 1153474.9711
80 | 2559433.3774 | 1153489.5467
81 | 2559437.1885 | 1153526.8546
82 | 2559426.168 | 1153479.2498
83 | 2559445.6385 | 1153548.2674
84 | 2559426.0321 | 1153478.7106
85 | 2559890.4128 | 1153278.0593
86 | 2559887.3038 | 1153274.6072
87 | 2559380.278 | 1153361.5441
88 | 2559184.4834 | 1153454.7429
89 | 2559183.3319 | 1153453.793
90 | 2559201.3718 | 1153468.6738
91 | 2559234.3685 | 1153495.5191
92 | 2559244.2168 | 1153550.1563
93 | 2559252.552 | 1153573.6171
94 | 2559650.3837 | 1153480.6356
95 | 2559852.0509 | 1153840.3136
96 | 2559766.7352 | 1153762.0795
97 | 2559451.9336 | 1153564.2197
98 | 2559455.7304 | 1153573.8409
99 | 2559468.1265 | 1153608.3242
100 | 2559460.8821 | 1153800.5899
101 | 2559446.9488 | 1153741.2853
102 | 2559444.6215 | 1153730.9723
103 | 2559443.3118 | 1153712.65
104 | 2559459.311 | 1153656.2122
105 | 2559310.109 | 1153576.2492
106 | 2559310.1086 | 1153576.2481
107 | 2559305.2701 | 1153563.6971
108 | 2559303.8718 | 1153560.0699
109 | 2559385.7112 | 1153362.8337
110 | 2559568.593 | 1153280.6459
111 | 2559593.4608 | 1153268.4574
112 | 2559615.3482 | 1153257.7886
113 | 2559391.1039 | 1153421.4721
114 | 2559387.5282 | 1153422.9433
115 | 2559379.3409 | 1153426.3117
116 | 2559637.5687 | 1153246.3587
117 | 2559670.9806 | 1153140.4392
118 | 2559783.7944 | 1153199.9645
119 | 2559687.151 | 1153141.119
120 | 2559671.5198 | 1153140.42
121 | 2559275.0272 | 1153220.9821
122 | 2559210.3078 | 1153616.6792
123 | 2559379.3409 | 1153426.3117

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98652 | -0.25741 | 0.0073159 | 0.0018335
1 | 0.98825 | -0.22413 | 0.0074856 | 0.0018761
2 | 0.9861 | -0.26565 | 0.0033558 | 0.00084104
3 | 0.98859 | -0.21745 | 0 | 0
4 | 0.98433 | -0.29978 | 0.0095497 | 0.0023934
5 | 0.98811 | -0.22683 | 0 | 0
6 | 0.99013 | -0.18778 | 0.0039117 | 0.00098038
7 | 0.98391 | -0.30799 | 0.011343 | 0.0028429
8 | 0.98803 | -0.22845 | 0.0036156 | 0.00090616
9 | 0.99575 | -0.080419 | 0.0021708 | 0.00054405
10 | 0.98664 | -0.25842 | 0.00054881 | 0.00013755
11 | 0.98664 | -0.25843 | 9.3825e-05 | 2.3515e-05
12 | 0.98666 | -0.25792 | 0 | 0
13 | 0.98677 | -0.25578 | 0 | 0
14 | 0.98664 | -0.25829 | 0.00047303 | 0.00011855
15 | 0.98666 | -0.25798 | 0.00011482 | 2.8776e-05
16 | 0.98673 | -0.25658 | 0.00037883 | 9.4944e-05
17 | 0.98701 | -0.25102 | 0.00062258 | 0.00015603
18 | 0.9866 | -0.25916 | 0.00038134 | 9.5572e-05
19 | 0.9957 | -0.081501 | 0 | 0
20 | 0.99964 | -0.0067653 | 0.0010648 | 0.00026687
21 | 0.99567 | -0.082082 | 0.0013034 | 0.00032667
22 | 0.98801 | -0.22884 | 0 | 0
23 | 0.9822 | -0.34113 | 0.000623 | 0.00015614
24 | 0.9804 | -0.3762 | 0.0015528 | 0.00038916
25 | 0.97926 | -0.3985 | 0 | 0
26 | 0.97832 | -0.41698 | 0.0042949 | 0.0010764
27 | 0.98756 | -0.24023 | 0.00029684 | 7.4395e-05
28 | 0.9878 | -0.23556 | 0 | 0
29 | 0.9879 | -0.23358 | 0.00037555 | 9.4123e-05
30 | 0.98795 | -0.23262 | 0 | 0
31 | 0.98671 | -0.25701 | 0.00011627 | 2.9139e-05
32 | 0.9867 | -0.25727 | 0.00068179 | 0.00017087
33 | 0.98693 | -0.25257 | 0.00016965 | 4.2517e-05
34 | 0.9867 | -0.25727 | 0.0006809 | 0.00017065
35 | 0.98816 | -0.22855 | 0.00033123 | 8.3014e-05
36 | 0.97611 | -0.46044 | 0.0054452 | 0.0013647
37 | 0.97638 | -0.45504 | 0.0010474 | 0.00026251
38 | 0.97578 | -0.46682 | 0 | 0
39 | 0.9764 | -0.45473 | 0.0014344 | 0.00035949
40 | 0.97574 | -0.46767 | 0 | 0
41 | 0.9756 | -0.47049 | 0 | 0
42 | 0.97673 | -0.44828 | 0.0013627 | 0.00034152
43 | 0.9757 | -0.46843 | 0.0016873 | 0.00042288
44 | 0.97571 | -0.46831 | 0.0010739 | 0.00026913
45 | 0.97551 | -0.47221 | 0.002149 | 0.00053859
46 | 0.97751 | -0.43287 | 0 | 0
47 | 0.97565 | -0.4694 | 0.0010595 | 0.00026555
48 | 0.98822 | -0.2273 | 0.00018391 | 4.6092e-05
49 | 0.97403 | -0.50134 | 0.002078 | 0.00052079
50 | 0.97392 | -0.50347 | 0 | 0
51 | 0.97416 | -0.49882 | 0.0010972 | 0.00027499
52 | 0.97389 | -0.50409 | 0.001489 | 0.00037317
53 | 0.97384 | -0.50516 | 0.00075191 | 0.00018845
54 | 0.9746 | -0.49014 | 0.0010341 | 0.00025917
55 | 0.97388 | -0.5043 | 0.00058933 | 0.0001477
56 | 0.97375 | -0.5069 | 0.00055089 | 0.00013807
57 | 0.97482 | -0.48578 | 0.0013098 | 0.00032827
58 | 0.97366 | -0.50868 | 0.00076025 | 0.00019054
59 | 0.98775 | -0.23632 | 0.00017847 | 4.4729e-05
60 | 0.98805 | -0.23048 | 0.00026027 | 6.5229e-05
61 | 0.98739 | -0.24344 | 0 | 0
62 | 0.98813 | -0.22899 | 7.9656e-05 | 1.9964e-05
63 | 0.98712 | -0.24872 | 0.00043283 | 0.00010848
64 | 0.98889 | -0.21416 | 0.00024923 | 6.2463e-05
65 | 0.98709 | -0.24925 | 0.00026803 | 6.7175e-05
66 | 0.98645 | -0.26158 | 0.00016806 | 4.212e-05
67 | 0.99055 | -0.18194 | 0 | 0
68 | 0.98708 | -0.24938 | 0.00022398 | 5.6135e-05
69 | 0.99336 | -0.12742 | 0.00062243 | 0.000156
70 | 0.99345 | -0.1258 | 0.001578 | 0.00039549
71 | 0.99307 | -0.13316 | 0 | 0
72 | 0.99369 | -0.12104 | 0.00062401 | 0.00015639
73 | 0.99271 | -0.14013 | 0 | 0
74 | 0.99438 | -0.10773 | 0.0019475 | 0.0004881
75 | 0.99074 | -0.17826 | 0 | 0
76 | 0.99559 | -0.083615 | 0.00075775 | 0.00018991
77 | 0.99562 | -0.082972 | 0.0011111 | 0.00027846
78 | 0.99469 | -0.10194 | 0.0014563 | 0.00036498
79 | 0.99476 | -0.10055 | 0.0028657 | 0.00071821
80 | 0.99533 | -0.089452 | 0 | 0
81 | 0.99477 | -0.1003 | 0.0028527 | 0.00071496
82 | 0.99585 | -0.079549 | 0.0024522 | 0.00061457
83 | 0.9945 | -0.10558 | 0.00098347 | 0.00024648
84 | 0.99587 | -0.079098 | 0.0022376 | 0.0005608
85 | 0.98708 | -0.2494 | 7.7397e-05 | 1.9398e-05
86 | 0.98708 | -0.24939 | 7.082e-05 | 1.7749e-05
87 | 0.99564 | -0.08268 | 0.00083464 | 0.00020918
88 | 0.97721 | -0.43865 | 0.0020379 | 0.00051074
89 | 0.97725 | -0.43804 | 0.010104 | 0.0025324
90 | 0.9768 | -0.44687 | 0 | 0
91 | 0.97665 | -0.44972 | 0.0034408 | 0.00086235
92 | 0.97526 | -0.47709 | 0.0015935 | 0.00039937
93 | 0.9749 | -0.48417 | 0.0010828 | 0.00027137
94 | 0.99045 | -0.18388 | 0.0023587 | 0.00059115
95 | 0.98668 | -0.25753 | 0 | 0
96 | 0.98667 | -0.25779 | 0.00012251 | 3.0704e-05
97 | 0.99431 | -0.10921 | 0.003629 | 0.00090952
98 | 0.99423 | -0.11075 | 0.0010044 | 0.00025173
99 | 0.99398 | -0.11553 | 0.00098099 | 0.00024586
100 | 0.99342 | -0.12642 | 0.0010323 | 0.00025871
101 | 0.99348 | -0.12531 | 0.0011369 | 0.00028492
102 | 0.9935 | -0.12491 | 0 | 0
103 | 0.99354 | -0.12419 | 0.00079391 | 0.00019897
104 | 0.9937 | -0.12111 | 0.0034465 | 0.00086379
105 | 0.97357 | -0.51042 | 0.0010905 | 0.00027332
106 | 0.97357 | -0.51042 | 0.0010902 | 0.00027324
107 | 0.97354 | -0.51106 | 0.0013519 | 0.00033882
108 | 0.97353 | -0.51115 | 0.0012297 | 0.00030819
109 | 0.99562 | -0.082971 | 0.0010969 | 0.00027491
110 | 0.98489 | -0.29213 | 0.00087022 | 0.0002181
111 | 0.98491 | -0.2917 | 0.0023015 | 0.00057681
112 | 0.98498 | -0.29031 | 0.00021016 | 5.2672e-05
113 | 0.99928 | -0.013743 | 0.0010155 | 0.00025452
114 | 0.99945 | -0.010405 | 0.0013626 | 0.00034151
115 | 1 | 0 | -0.16725 | -0.04234
116 | 0.98506 | -0.28879 | 0.0013126 | 0.00032898
117 | 0.98554 | -0.27942 | 0.00073243 | 0.00018356
118 | 0.98644 | -0.26185 | 0.00078709 | 0.00019726
119 | 0.98565 | -0.27728 | 0.00054618 | 0.00013689
120 | 0.98554 | -0.27937 | 0.0020067 | 0.00050293
121 | 0.98799 | -0.22918 | 0.0015948 | 0.00039968
122 | 0.97565 | -0.46947 | 0.0016615 | 0.00041642
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.088235 | -0.022335 | 0.088376 | 0.022425 | 0.00014123 | 9.0116e-05 | 0.13317 | 0.13317 | 0.13317 | 0.98652 | -0.25741 | 0.98825 | -0.22413 | 36.5847
1 | 0.080919 | 0.020501 | -0.080887 | -0.020481 | 3.2007e-05 | 2.0411e-05 | 0.12213 | 0.12213 | 0.12213 | 0.98652 | -0.25741 | 0.9861 | -0.26565 | 33.5531
2 | -0.095862 | -0.024301 | 0.095893 | 0.02432 | 3.0752e-05 | 1.9631e-05 | 0.14444 | 0.14444 | 0.14444 | 0.98825 | -0.22413 | 0.98859 | -0.21745 | 39.6811
3 | 0.077531 | 0.01964 | -0.077405 | -0.019559 | 0.0001269 | 8.0899e-05 | 0.11707 | 0.11707 | 0.11707 | 0.9861 | -0.26565 | 0.98433 | -0.29978 | 32.1619
4 | 0.0052132 | 0.0013058 | -0.0052108 | -0.0013056 | 2.3274e-06 | 1.9774e-07 | 0.0078465 | 0.007847 | 0.007847 | 0.98859 | -0.21745 | 0.98811 | -0.22683 | 2.1558
5 | -0.10111 | -0.025626 | 0.10125 | 0.025718 | 0.00014438 | 9.2187e-05 | 0.15229 | 0.15229 | 0.15229 | 0.98859 | -0.21745 | 0.99013 | -0.18778 | 41.8367
6 | 0.067855 | 0.017165 | -0.067828 | -0.017148 | 2.6713e-05 | 1.701e-05 | 0.10263 | 0.10263 | 0.10263 | 0.98433 | -0.29978 | 0.98391 | -0.30799 | 28.196
7 | 0.0052108 | 0.0013056 | -0.0052104 | -0.0013056 | 4.0293e-07 | 3.4378e-08 | 0.007847 | 0.0078471 | 0.0078471 | 0.98811 | -0.22683 | 0.98803 | -0.22845 | 2.1558
8 | -0.10516 | -0.026699 | 0.10571 | 0.027048 | 0.00054633 | 0.0003489 | 0.15816 | 0.15816 | 0.15816 | 0.99013 | -0.18778 | 0.99575 | -0.080419 | 43.4517
9 | 0.056485 | 0.014305 | -0.056395 | -0.014248 | 8.9737e-05 | 5.7017e-05 | 0.085478 | 0.085478 | 0.085478 | 0.98391 | -0.30799 | 0.9822 | -0.34113 | 23.483
10 | 0.0015948 | 0.00039939 | -0.0015948 | -0.00039955 | 2.9767e-08 | -1.5718e-07 | 0.0024017 | 0.0024018 | 0.0024018 | 0.98803 | -0.22845 | 0.98801 | -0.22884 | 0.65984
11 | 0.0051044 | 0.0012784 | -0.0051041 | -0.0012784 | 2.6298e-07 | 1.1518e-08 | 0.0076275 | 0.0076275 | 0.0076275 | 0.99575 | -0.080419 | 0.9957 | -0.081501 | 2.0955
12 | -0.11298 | -0.02887 | 0.11339 | 0.029127 | 0.00040399 | 0.00025658 | 0.16904 | 0.16903 | 0.16904 | 0.99575 | -0.080419 | 0.99964 | -0.0067653 | 23.2191
13 | 9.3825e-05 | 2.3483e-05 | -9.3825e-05 | -2.3515e-05 | 1.8767e-11 | -3.1921e-08 | 0.00014149 | 0.0001415 | 0.0001415 | 0.98664 | -0.25842 | 0.98664 | -0.25843 | 0.038875
14 | -0.00064264 | -0.00016103 | 0.00064265 | 0.00016048 | 1.5488e-08 | -5.5175e-07 | 0.00096919 | 0.00096899 | 0.00096919 | 0.98664 | -0.25842 | 0.98666 | -0.25792 | 0.26626
15 | -0.0016119 | -0.00040111 | 0.001612 | 0.00040027 | 1.6349e-07 | -8.3865e-07 | 0.0024299 | 0.0024296 | 0.0024299 | 0.98666 | -0.25792 | 0.98677 | -0.25578 | 0.66755
16 | 0.00085439 | 0.00021222 | -0.00085438 | -0.00021251 | 1.4889e-08 | -2.9617e-07 | 0.0012879 | 0.001288 | 0.001288 | 0.98666 | -0.25792 | 0.98664 | -0.25829 | 0.35384
17 | 0.00011482 | 2.8417e-05 | -0.00011482 | -2.8776e-05 | 3.165e-10 | -3.5955e-07 | 0.00017304 | 0.00017316 | 0.00017316 | 0.98666 | -0.25792 | 0.98666 | -0.25798 | 0.047572
18 | 0.00037884 | 9.3455e-05 | -0.00037883 | -9.4944e-05 | 1.4338e-08 | -1.4887e-06 | 0.00057076 | 0.00057129 | 0.00057129 | 0.98677 | -0.25578 | 0.98673 | -0.25658 | 0.15695
19 | -0.0019909 | -0.00049373 | 0.0019913 | 0.00049232 | 4.4668e-07 | -1.4052e-06 | 0.0030003 | 0.0029997 | 0.0030003 | 0.98677 | -0.25578 | 0.98701 | -0.25102 | 0.82426
20 | 0.00038135 | 9.3962e-05 | -0.00038134 | -9.5572e-05 | 1.5721e-08 | -1.61e-06 | 0.00057457 | 0.00057514 | 0.00057514 | 0.98664 | -0.25829 | 0.9866 | -0.25916 | 0.15801
21 | 0.0017716 | 0.00043855 | -0.0017715 | -0.00043908 | 1.2972e-07 | -5.3754e-07 | 0.0026689 | 0.0026691 | 0.0026691 | 0.98701 | -0.25102 | 0.98693 | -0.25257 | 0.73328
22 | -0.0043855 | -0.0010869 | 0.0043877 | 0.0010866 | 2.2358e-06 | -3.1572e-07 | 0.0066072 | 0.0066066 | 0.0066072 | 0.98701 | -0.25102 | 0.98756 | -0.24023 | 1.8152
23 | 0.0051041 | 0.0012784 | -0.005104 | -0.0012784 | 1.4122e-07 | 6.1934e-09 | 0.0076275 | 0.0076276 | 0.0076276 | 0.9957 | -0.081501 | 0.99567 | -0.082082 | 2.0955
24 | -0.16555 | -0.042305 | 0.1656 | 0.04234 | 5.4184e-05 | 3.4553e-05 | 0.24672 | 0.24672 | 0.24672 | 0.99964 | -0.0067653 | 1 | 0 | 33.8895
25 | 0.051096 | 0.012912 | -0.051087 | -0.012906 | 8.9151e-06 | 5.6519e-06 | 0.076096 | 0.076096 | 0.076096 | 0.99964 | -0.0067653 | 0.99945 | -0.010405 | 20.9056
26 | 0.0038005 | 0.00095175 | -0.0038004 | -0.0009518 | 1.0819e-07 | -4.7077e-08 | 0.0056796 | 0.0056796 | 0.0056796 | 0.99567 | -0.082082 | 0.99564 | -0.08268 | 1.5603
27 | 0.0015948 | 0.00039955 | -0.0015948 | -0.00039968 | 2.5616e-08 | -1.3525e-07 | 0.0024018 | 0.0024019 | 0.0024019 | 0.98801 | -0.22884 | 0.98799 | -0.22918 | 0.65985
28 | 0.055772 | 0.014092 | -0.055678 | -0.014033 | 9.3584e-05 | 5.9453e-05 | 0.084534 | 0.084535 | 0.084535 | 0.9822 | -0.34113 | 0.9804 | -0.3762 | 23.2238
29 | 0.054126 | 0.013644 | -0.054068 | -0.013607 | 5.7684e-05 | 3.6631e-05 | 0.082178 | 0.082178 | 0.082178 | 0.9804 | -0.3762 | 0.97926 | -0.3985 | 22.5763
30 | 0.054068 | 0.013607 | -0.05402 | -0.013577 | 4.7724e-05 | 3.0307e-05 | 0.082178 | 0.082178 | 0.082178 | 0.97926 | -0.3985 | 0.97832 | -0.41698 | 22.5764
31 | 0.049725 | 0.0125 | -0.049688 | -0.012476 | 3.7679e-05 | 2.3895e-05 | 0.075645 | 0.075646 | 0.075646 | 0.97832 | -0.41698 | 0.97751 | -0.43287 | 20.7817
32 | -0.0046846 | -0.001161 | 0.0046856 | 0.0011609 | 1.034e-06 | -4.7475e-08 | 0.0070539 | 0.0070536 | 0.0070539 | 0.98756 | -0.24023 | 0.9878 | -0.23556 | 1.9379
33 | -0.0046856 | -0.0011609 | 0.0046861 | 0.0011609 | 4.3843e-07 | -2.0249e-08 | 0.0070536 | 0.0070535 | 0.0070536 | 0.9878 | -0.23556 | 0.9879 | -0.23358 | 1.9378
34 | -0.0050616 | -0.001255 | 0.0050618 | 0.001255 | 2.2949e-07 | 1.1892e-08 | 0.0076192 | 0.0076192 | 0.0076192 | 0.9879 | -0.23358 | 0.98795 | -0.23262 | 2.0932
35 | -0.0050618 | -0.001255 | 0.0050628 | 0.0012551 | 9.7276e-07 | 5.024e-08 | 0.0076192 | 0.007619 | 0.0076192 | 0.98795 | -0.23262 | 0.98816 | -0.22855 | 2.0932
36 | 0.0014852 | 0.00036918 | -0.0014852 | -0.00036929 | 1.8381e-08 | -1.1315e-07 | 0.0022387 | 0.0022388 | 0.0022388 | 0.98671 | -0.25701 | 0.9867 | -0.25727 | 0.61505
37 | -0.0016015 | -0.00039832 | 0.0016018 | 0.00039657 | 3.3604e-07 | -1.75e-06 | 0.0024141 | 0.0024134 | 0.0024141 | 0.98671 | -0.25701 | 0.98693 | -0.25257 | 0.6632
38 | 0.00080341 | 0.00019842 | -0.00080341 | -0.00019842 | 4.103e-13 | 2.6259e-13 | 0.0012106 | 0.0012106 | 0.0012106 | 0.9867 | -0.25727 | 0.9867 | -0.25727 | 0.33258
39 | 0.00012251 | 2.7768e-05 | -0.00012251 | -2.9223e-05 | 1.4468e-09 | -1.4545e-06 | 0.00018376 | 0.00018425 | 0.00018425 | 0.9867 | -0.25727 | 0.98668 | -0.25753 | 0.050617
40 | -0.005394 | -0.0013381 | 0.0053944 | 0.0013382 | 3.1786e-07 | 3.8641e-08 | 0.0081177 | 0.0081177 | 0.0081177 | 0.98816 | -0.22855 | 0.98822 | -0.2273 | 2.2301
41 | -0.01308 | -0.0032763 | 0.013083 | 0.0032782 | 3.3651e-06 | 1.8714e-06 | 0.019939 | 0.019939 | 0.019939 | 0.97611 | -0.46044 | 0.97638 | -0.45504 | 5.4777
42 | 0.0076346 | 0.0019116 | -0.0076323 | -0.0019107 | 2.3172e-06 | 9.1292e-07 | 0.011638 | 0.011638 | 0.011638 | 0.97611 | -0.46044 | 0.97578 | -0.46682 | 3.1973
43 | -0.014131 | -0.0035407 | 0.014131 | 0.0035408 | 2.1057e-07 | 1.1962e-07 | 0.021535 | 0.021535 | 0.021535 | 0.97638 | -0.45504 | 0.9764 | -0.45473 | 5.9162
44 | 0.0054828 | 0.0013735 | -0.0054826 | -0.0013735 | 2.2082e-07 | 3.6101e-08 | 0.0083607 | 0.0083608 | 0.0083608 | 0.97578 | -0.46682 | 0.97574 | -0.46767 | 2.2969
45 | 0.0021495 | 0.00053723 | -0.0021492 | -0.00053815 | 3.7568e-07 | -9.2425e-07 | 0.0032774 | 0.0032778 | 0.0032778 | 0.97578 | -0.46682 | 0.9756 | -0.47049 | 0.9005
46 | -0.015565 | -0.0039003 | 0.01557 | 0.0039031 | 4.782e-06 | 2.7769e-06 | 0.023721 | 0.023721 | 0.023721 | 0.9764 | -0.45473 | 0.97673 | -0.44828 | 6.5167
47 | 0.0016874 | 0.00042261 | -0.0016873 | -0.00042288 | 6.1496e-08 | -2.6997e-07 | 0.0025732 | 0.0025733 | 0.0025733 | 0.97574 | -0.46767 | 0.9757 | -0.46843 | 0.70695
48 | 0.0037952 | 0.00095085 | -0.0037951 | -0.00095089 | 1.1608e-07 | -4.1132e-08 | 0.0057876 | 0.0057876 | 0.0057876 | 0.97574 | -0.46767 | 0.97571 | -0.46831 | 1.59
49 | 0.0021492 | 0.00053815 | -0.002149 | -0.00053859 | 1.7602e-07 | -4.328e-07 | 0.0032778 | 0.003278 | 0.003278 | 0.9756 | -0.47049 | 0.97551 | -0.47221 | 0.90055
50 | -0.016933 | -0.0042446 | 0.016945 | 0.004252 | 1.2446e-05 | 7.3406e-06 | 0.025797 | 0.025797 | 0.025797 | 0.97673 | -0.44828 | 0.97751 | -0.43287 | 7.087
51 | 0.0027212 | 0.00068176 | -0.0027211 | -0.00068194 | 1.4202e-07 | -1.8374e-07 | 0.0041499 | 0.00415 | 0.00415 | 0.97571 | -0.46831 | 0.97565 | -0.4694 | 1.1401
52 | 0.032742 | 0.0082245 | -0.032734 | -0.0082194 | 8.0794e-06 | 5.0622e-06 | 0.049849 | 0.049849 | 0.049849 | 0.97751 | -0.43287 | 0.97725 | -0.43804 | 13.6948
53 | 0.0016615 | 0.00041639 | -0.0016615 | -0.00041642 | 5.3024e-09 | -2.4104e-08 | 0.0025341 | 0.0025341 | 0.0025341 | 0.97565 | -0.4694 | 0.97565 | -0.46947 | 0.69618
54 | -0.0055783 | -0.0013842 | 0.0055817 | 0.0013848 | 3.4691e-06 | 5.3705e-07 | 0.0083946 | 0.008394 | 0.0083946 | 0.98822 | -0.2273 | 0.98889 | -0.21416 | 2.3062
55 | 0.0089067 | 0.0022317 | -0.0089058 | -0.0022313 | 9.0372e-07 | 4.1638e-07 | 0.013606 | 0.013607 | 0.013607 | 0.97403 | -0.50134 | 0.97392 | -0.50347 | 3.7381
56 | -0.010985 | -0.0027525 | 0.010986 | 0.0027532 | 1.3199e-06 | 6.8916e-07 | 0.016781 | 0.016781 | 0.016781 | 0.97403 | -0.50134 | 0.97416 | -0.49882 | 4.6102
57 | 0.0020783 | 0.00052046 | -0.0020783 | -0.00052063 | 6.1201e-08 | -1.6225e-07 | 0.0031753 | 0.0031753 | 0.0031753 | 0.97392 | -0.50347 | 0.97389 | -0.50409 | 0.87235
58 | 0.0068274 | 0.0017108 | -0.0068269 | -0.0017107 | 5.4746e-07 | 1.8343e-07 | 0.010431 | 0.010431 | 0.010431 | 0.97392 | -0.50347 | 0.97384 | -0.50516 | 2.8657
59 | -0.012083 | -0.0030282 | 0.012088 | 0.0030309 | 4.9975e-06 | 2.7111e-06 | 0.018457 | 0.018457 | 0.018457 | 0.97416 | -0.49882 | 0.9746 | -0.49014 | 5.0706
60 | 0.00058933 | 0.00014746 | -0.00058933 | -0.0001477 | 5.947e-09 | -2.3959e-07 | 0.00090036 | 0.00090045 | 0.00090045 | 0.97389 | -0.50409 | 0.97388 | -0.5043 | 0.24738
61 | 0.006075 | 0.0015222 | -0.0060745 | -0.0015221 | 5.0293e-07 | 1.2824e-07 | 0.0092824 | 0.0092825 | 0.0092825 | 0.97384 | -0.50516 | 0.97375 | -0.5069 | 2.5501
62 | -0.013122 | -0.0032901 | 0.013125 | 0.0032916 | 2.7301e-06 | 1.5212e-06 | 0.020036 | 0.020036 | 0.020036 | 0.9746 | -0.49014 | 0.97482 | -0.48578 | 5.5043
63 | 0.0055236 | 0.001384 | -0.0055231 | -0.0013839 | 4.6957e-07 | 8.1911e-08 | 0.0084406 | 0.0084407 | 0.0084407 | 0.97375 | -0.5069 | 0.97366 | -0.50868 | 2.3189
64 | -0.014435 | -0.0036199 | 0.014436 | 0.0036205 | 1.1062e-06 | 6.3219e-07 | 0.022035 | 0.022035 | 0.022035 | 0.97482 | -0.48578 | 0.9749 | -0.48417 | 6.0535
65 | 0.0047629 | 0.0011934 | -0.0047625 | -0.0011934 | 3.9523e-07 | 5.563e-09 | 0.0072788 | 0.0072789 | 0.0072789 | 0.97366 | -0.50868 | 0.97357 | -0.51042 | 1.9997
66 | -0.010207 | -0.0025592 | 0.01021 | 0.0025606 | 2.8432e-06 | 1.4091e-06 | 0.015377 | 0.015377 | 0.015377 | 0.98775 | -0.23632 | 0.98805 | -0.23048 | 4.2245
67 | 0.010029 | 0.0025144 | -0.010025 | -0.0025128 | 3.4003e-06 | 1.6679e-06 | 0.015108 | 0.015109 | 0.015109 | 0.98775 | -0.23632 | 0.98739 | -0.24344 | 4.1507
68 | -0.01047 | -0.0026258 | 0.010471 | 0.0026262 | 7.433e-07 | 3.7361e-07 | 0.015769 | 0.015769 | 0.015769 | 0.98805 | -0.23048 | 0.98813 | -0.22899 | 4.3322
69 | 0.010025 | 0.0025128 | -0.010023 | -0.0025115 | 2.5192e-06 | 1.236e-06 | 0.015109 | 0.015109 | 0.015109 | 0.98739 | -0.24344 | 0.98712 | -0.24872 | 4.1507
70 | -0.010551 | -0.0026461 | 0.010558 | 0.0026499 | 7.4659e-06 | 3.7672e-06 | 0.015889 | 0.015889 | 0.015889 | 0.98813 | -0.22899 | 0.98889 | -0.21416 | 4.3651
71 | 0.00064025 | 0.00015952 | -0.00064023 | -0.0001601 | 1.6063e-08 | -5.7781e-07 | 0.00096481 | 0.00096501 | 0.00096501 | 0.98712 | -0.24872 | 0.98709 | -0.24925 | 0.26511
72 | 0.0089498 | 0.0022435 | -0.0089443 | -0.002241 | 5.4845e-06 | 2.4836e-06 | 0.013491 | 0.013492 | 0.013492 | 0.98712 | -0.24872 | 0.98645 | -0.26158 | 3.7065
73 | -0.016389 | -0.0040971 | 0.016414 | 0.0041118 | 2.5144e-05 | 1.4675e-05 | 0.024658 | 0.024657 | 0.024658 | 0.98889 | -0.21416 | 0.99055 | -0.18194 | 6.7741
74 | 0.0003722 | 9.2928e-05 | -0.0003722 | -9.3193e-05 | 2.4644e-09 | -2.6533e-07 | 0.00056096 | 0.00056106 | 0.00056106 | 0.98709 | -0.24925 | 0.98708 | -0.24938 | 0.15414
75 | 0.0007871 | 0.00019703 | -0.00078709 | -0.00019726 | 9.7735e-09 | -2.2979e-07 | 0.0011872 | 0.0011873 | 0.0011873 | 0.98645 | -0.26158 | 0.98644 | -0.26185 | 0.32618
76 | 0.0079891 | 0.0020019 | -0.0079832 | -0.0019995 | 5.9689e-06 | 2.4221e-06 | 0.012051 | 0.012052 | 0.012052 | 0.98645 | -0.26158 | 0.98565 | -0.27728 | 3.3109
77 | 0.0023589 | 0.00059069 | -0.0023587 | -0.00059115 | 2.179e-07 | -4.5616e-07 | 0.0035434 | 0.0035436 | 0.0035436 | 0.99055 | -0.18194 | 0.99045 | -0.18388 | 0.97353
78 | -0.018773 | -0.0047025 | 0.018777 | 0.0047045 | 3.287e-06 | 1.9618e-06 | 0.028201 | 0.028201 | 0.028201 | 0.99055 | -0.18194 | 0.99074 | -0.17826 | 7.7474
79 | 0.00014822 | 3.7058e-05 | -0.00014822 | -3.7087e-05 | 4.3637e-11 | -2.9758e-08 | 0.0002234 | 0.00022342 | 0.00022342 | 0.98708 | -0.24938 | 0.98708 | -0.24939 | 0.061378
80 | -0.019445 | -0.0048877 | 0.019446 | 0.0048886 | 1.5048e-06 | 9.0183e-07 | 0.029132 | 0.029132 | 0.029132 | 0.99336 | -0.12742 | 0.99345 | -0.1258 | 8.0033
81 | 0.018822 | 0.0047317 | -0.018817 | -0.0047286 | 5.1585e-06 | 3.0776e-06 | 0.0282 | 0.0282 | 0.0282 | 0.99336 | -0.12742 | 0.99307 | -0.13316 | 7.7472
82 | -0.021024 | -0.0052841 | 0.021029 | 0.0052869 | 4.771e-06 | 2.8874e-06 | 0.031496 | 0.031496 | 0.031496 | 0.99345 | -0.1258 | 0.99369 | -0.12104 | 8.6527
83 | 0.018817 | 0.0047286 | -0.018811 | -0.0047249 | 6.2619e-06 | 3.736e-06 | 0.0282 | 0.0282 | 0.0282 | 0.99307 | -0.13316 | 0.99271 | -0.14013 | 7.7472
84 | -0.021653 | -0.0054433 | 0.021667 | 0.0054517 | 1.3774e-05 | 8.3628e-06 | 0.03243 | 0.03243 | 0.03243 | 0.99369 | -0.12104 | 0.99438 | -0.10773 | 8.9094
85 | 0.018811 | 0.0047249 | -0.018777 | -0.0047045 | 3.4163e-05 | 2.0386e-05 | 0.0282 | 0.028201 | 0.028201 | 0.99271 | -0.14013 | 0.99074 | -0.17826 | 7.7474
86 | -0.023614 | -0.0059398 | 0.023621 | 0.0059438 | 6.5393e-06 | 4.004e-06 | 0.035344 | 0.035344 | 0.035344 | 0.99438 | -0.10773 | 0.99469 | -0.10194 | 9.71
87 | -0.00075775 | -0.00018991 | 0.00075777 | 0.0001893 | 2.3204e-08 | -6.1262e-07 | 0.0011325 | 0.0011323 | 0.0011325 | 0.99559 | -0.083615 | 0.99562 | -0.082972 | 0.31114
88 | -0.0018688 | -0.00046775 | 0.0018688 | 0.00046775 | 1.2281e-11 | -5.0039e-11 | 0.0027929 | 0.0027929 | 0.0027929 | 0.99562 | -0.082972 | 0.99562 | -0.082971 | 0.76727
89 | -0.025077 | -0.0063088 | 0.025079 | 0.0063098 | 1.667e-06 | 1.0259e-06 | 0.037523 | 0.037523 | 0.037523 | 0.99469 | -0.10194 | 0.99476 | -0.10055 | 10.3085
90 | -0.027944 | -0.007028 | 0.027959 | 0.0070372 | 1.4816e-05 | 9.1886e-06 | 0.041809 | 0.041809 | 0.041809 | 0.99476 | -0.10055 | 0.99533 | -0.089452 | 11.4861
91 | 0.015878 | 0.0039824 | -0.01587 | -0.0039776 | 8.2041e-06 | 4.7463e-06 | 0.023739 | 0.023739 | 0.023739 | 0.99533 | -0.089452 | 0.99477 | -0.1003 | 6.5218
92 | -0.043838 | -0.01102 | 0.043858 | 0.011033 | 2.0738e-05 | 1.3105e-05 | 0.065548 | 0.065548 | 0.065548 | 0.99533 | -0.089452 | 0.99585 | -0.079549 | 18.0078
93 | 0.013017 | 0.0032627 | -0.013014 | -0.0032609 | 3.2731e-06 | 1.796e-06 | 0.019472 | 0.019472 | 0.019472 | 0.99477 | -0.1003 | 0.9945 | -0.10558 | 5.3495
94 | -0.04631 | -0.011647 | 0.046311 | 0.011648 | 9.989e-07 | 6.3206e-07 | 0.069212 | 0.069212 | 0.069212 | 0.99585 | -0.079549 | 0.99587 | -0.079098 | 19.0144
95 | 0.012031 | 0.0030144 | -0.012029 | -0.0030133 | 2.0838e-06 | 1.1112e-06 | 0.018001 | 0.018001 | 0.018001 | 0.9945 | -0.10558 | 0.99431 | -0.10921 | 4.9452
96 | -0.048549 | -0.012209 | 0.048701 | 0.012305 | 0.00015206 | 9.6312e-05 | 0.072556 | 0.072555 | 0.072556 | 0.99587 | -0.079098 | 0.99928 | -0.013743 | 19.9329
97 | -7.7397e-05 | -1.9398e-05 | 7.7397e-05 | 1.9338e-05 | 2.367e-11 | -5.9368e-08 | 0.00011668 | 0.00011665 | 0.00011668 | 0.98708 | -0.2494 | 0.98708 | -0.24939 | 0.032054
98 | 0.0029658 | 0.00074262 | -0.0029657 | -0.00074266 | 4.1137e-08 | -4.6293e-08 | 0.0044322 | 0.0044322 | 0.0044322 | 0.99564 | -0.08268 | 0.99562 | -0.082971 | 1.2177
99 | -0.022629 | -0.0056866 | 0.02263 | 0.005687 | 6.6487e-07 | 4.0682e-07 | 0.034463 | 0.034463 | 0.034463 | 0.97721 | -0.43865 | 0.97725 | -0.43804 | 9.468
100 | 0.020592 | 0.0051759 | -0.020583 | -0.005171 | 8.0741e-06 | 4.8933e-06 | 0.03136 | 0.03136 | 0.03136 | 0.97721 | -0.43865 | 0.9768 | -0.44687 | 8.6155
101 | 0.0034413 | 0.00086208 | -0.0034408 | -0.00086235 | 4.6711e-07 | -2.6833e-07 | 0.0052422 | 0.0052424 | 0.0052424 | 0.9768 | -0.44687 | 0.97665 | -0.44972 | 1.4402
102 | 0.017142 | 0.0043089 | -0.017117 | -0.0042943 | 2.4698e-05 | 1.46e-05 | 0.026118 | 0.026119 | 0.026119 | 0.9768 | -0.44687 | 0.97526 | -0.47709 | 7.1755
103 | 0.015524 | 0.0038949 | -0.015519 | -0.0038919 | 5.2393e-06 | 3.0426e-06 | 0.023687 | 0.023688 | 0.023688 | 0.97526 | -0.47709 | 0.9749 | -0.48417 | 6.5076
104 | 0.00012251 | 2.9223e-05 | -0.00012251 | -3.0704e-05 | 1.4817e-09 | -1.4815e-06 | 0.00018425 | 0.00018476 | 0.00018476 | 0.98668 | -0.25753 | 0.98667 | -0.25779 | 0.050759
105 | 0.0083996 | 0.0021037 | -0.008399 | -0.0021035 | 6.1283e-07 | 2.5807e-07 | 0.01257 | 0.01257 | 0.01257 | 0.99431 | -0.10921 | 0.99423 | -0.11075 | 3.4532
106 | 0.0073946 | 0.0018518 | -0.0073929 | -0.0018512 | 1.6848e-06 | 6.0263e-07 | 0.011067 | 0.011067 | 0.011067 | 0.99423 | -0.11075 | 0.99398 | -0.11553 | 3.0403
107 | 0.0064119 | 0.0016053 | -0.0064102 | -0.0016048 | 1.7026e-06 | 4.5103e-07 | 0.0095981 | 0.0095983 | 0.0095983 | 0.99398 | -0.11553 | 0.9937 | -0.12111 | 2.6369
108 | -0.0010323 | -0.00025871 | 0.0010323 | 0.00025795 | 5.4666e-08 | -7.5469e-07 | 0.0015462 | 0.0015459 | 0.0015462 | 0.99342 | -0.12642 | 0.99348 | -0.12531 | 0.42477
109 | -0.0021692 | -0.00054287 | 0.0021692 | 0.00054276 | 4.1849e-08 | -1.1014e-07 | 0.0032487 | 0.0032486 | 0.0032487 | 0.99348 | -0.12531 | 0.9935 | -0.12491 | 0.89249
110 | -0.0021692 | -0.00054276 | 0.0021693 | 0.00054257 | 7.3917e-08 | -1.9457e-07 | 0.0032486 | 0.0032485 | 0.0032486 | 0.9935 | -0.12491 | 0.99354 | -0.12419 | 0.89248
111 | -0.0029632 | -0.00074154 | 0.0029636 | 0.00074106 | 4.339e-07 | -4.834e-07 | 0.0044376 | 0.0044373 | 0.0044376 | 0.99354 | -0.12419 | 0.9937 | -0.12111 | 1.2191
112 | 0.0036719 | 0.00092008 | -0.0036719 | -0.00092008 | 1.3221e-11 | 8.4614e-12 | 0.0056121 | 0.0056121 | 0.0056121 | 0.97357 | -0.51042 | 0.97357 | -0.51042 | 1.5418
113 | 0.0025817 | 0.00064684 | -0.0025816 | -0.00064696 | 7.8536e-08 | -1.17e-07 | 0.0039458 | 0.0039458 | 0.0039458 | 0.97357 | -0.51042 | 0.97354 | -0.51106 | 1.084
114 | 0.0012297 | 0.00030814 | -0.0012297 | -0.00030819 | 5.1497e-09 | -4.504e-08 | 0.0018795 | 0.0018795 | 0.0018795 | 0.97354 | -0.51106 | 0.97353 | -0.51115 | 0.51635
115 | -0.00087022 | -0.0002181 | 0.00087023 | 0.00021776 | 1.7951e-08 | -3.4095e-07 | 0.0013148 | 0.0013146 | 0.0013148 | 0.98489 | -0.29213 | 0.98491 | -0.2917 | 0.3612
116 | -0.0031717 | -0.00079457 | 0.0031719 | 0.00079439 | 2.0965e-07 | -1.7572e-07 | 0.0047918 | 0.0047917 | 0.0047918 | 0.98491 | -0.2917 | 0.98498 | -0.29031 | 1.3164
117 | -0.0033821 | -0.00084706 | 0.0033824 | 0.0008469 | 2.4481e-07 | -1.6168e-07 | 0.0051092 | 0.005109 | 0.0051092 | 0.98498 | -0.29031 | 0.98506 | -0.28879 | 1.4036
118 | -0.049717 | -0.012559 | 0.049725 | 0.012565 | 7.9545e-06 | 5.0402e-06 | 0.074068 | 0.074068 | 0.074068 | 0.99928 | -0.013743 | 0.99945 | -0.010405 | 20.3482
119 | -0.004695 | -0.0011759 | 0.0046971 | 0.0011758 | 2.0946e-06 | -7.4028e-08 | 0.0070919 | 0.0070914 | 0.0070919 | 0.98506 | -0.28879 | 0.98554 | -0.27942 | 1.9483
120 | -0.0054295 | -0.0013594 | 0.0054295 | 0.0013594 | 1.3595e-08 | 1.8258e-09 | 0.0081972 | 0.0081972 | 0.0081972 | 0.98554 | -0.27942 | 0.98554 | -0.27937 | 2.252
121 | 0.007437 | 0.0018626 | -0.0074362 | -0.0018623 | 7.3958e-07 | 2.7393e-07 | 0.011227 | 0.011227 | 0.011227 | 0.98565 | -0.27728 | 0.98554 | -0.27937 | 3.0844

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.16859 | 0.042676

## res_load
| p_mw | q_mvar
0 | 0.0073159 | 0.0018335
1 | 0.0074856 | 0.0018761
2 | 0.0033558 | 0.00084104
3 | 0.0095497 | 0.0023934
4 | 0.0039117 | 0.00098038
5 | 0.011343 | 0.0028429
6 | 0.0036156 | 0.00090616
7 | 0.0021708 | 0.00054405
8 | 0.00054881 | 0.00013755
9 | 9.3825e-05 | 2.3515e-05
10 | 0.00047303 | 0.00011855
11 | 0.00011482 | 2.8776e-05
12 | 0.00037883 | 9.4944e-05
13 | 0.00062258 | 0.00015603
14 | 0.00038134 | 9.5572e-05
15 | 0.0010648 | 0.00026687
16 | 0.0013034 | 0.00032667
17 | 0.000623 | 0.00015614
18 | 0.0015528 | 0.00038916
19 | 0.0042949 | 0.0010764
20 | 0.00029684 | 7.4395e-05
21 | 0.00037555 | 9.4123e-05
22 | 0.00011627 | 2.9139e-05
23 | 0.00068179 | 0.00017087
24 | 0.00016965 | 4.2517e-05
25 | 0.0006809 | 0.00017065
26 | 0.00033123 | 8.3014e-05
27 | 0.0054452 | 0.0013647
28 | 0.0010474 | 0.00026251
29 | 0.0014344 | 0.00035949
30 | 0.0013627 | 0.00034152
31 | 0.0016873 | 0.00042288
32 | 0.0010739 | 0.00026913
33 | 0.002149 | 0.00053859
34 | 0.0010595 | 0.00026555
35 | 0.00018391 | 4.6092e-05
36 | 0.002078 | 0.00052079
37 | 0.0010972 | 0.00027499
38 | 0.001489 | 0.00037317
39 | 0.00075191 | 0.00018845
40 | 0.0010341 | 0.00025917
41 | 0.00058933 | 0.0001477
42 | 0.00055089 | 0.00013807
43 | 0.0013098 | 0.00032827
44 | 0.00076025 | 0.00019054
45 | 0.00017847 | 4.4729e-05
46 | 0.00026027 | 6.5229e-05
47 | 7.9656e-05 | 1.9964e-05
48 | 0.00043283 | 0.00010848
49 | 0.00024923 | 6.2463e-05
50 | 0.00026803 | 6.7175e-05
51 | 0.00016806 | 4.212e-05
52 | 0.00022398 | 5.6135e-05
53 | 0.00062243 | 0.000156
54 | 0.001578 | 0.00039549
55 | 0.00062401 | 0.00015639
56 | 0.0019475 | 0.0004881
57 | 0.00075775 | 0.00018991
58 | 0.0011111 | 0.00027846
59 | 0.0014563 | 0.00036498
60 | 0.0028657 | 0.00071821
61 | 0.0028527 | 0.00071496
62 | 0.0024522 | 0.00061457
63 | 0.00098347 | 0.00024648
64 | 0.0022376 | 0.0005608
65 | 7.7397e-05 | 1.9398e-05
66 | 7.082e-05 | 1.7749e-05
67 | 0.00083464 | 0.00020918
68 | 0.0020379 | 0.00051074
69 | 0.010104 | 0.0025324
70 | 0.0034408 | 0.00086235
71 | 0.0015935 | 0.00039937
72 | 0.0010828 | 0.00027137
73 | 0.0023587 | 0.00059115
74 | 0.00012251 | 3.0704e-05
75 | 0.003629 | 0.00090952
76 | 0.0010044 | 0.00025173
77 | 0.00098099 | 0.00024586
78 | 0.0010323 | 0.00025871
79 | 0.0011369 | 0.00028492
80 | 0.00079391 | 0.00019897
81 | 0.0034465 | 0.00086379
82 | 0.0010905 | 0.00027332
83 | 0.0010902 | 0.00027324
84 | 0.0013519 | 0.00033882
85 | 0.0012297 | 0.00030819
86 | 0.0010969 | 0.00027491
87 | 0.00087022 | 0.0002181
88 | 0.0023015 | 0.00057681
89 | 0.00021016 | 5.2672e-05
90 | 0.0010155 | 0.00025452
91 | 0.0013626 | 0.00034151
92 | 0.0013386 | 0.00033549
93 | 0.0013126 | 0.00032898
94 | 0.00073243 | 0.00018356
95 | 0.00078709 | 0.00019726
96 | 0.00054618 | 0.00013689
97 | 0.0020067 | 0.00050293
98 | 0.0015948 | 0.00039968
99 | 0.0016615 | 0.00041642

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1