## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2325-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2325-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2325-7_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2325-7_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2325-7_0_6_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2325-7_0_6_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2325-7_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2325-7_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2325-7_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2325-7_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2325-7_0_6_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_2325-7_0_6_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_2325-7_0_6_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_2325-7_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2325-7_0_6_node_61 | 0.4 | n |  | TRUE
18 | bus_LV_2325-7_0_6_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_2325-7_0_6_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_2325-7_0_6_node_38 | 0.4 | n |  | TRUE
21 | bus_LV_2325-7_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_2325-7_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_2325-7_0_6_node_84 | 0.4 | n |  | TRUE
24 | bus_LV_2325-7_0_6_node_101 | 0.4 | n |  | TRUE
25 | bus_LV_2325-7_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2325-7_0_6_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_2325-7_0_6_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2325-7_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2325-7_0_6_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2325-7_0_6_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2325-7_0_6_node_75 | 0.4 | n |  | TRUE
32 | bus_LV_2325-7_0_6_node_76 | 0.4 | n |  | TRUE
33 | bus_LV_2325-7_0_6_node_46 | 0.4 | n |  | TRUE
34 | bus_LV_2325-7_0_6_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_2325-7_0_6_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_2325-7_0_6_node_73 | 0.4 | n |  | TRUE
37 | bus_LV_2325-7_0_6_node_52 | 0.4 | n |  | TRUE
38 | bus_LV_2325-7_0_6_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_2325-7_0_6_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_2325-7_0_6_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2325-7_0_6_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2325-7_0_6_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2325-7_0_6_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_2325-7_0_6_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_2325-7_0_6_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2325-7_0_6_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_2325-7_0_6_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_2325-7_0_6_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2325-7_0_6_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2325-7_0_6_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2325-7_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2325-7_0_6_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_2325-7_0_6_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_2325-7_0_6_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_2325-7_0_6_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2325-7_0_6_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2325-7_0_6_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2325-7_0_6_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_2325-7_0_6_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2325-7_0_6_node_77 | 0.4 | n |  | TRUE
61 | bus_LV_2325-7_0_6_node_80 | 0.4 | n |  | TRUE
62 | bus_LV_2325-7_0_6_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_2325-7_0_6_node_78 | 0.4 | n |  | TRUE
64 | bus_LV_2325-7_0_6_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_2325-7_0_6_node_120 | 0.4 | n |  | TRUE
66 | bus_LV_2325-7_0_6_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_2325-7_0_6_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2325-7_0_6_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_2325-7_0_6_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_2325-7_0_6_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2325-7_0_6_node_51 | 0.4 | n |  | TRUE
72 | bus_LV_2325-7_0_6_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_2325-7_0_6_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_2325-7_0_6_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_2325-7_0_6_node_88 | 0.4 | n |  | TRUE
76 | bus_LV_2325-7_0_6_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_2325-7_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_2325-7_0_6_node_86 | 0.4 | n |  | TRUE
79 | bus_LV_2325-7_0_6_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_2325-7_0_6_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_2325-7_0_6_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_2325-7_0_6_node_103 | 0.4 | n |  | TRUE
83 | bus_LV_2325-7_0_6_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_2325-7_0_6_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_2325-7_0_6_node_67 | 0.4 | n |  | TRUE
86 | bus_LV_2325-7_0_6_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_2325-7_0_6_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_2325-7_0_6_node_126 | 0.4 | n |  | TRUE
89 | bus_LV_2325-7_0_6_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_2325-7_0_6_node_121 | 0.4 | n |  | TRUE
91 | bus_LV_2325-7_0_6_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_2325-7_0_6_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_2325-7_0_6_node_105 | 0.4 | n |  | TRUE
94 | bus_LV_2325-7_0_6_node_98 | 0.4 | n |  | TRUE
95 | bus_LV_2325-7_0_6_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_2325-7_0_6_node_102 | 0.4 | n |  | TRUE
97 | bus_LV_2325-7_0_6_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_2325-7_0_6_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_2325-7_0_6_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_2325-7_0_6_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_2325-7_0_6_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_2325-7_0_6_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_2325-7_0_6_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_2325-7_0_6_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_2325-7_0_6_node_106 | 0.4 | n |  | TRUE
106 | bus_LV_2325-7_0_6_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_2325-7_0_6_node_127 | 0.4 | n |  | TRUE
108 | bus_LV_2325-7_0_6_node_114 | 0.4 | n |  | TRUE
109 | bus_LV_2325-7_0_6_node_112 | 0.4 | n |  | TRUE
110 | bus_LV_2325-7_0_6_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_2325-7_0_6_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_2325-7_0_6_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_2325-7_0_6_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_2325-7_0_6_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_2325-7_0_6_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_2325-7_0_6_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2325-7_0_6_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_2325-7_0_6_node_128 | 0.4 | n |  | TRUE
119 | bus_LV_2325-7_0_6_node_113 | 0.4 | n |  | TRUE
120 | bus_LV_2325-7_0_6_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2325-7_0_6_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_2325-7_0_6_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_2325-7_0_6_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_2325-7_0_6_node_117 | 0.4 | n |  | TRUE
125 | bus_LV_2325-7_0_6_node_122 | 0.4 | n |  | TRUE
126 | bus_LV_2325-7_0_6_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_2325-7_0_6_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_2325-7_0_6_node_125 | 0.4 | n |  | TRUE
129 | bus_MV_37_0_node_47 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-7_0_6_load_0 | 0 | 0.0049515 | 0.001241 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-7_0_6_load_1 | 1 | 0.0049387 | 0.0012378 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-7_0_6_load_2 | 2 | 0.0047796 | 0.0011979 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-7_0_6_load_3 | 3 | 0.0042768 | 0.0010719 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-7_0_6_load_4 | 4 | 0.0025449 | 0.00063781 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-7_0_6_load_5 | 5 | 0.015861 | 0.0039752 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-7_0_6_load_6 | 6 | 0.004479 | 0.0011226 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-7_0_6_load_12 | 7 | 0.0040343 | 0.0010111 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-7_0_6_load_13 | 8 | 0.0034719 | 0.00087015 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-7_0_6_load_7 | 9 | 0.0020187 | 0.00050593 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-7_0_6_load_9 | 11 | 0.0034771 | 0.00087144 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-7_0_6_load_10 | 12 | 0.0022409 | 0.00056163 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-7_0_6_load_24 | 15 | 0.0044705 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-7_0_6_load_11 | 16 | 0.008548 | 0.0021423 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-7_0_6_load_61 | 17 | 0.0095041 | 0.002382 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-7_0_6_load_38 | 20 | 0.0028388 | 0.00071148 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-7_0_6_load_14 | 21 | 0.0062679 | 0.0015709 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-7_0_6_load_15 | 22 | 0.0028847 | 0.00072297 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-7_0_6_load_84 | 23 | 0.0029391 | 0.0007366 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-7_0_6_load_101 | 24 | 0.0022489 | 0.00056364 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-7_0_6_load_16 | 25 | 0.0014622 | 0.00036645 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-7_0_6_load_17 | 26 | 0.0018933 | 0.0004745 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-7_0_6_load_18 | 27 | 0.0015691 | 0.00039325 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-7_0_6_load_19 | 28 | 0.0054171 | 0.0013577 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-7_0_6_load_20 | 29 | 0.0046489 | 0.0011651 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-7_0_6_load_21 | 30 | 0.004479 | 0.0011225 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-7_0_6_load_75 | 31 | 0.0016046 | 0.00040215 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-7_0_6_load_76 | 32 | 0.0015579 | 0.00039045 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-7_0_6_load_37 | 34 | 0.0032005 | 0.00080211 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-7_0_6_load_68 | 35 | 0.0027349 | 0.00068542 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-7_0_6_load_73 | 36 | 0.0037667 | 0.00094402 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-7_0_6_load_35 | 38 | 0.002473 | 0.0006198 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-7_0_6_load_25 | 40 | 0.0064323 | 0.0016121 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-7_0_6_load_26 | 41 | 0.0054272 | 0.0013602 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-7_0_6_load_27 | 42 | 0.001395 | 0.00034962 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-7_0_6_load_28 | 43 | 0.0044629 | 0.0011185 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-7_0_6_load_30 | 45 | 0.0013345 | 0.00033445 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-7_0_6_load_69 | 46 | 0.0012988 | 0.00032552 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-7_0_6_load_55 | 47 | 0.004259 | 0.0010674 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-7_0_6_load_31 | 48 | 0.0029352 | 0.00073562 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-7_0_6_load_32 | 49 | 0.0028295 | 0.00070914 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-7_0_6_load_34 | 51 | 0.0055818 | 0.0013989 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-7_0_6_load_36 | 52 | 0.0028557 | 0.00071571 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-7_0_6_load_39 | 53 | 0.0044942 | 0.0011264 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-7_0_6_load_40 | 54 | 0.0024099 | 0.00060398 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-7_0_6_load_41 | 55 | 0.0031031 | 0.0007777 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-7_0_6_load_42 | 56 | 0.0045448 | 0.001139 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-7_0_6_load_43 | 57 | 0.002705 | 0.00067794 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-7_0_6_load_44 | 58 | 0.00363 | 0.00090976 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-7_0_6_load_77 | 60 | 0.0041176 | 0.001032 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-7_0_6_load_80 | 61 | 0.0037109 | 0.00093004 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2325-7_0_6_load_79 | 62 | 0.0028802 | 0.00072185 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2325-7_0_6_load_78 | 63 | 0.0021649 | 0.00054258 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2325-7_0_6_load_81 | 64 | 0.002737 | 0.00068595 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2325-7_0_6_load_120 | 65 | 0.0034982 | 0.00087674 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2325-7_0_6_load_56 | 66 | 0.0048654 | 0.0012194 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2325-7_0_6_load_47 | 68 | 0.004904 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2325-7_0_6_load_50 | 70 | 0.006215 | 0.0015576 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2325-7_0_6_load_51 | 71 | 0.0012774 | 0.00032015 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2325-7_0_6_load_53 | 72 | 0.0057273 | 0.0014354 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2325-7_0_6_load_54 | 73 | 0.0055428 | 0.0013892 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2325-7_0_6_load_57 | 74 | 0.0041191 | 0.0010323 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2325-7_0_6_load_88 | 75 | 0.011157 | 0.0027963 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2325-7_0_6_load_70 | 76 | 0.0018473 | 0.00046297 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2325-7_0_6_load_58 | 77 | 0.0028051 | 0.00070304 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2325-7_0_6_load_86 | 78 | 0.0049673 | 0.0012449 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2325-7_0_6_load_71 | 79 | 0.0084464 | 0.0021169 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2325-7_0_6_load_59 | 80 | 0.0012897 | 0.00032322 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2325-7_0_6_load_60 | 81 | 0.0070908 | 0.0017771 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2325-7_0_6_load_103 | 82 | 0.0034505 | 0.00086477 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2325-7_0_6_load_64 | 83 | 0.0040178 | 0.001007 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2325-7_0_6_load_65 | 84 | 0.0041126 | 0.0010307 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2325-7_0_6_load_67 | 85 | 0.0032329 | 0.00081024 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2325-7_0_6_load_74 | 86 | 0.0036568 | 0.00091647 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2325-7_0_6_load_72 | 87 | 0.0014079 | 0.00035286 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2325-7_0_6_load_126 | 88 | 0.0015207 | 0.00038111 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2325-7_0_6_load_83 | 89 | 0.0015645 | 0.0003921 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2325-7_0_6_load_121 | 90 | 0.0033778 | 0.00084655 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2325-7_0_6_load_82 | 91 | 0.0013819 | 0.00034635 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2325-7_0_6_load_107 | 92 | 0.0025676 | 0.0006435 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2325-7_0_6_load_105 | 93 | 0.0027094 | 0.00067905 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2325-7_0_6_load_98 | 94 | 0.004677 | 0.0011722 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2325-7_0_6_load_96 | 95 | 0.0017669 | 0.00044284 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2325-7_0_6_load_102 | 96 | 0.0021773 | 0.00054569 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2325-7_0_6_load_85 | 97 | 0.0033713 | 0.00084493 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2325-7_0_6_load_87 | 98 | 0.001918 | 0.00048071 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2325-7_0_6_load_89 | 99 | 0.003465 | 0.00086841 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2325-7_0_6_load_91 | 100 | 0.044213 | 0.011081 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2325-7_0_6_load_90 | 101 | 0.002917 | 0.00073106 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2325-7_0_6_load_92 | 102 | 0.0023526 | 0.00058961 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2325-7_0_6_load_108 | 104 | 0.0018118 | 0.00045409 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2325-7_0_6_load_106 | 105 | 0.002147 | 0.00053809 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2325-7_0_6_load_94 | 106 | 0.08157 | 0.020443 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2325-7_0_6_load_127 | 107 | 0.063212 | 0.015842 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2325-7_0_6_load_114 | 108 | 0.0024269 | 0.00060824 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2325-7_0_6_load_112 | 109 | 0.0023451 | 0.00058775 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2325-7_0_6_load_95 | 110 | 0.0022585 | 0.00056605 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2325-7_0_6_load_97 | 111 | 0.0022676 | 0.0005683 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2325-7_0_6_load_99 | 112 | 0.0076888 | 0.001927 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2325-7_0_6_load_100 | 113 | 0.0022212 | 0.00055667 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2325-7_0_6_load_104 | 114 | 0.0025658 | 0.00064304 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2325-7_0_6_load_109 | 115 | 0.0023455 | 0.00058785 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2325-7_0_6_load_110 | 116 | 0.0023459 | 0.00058793 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2325-7_0_6_load_111 | 117 | 0.0023458 | 0.00058792 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2325-7_0_6_load_128 | 118 | 0.0091903 | 0.0023033 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2325-7_0_6_load_113 | 119 | 0.0024327 | 0.00060968 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2325-7_0_6_load_115 | 120 | 0.002433 | 0.00060977 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2325-7_0_6_load_119 | 121 | 0.002346 | 0.00058797 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2325-7_0_6_load_118 | 122 | 0.0023457 | 0.00058789 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2325-7_0_6_load_116 | 123 | 0.0017986 | 0.00045077 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2325-7_0_6_load_117 | 124 | 0.0017957 | 0.00045004 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2325-7_0_6_load_122 | 125 | 0.002672 | 0.00066967 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2325-7_0_6_load_123 | 126 | 0.0015057 | 0.00037736 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2325-7_0_6_load_124 | 127 | 0.0015149 | 0.00037967 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2325-7_0_6_load_125 | 128 | 0.0020881 | 0.00052334 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 75 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-7_0_6_line_0 |  | 0 | 1 | 0.017474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-7_0_6_line_1 |  | 0 | 2 | 0.025472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-7_0_6_line_2 |  | 1 | 3 | 0.007393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-7_0_6_line_3 |  | 2 | 4 | 0.0027313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-7_0_6_line_4 |  | 3 | 5 | 0.01732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-7_0_6_line_5 |  | 4 | 6 | 0.022446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-7_0_6_line_6 |  | 6 | 7 | 0.0073625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-7_0_6_line_7 |  | 7 | 8 | 0.018315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2325-7_0_6_line_8 |  | 8 | 21 | 0.0092229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2325-7_0_6_line_9 |  | 9 | 10 | 0.036527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2325-7_0_6_line_10 |  | 10 | 11 | 0.020322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2325-7_0_6_line_11 |  | 11 | 12 | 0.03045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-7_0_6_line_12 |  | 12 | 13 | 0.048462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2325-7_0_6_line_13 |  | 13 | 14 | 0.023584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-7_0_6_line_14 |  | 13 | 15 | 0.019083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-7_0_6_line_15 |  | 14 | 33 | 0.042721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-7_0_6_line_16 |  | 14 | 34 | 0.03487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-7_0_6_line_17 |  | 15 | 35 | 0.0026862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2325-7_0_6_line_18 |  | 16 | 17 | 0.10678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-7_0_6_line_19 |  | 17 | 18 | 0.00027977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-7_0_6_line_20 |  | 18 | 19 | 0.080137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-7_0_6_line_21 |  | 19 | 20 | 0.030107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-7_0_6_line_22 |  | 20 | 52 | 0.0092958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-7_0_6_line_23 |  | 21 | 22 | 0.012606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2325-7_0_6_line_24 |  | 22 | 23 | 0.0080502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-7_0_6_line_25 |  | 23 | 24 | 0.0077061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-7_0_6_line_26 |  | 24 | 96 | 0.0073573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-7_0_6_line_27 |  | 25 | 26 | 0.0068931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2325-7_0_6_line_28 |  | 25 | 27 | 0.0068055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-7_0_6_line_29 |  | 26 | 28 | 0.0060353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-7_0_6_line_30 |  | 27 | 29 | 0.0061723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-7_0_6_line_31 |  | 29 | 30 | 0.0068237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-7_0_6_line_32 |  | 30 | 31 | 0.011379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-7_0_6_line_33 |  | 31 | 32 | 0.0070898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-7_0_6_line_34 |  | 32 | 91 | 0.0064603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-7_0_6_line_35 |  | 33 | 36 | 0.023268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-7_0_6_line_36 |  | 33 | 37 | 0.043257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-7_0_6_line_37 |  | 34 | 38 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-7_0_6_line_38 |  | 35 | 39 | 0.020268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-7_0_6_line_39 |  | 36 | 65 | 0.025067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-7_0_6_line_40 |  | 37 | 66 | 0.028671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-7_0_6_line_41 |  | 37 | 67 | 0.021511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-7_0_6_line_42 |  | 38 | 50 | 0.047932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-7_0_6_line_43 |  | 39 | 85 | 0.003043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-7_0_6_line_44 |  | 39 | 84 | 0.014731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-7_0_6_line_45 |  | 40 | 41 | 0.0042189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-7_0_6_line_46 |  | 40 | 42 | 0.028255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2325-7_0_6_line_47 |  | 41 | 43 | 0.026708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2325-7_0_6_line_48 |  | 42 | 44 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2325-7_0_6_line_49 |  | 44 | 45 | 0.033735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-7_0_6_line_50 |  | 45 | 46 | 0.025467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2325-7_0_6_line_51 |  | 46 | 47 | 0.043949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2325-7_0_6_line_52 |  | 47 | 71 | 0.0032559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2325-7_0_6_line_53 |  | 48 | 49 | 0.035961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2325-7_0_6_line_54 |  | 48 | 50 | 0.021842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2325-7_0_6_line_55 |  | 49 | 51 | 0.038894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2325-7_0_6_line_56 |  | 50 | 52 | 0.028218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2325-7_0_6_line_57 |  | 53 | 54 | 0.0030429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2325-7_0_6_line_58 |  | 53 | 55 | 0.02349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2325-7_0_6_line_59 |  | 54 | 56 | 0.016437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_2325-7_0_6_line_60 |  | 55 | 57 | 0.0033019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2325-7_0_6_line_61 |  | 56 | 58 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2325-7_0_6_line_62 |  | 57 | 59 | 0.015421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_2325-7_0_6_line_63 |  | 58 | 60 | 0.0087856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2325-7_0_6_line_64 |  | 59 | 61 | 0.029251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2325-7_0_6_line_65 |  | 59 | 62 | 0.014135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-7_0_6_line_66 |  | 60 | 63 | 0.020355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2325-7_0_6_line_67 |  | 61 | 64 | 0.0080844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2325-7_0_6_line_68 |  | 63 | 92 | 0.0040213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2325-7_0_6_line_69 |  | 64 | 94 | 0.030003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_2325-7_0_6_line_70 |  | 65 | 90 | 0.0082566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2325-7_0_6_line_71 |  | 66 | 76 | 0.031916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2325-7_0_6_line_72 |  | 67 | 72 | 0.025522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2325-7_0_6_line_73 |  | 67 | 68 | 0.023371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2325-7_0_6_line_74 |  | 68 | 69 | 0.040291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_2325-7_0_6_line_75 |  | 69 | 70 | 0.016961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2325-7_0_6_line_76 |  | 69 | 71 | 0.034484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2325-7_0_6_line_77 |  | 70 | 73 | 0.046431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_2325-7_0_6_line_78 |  | 72 | 74 | 0.05175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2325-7_0_6_line_79 |  | 73 | 75 | 0.0061836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2325-7_0_6_line_80 |  | 74 | 77 | 0.023267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2325-7_0_6_line_81 |  | 75 | 78 | 0.040697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_2325-7_0_6_line_82 |  | 76 | 79 | 0.012537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2325-7_0_6_line_83 |  | 77 | 80 | 0.019375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2325-7_0_6_line_84 |  | 78 | 97 | 0.0181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2325-7_0_6_line_85 |  | 79 | 87 | 0.033936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2325-7_0_6_line_86 |  | 80 | 81 | 0.021682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2325-7_0_6_line_87 |  | 81 | 82 | 0.021569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2325-7_0_6_line_88 |  | 83 | 84 | 0.031793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2325-7_0_6_line_89 |  | 85 | 86 | 0.019432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2325-7_0_6_line_90 |  | 87 | 88 | 0.006601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2325-7_0_6_line_91 |  | 88 | 89 | 0.0068841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2325-7_0_6_line_92 |  | 89 | 91 | 0.0083788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2325-7_0_6_line_93 |  | 90 | 125 | 0.025871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2325-7_0_6_line_94 |  | 92 | 93 | 0.024111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2325-7_0_6_line_95 |  | 93 | 114 | 0.0014142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2325-7_0_6_line_96 |  | 94 | 95 | 0.015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2325-7_0_6_line_97 |  | 95 | 110 | 0.022047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2325-7_0_6_line_98 |  | 96 | 113 | 0.0075302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2325-7_0_6_line_99 |  | 97 | 98 | 0.02214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2325-7_0_6_line_100 |  | 98 | 99 | 0.020881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_2325-7_0_6_line_101 |  | 98 | 100 | 0.11121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2325-7_0_6_line_102 |  | 99 | 101 | 0.0016309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_2325-7_0_6_line_103 |  | 100 | 102 | 0.03554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_2325-7_0_6_line_104 |  | 101 | 104 | 0.026388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_2325-7_0_6_line_105 |  | 102 | 103 | 0.014466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2325-7_0_6_line_106 |  | 103 | 106 | 0.019753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_2325-7_0_6_line_107 |  | 104 | 105 | 0.0026615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_2325-7_0_6_line_108 |  | 105 | 114 | 0.022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_2325-7_0_6_line_109 |  | 106 | 107 | 0.033263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2325-7_0_6_line_110 |  | 107 | 108 | 0.094625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2325-7_0_6_line_111 |  | 108 | 109 | 0.0067237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2325-7_0_6_line_112 |  | 109 | 116 | 0.0065971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2325-7_0_6_line_113 |  | 110 | 111 | 0.0075146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2325-7_0_6_line_114 |  | 111 | 112 | 0.0074235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2325-7_0_6_line_115 |  | 112 | 113 | 0.00025177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2325-7_0_6_line_116 |  | 115 | 116 | 0.0065968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2325-7_0_6_line_117 |  | 115 | 117 | 0.0065971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2325-7_0_6_line_118 |  | 115 | 118 | 0.084092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2325-7_0_6_line_119 |  | 117 | 119 | 0.00672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2325-7_0_6_line_120 |  | 119 | 120 | 0.010856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2325-7_0_6_line_121 |  | 120 | 121 | 0.0067203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2325-7_0_6_line_122 |  | 121 | 122 | 0.0065968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2325-7_0_6_line_123 |  | 122 | 124 | 0.0065971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2325-7_0_6_line_124 |  | 123 | 124 | 0.0066031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2325-7_0_6_line_125 |  | 125 | 126 | 0.007666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2325-7_0_6_line_126 |  | 126 | 127 | 0.0088099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2325-7_0_6_line_127 |  | 127 | 128 | 0.0057575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-7_0_6_trafo_88 | 0.63 MVA 20/0.4 kV | 129 | 75 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2558093.1604 | 1152174.6938 | 2558098.4486 | 1152191.348
1 | 2558093.1604 | 1152174.6938 | 2558085.4516 | 1152150.4161
2 | 2558098.4486 | 1152191.348 | 2558100.686 | 1152198.3943
3 | 2558084.625 | 1152147.8129 | 2558085.4516 | 1152150.4161
4 | 2558105.9277 | 1152214.9024 | 2558100.686 | 1152198.3943
5 | 2558084.625 | 1152147.8129 | 2558077.8319 | 1152126.4194
6 | 2558075.6038 | 1152119.4021 | 2558077.8319 | 1152126.4194
7 | 2558075.6038 | 1152119.4021 | 2558070.061 | 1152101.9461
8 | 2558070.061 | 1152101.9461 | 2558067.2698 | 1152093.1557
9 | 2558141.1029 | 1152616.4634 | 2558166.3674 | 1152642.8439
10 | 2558141.1029 | 1152616.4634 | 2558128.8579 | 1152600.2451
11 | 2558110.51 | 1152575.9435 | 2558128.8579 | 1152600.2451
12 | 2558083.9158 | 1152535.4983 | 2558100.1243 | 1152562.1878 | 2558110.51 | 1152575.9435
13 | 2558065.1612 | 1152521.1329 | 2558083.9158 | 1152535.4983
14 | 2558083.9158 | 1152535.4983 | 2558100.0213 | 1152525.2626
15 | 2558092.5531 | 1152488.8696 | 2558078.935 | 1152500.226 | 2558065.1612 | 1152521.1329
16 | 2558065.1612 | 1152521.1329 | 2558036.9221 | 1152500.6756
17 | 2558100.0213 | 1152525.2626 | 2558102.2884 | 1152523.8218
18 | 2557896.319 | 1152566.2381 | 2557984.7198 | 1152626.1245
19 | 2557896.319 | 1152566.2381 | 2557896.4277 | 1152565.9803
20 | 2557955.9512 | 1152512.3249 | 2557896.4277 | 1152565.9803
21 | 2557955.9512 | 1152512.3249 | 2557967.4745 | 1152490.055 | 2557969.2597 | 1152485.3503
22 | 2557972.5577 | 1152476.6593 | 2557969.2597 | 1152485.3503
23 | 2558067.2698 | 1152093.1557 | 2558063.4548 | 1152081.1411 | 2558063.4548 | 1152081.1411
24 | 2558061.9329 | 1152073.2361 | 2558063.4548 | 1152081.1411
25 | 2558060.476 | 1152065.669 | 2558061.9329 | 1152073.2361
26 | 2558060.476 | 1152065.669 | 2558059.085 | 1152058.4444
27 | 2558089.7891 | 1152295.5796 | 2558087.8054 | 1152288.9781
28 | 2558089.7891 | 1152295.5796 | 2558091.7477 | 1152302.0971
29 | 2558086.0685 | 1152283.1981 | 2558087.8054 | 1152288.9781
30 | 2558093.524 | 1152308.0083 | 2558091.7477 | 1152302.0971
31 | 2558093.524 | 1152308.0083 | 2558095.4878 | 1152314.5433
32 | 2558098.5295 | 1152325.5055 | 2558097.1929 | 1152320.2173 | 2558095.4878 | 1152314.5433
33 | 2558098.5295 | 1152325.5055 | 2558100.2667 | 1152332.3792
34 | 2558101.8497 | 1152338.6426 | 2558100.2667 | 1152332.3792
35 | 2558092.5531 | 1152488.8696 | 2558084.5593 | 1152472.6838 | 2558084.3023 | 1152467.4746
36 | 2558092.5531 | 1152488.8696 | 2558123.9646 | 1152467.3729 | 2558128.0389 | 1152464.0206
37 | 2558019.1206 | 1152487.2778 | 2558020.5824 | 1152488.8387 | 2558036.9221 | 1152500.6756
38 | 2558119.3943 | 1152512.9504 | 2558102.2884 | 1152523.8218
39 | 2558083.3875 | 1152442.4252 | 2558083.8175 | 1152457.6479 | 2558084.3023 | 1152467.4746
40 | 2558128.0389 | 1152464.0206 | 2558124.622 | 1152459.3198 | 2558123.131 | 1152455.6727 | 2558119.322 | 1152437.1402
41 | 2558142.9716 | 1152448.5975 | 2558133.8146 | 1152459.2557 | 2558128.0389 | 1152464.0206
42 | 2557986.3559 | 1152452.2925 | 2558019.1206 | 1152487.2778
43 | 2558119.3943 | 1152512.9504 | 2558121.9984 | 1152511.376
44 | 2558119.3943 | 1152512.9504 | 2558125.3173 | 1152526.4382
45 | 2558248.4877 | 1152537.8964 | 2558248.3864 | 1152533.6787
46 | 2558258.6644 | 1152509.5524 | 2558255.5766 | 1152511.8466 | 2558248.0926 | 1152521.448 | 2558248.3864 | 1152533.6787
47 | 2558249.1292 | 1152564.5963 | 2558248.4877 | 1152537.8964
48 | 2558268.1576 | 1152502.4989 | 2558258.6644 | 1152509.5524
49 | 2558268.1576 | 1152502.4989 | 2558265.5778 | 1152496.7583 | 2558256.8921 | 1152470.7279
50 | 2558256.8921 | 1152470.7279 | 2558248.8312 | 1152446.5699
51 | 2558248.8312 | 1152446.5699 | 2558248.2505 | 1152444.8298 | 2558232.8291 | 1152417.6119 | 2558223.2715 | 1152412.516
52 | 2558220.3984 | 1152410.9841 | 2558223.2715 | 1152412.516
53 | 2557952.9074 | 1152405.2579 | 2557958.6889 | 1152415.6116 | 2557973.203 | 1152434.8544
54 | 2557986.3559 | 1152452.2925 | 2557973.203 | 1152434.8544
55 | 2557952.9074 | 1152405.2579 | 2557933.9451 | 1152371.2999
56 | 2557986.3559 | 1152452.2925 | 2557976.5386 | 1152466.1682 | 2557972.5577 | 1152476.6593
57 | 2558143.6334 | 1152097.6675 | 2558142.9353 | 1152094.7058
58 | 2558137.5462 | 1152071.842 | 2558142.9353 | 1152094.7058
59 | 2558147.4043 | 1152113.6659 | 2558143.6334 | 1152097.6675
60 | 2558137.5462 | 1152071.842 | 2558136.7886 | 1152068.6281
61 | 2558147.4043 | 1152113.6659 | 2558151.5162 | 1152131.111
62 | 2558133.2507 | 1152053.618 | 2558136.7886 | 1152068.6281
63 | 2558153.5318 | 1152139.6622 | 2558151.5162 | 1152131.111
64 | 2558133.2507 | 1152053.618 | 2558108.114 | 1152038.6593
65 | 2558133.2507 | 1152053.618 | 2558142.1624 | 1152042.6464
66 | 2558153.5318 | 1152139.6622 | 2558158.2017 | 1152159.4745
67 | 2558108.114 | 1152038.6593 | 2558101.1668 | 1152034.525
68 | 2558159.1242 | 1152163.3886 | 2558158.2017 | 1152159.4745
69 | 2558101.1668 | 1152034.525 | 2558083.6925 | 1152024.1261 | 2558074.904 | 1152020.0945
70 | 2558083.3875 | 1152442.4252 | 2558083.1543 | 1152434.1718
71 | 2558119.322 | 1152437.1402 | 2558113.8931 | 1152410.7252 | 2558113.1841 | 1152405.8272
72 | 2558142.9716 | 1152448.5975 | 2558151.7774 | 1152462.41 | 2558154.2821 | 1152471.2012
73 | 2558142.9716 | 1152448.5975 | 2558156.4015 | 1152429.4701
74 | 2558187.0487 | 1152404.4791 | 2558164.0871 | 1152418.5239 | 2558156.4015 | 1152429.4701
75 | 2558187.0487 | 1152404.4791 | 2558181.3265 | 1152388.5127
76 | 2558187.0487 | 1152404.4791 | 2558212.7417 | 1152406.9016 | 2558220.3984 | 1152410.9841
77 | 2558169.4295 | 1152344.0527 | 2558170.0746 | 1152357.1174 | 2558181.3265 | 1152388.5127
78 | 2558154.2821 | 1152471.2012 | 2558163.3718 | 1152503.1057 | 2558166.1137 | 1152521.4786
79 | 2558169.1245 | 1152337.8766 | 2558169.4295 | 1152344.0527
80 | 2558166.1137 | 1152521.4786 | 2558169.5479 | 1152544.4905
81 | 2558167.1175 | 1152297.2294 | 2558169.1245 | 1152337.8766
82 | 2558113.1841 | 1152405.8272 | 2558111.7727 | 1152396.0769 | 2558111.5528 | 1152393.4012
83 | 2558169.5479 | 1152544.4905 | 2558171.1313 | 1152555.1006 | 2558172.9262 | 1152563.5602
84 | 2558174.0088 | 1152280.4931 | 2558167.1175 | 1152297.2294 | 2558167.1175 | 1152297.2294
85 | 2558111.5528 | 1152393.4012 | 2558109.559 | 1152369.1451 | 2558107.2072 | 1152359.84
86 | 2558177.4264 | 1152584.77 | 2558172.9262 | 1152563.5602
87 | 2558177.4264 | 1152584.77 | 2558179.6761 | 1152595.3729 | 2558182.7492 | 1152605.6539
88 | 2558125.3173 | 1152526.4382 | 2558138.1004 | 1152555.5477
89 | 2558138.6275 | 1152501.3215 | 2558121.9984 | 1152511.376
90 | 2558105.5897 | 1152353.4402 | 2558107.2072 | 1152359.84
91 | 2558105.5897 | 1152353.4402 | 2558103.9029 | 1152346.766
92 | 2558101.8497 | 1152338.6426 | 2558103.9029 | 1152346.766
93 | 2558082.7898 | 1152408.3064 | 2558082.7471 | 1152419.7359 | 2558082.8492 | 1152423.3704 | 2558083.1543 | 1152434.1718
94 | 2558159.1242 | 1152163.3886 | 2558164.6558 | 1152186.8567
95 | 2558164.9802 | 1152188.2331 | 2558164.6558 | 1152186.8567
96 | 2558074.904 | 1152020.0945 | 2558064.2145 | 1152015.1908 | 2558061.1139 | 1152017.9942
97 | 2558054.7896 | 1152036.134 | 2558052.7526 | 1152025.5539 | 2558061.1139 | 1152017.9942
98 | 2558057.6614 | 1152051.0499 | 2558059.085 | 1152058.4444
99 | 2558174.0088 | 1152280.4931 | 2558182.0967 | 1152260.8509 | 2558181.8906 | 1152259.9767
100 | 2558177.1001 | 1152239.6525 | 2558181.8906 | 1152259.9767
101 | 2558181.8906 | 1152259.9767 | 2558292.8973 | 1152266.6398
102 | 2558177.1001 | 1152239.6525 | 2558176.7259 | 1152238.0651
103 | 2558292.8973 | 1152266.6398 | 2558306.8477 | 1152279.2268 | 2558317.9535 | 1152291.7659
104 | 2558176.7259 | 1152238.0651 | 2558170.6721 | 1152212.3813
105 | 2558327.545 | 1152302.5952 | 2558317.9535 | 1152291.7659
106 | 2558327.545 | 1152302.5952 | 2558323.0926 | 1152310.0966 | 2558322.8955 | 1152317.0794 | 2558324.0407 | 1152320.9581
107 | 2558170.0615 | 1152209.7908 | 2558170.6721 | 1152212.3813
108 | 2558164.9802 | 1152188.2331 | 2558170.0615 | 1152209.7908
109 | 2558331.3948 | 1152352.6243 | 2558332.7069 | 1152346.4597 | 2558328.2314 | 1152335.1516 | 2558324.0407 | 1152320.9581
110 | 2558295.8812 | 1152440.3321 | 2558331.3948 | 1152352.6243
111 | 2558295.8812 | 1152440.3321 | 2558297.2033 | 1152446.9246
112 | 2558298.5004 | 1152453.3929 | 2558297.2033 | 1152446.9246
113 | 2558054.7896 | 1152036.134 | 2558056.2103 | 1152043.5131
114 | 2558057.6138 | 1152050.8027 | 2558056.2103 | 1152043.5131
115 | 2558057.6614 | 1152051.0499 | 2558057.6138 | 1152050.8027
116 | 2558299.7974 | 1152459.8608 | 2558298.5004 | 1152453.3929
117 | 2558301.0946 | 1152466.3292 | 2558299.7974 | 1152459.8608
118 | 2558299.7974 | 1152459.8608 | 2558382.4036 | 1152444.121
119 | 2558301.0946 | 1152466.3292 | 2558302.4159 | 1152472.9181
120 | 2558304.5504 | 1152483.5622 | 2558302.4159 | 1152472.9181
121 | 2558304.5504 | 1152483.5622 | 2558305.8717 | 1152490.1513
122 | 2558305.8717 | 1152490.1513 | 2558307.1688 | 1152496.6193
123 | 2558307.1688 | 1152496.6193 | 2558308.4659 | 1152503.0876
124 | 2558308.4659 | 1152503.0876 | 2558309.7642 | 1152509.5618
125 | 2558082.7898 | 1152408.3064 | 2558082.8184 | 1152400.6405
126 | 2558082.8184 | 1152400.6405 | 2558082.8513 | 1152391.8307
127 | 2558082.8728 | 1152386.0733 | 2558082.8513 | 1152391.8307

## bus_geodata
| x | y | coords
0 | 2558093.1604 | 1152174.6938
1 | 2558098.4486 | 1152191.348
2 | 2558085.4516 | 1152150.4161
3 | 2558100.686 | 1152198.3943
4 | 2558084.625 | 1152147.8129
5 | 2558105.9277 | 1152214.9024
6 | 2558077.8319 | 1152126.4194
7 | 2558075.6038 | 1152119.4021
8 | 2558070.061 | 1152101.9461
9 | 2558166.3674 | 1152642.8439
10 | 2558141.1029 | 1152616.4634
11 | 2558128.8579 | 1152600.2451
12 | 2558110.51 | 1152575.9435
13 | 2558083.9158 | 1152535.4983
14 | 2558065.1612 | 1152521.1329
15 | 2558100.0213 | 1152525.2626
16 | 2557984.7198 | 1152626.1245
17 | 2557896.319 | 1152566.2381
18 | 2557896.4277 | 1152565.9803
19 | 2557955.9512 | 1152512.3249
20 | 2557969.2597 | 1152485.3503
21 | 2558067.2698 | 1152093.1557
22 | 2558063.4548 | 1152081.1411
23 | 2558061.9329 | 1152073.2361
24 | 2558060.476 | 1152065.669
25 | 2558089.7891 | 1152295.5796
26 | 2558087.8054 | 1152288.9781
27 | 2558091.7477 | 1152302.0971
28 | 2558086.0685 | 1152283.1981
29 | 2558093.524 | 1152308.0083
30 | 2558095.4878 | 1152314.5433
31 | 2558098.5295 | 1152325.5055
32 | 2558100.2667 | 1152332.3792
33 | 2558092.5531 | 1152488.8696
34 | 2558036.9221 | 1152500.6756
35 | 2558102.2884 | 1152523.8218
36 | 2558084.3023 | 1152467.4746
37 | 2558128.0389 | 1152464.0206
38 | 2558019.1206 | 1152487.2778
39 | 2558119.3943 | 1152512.9504
40 | 2558248.3864 | 1152533.6787
41 | 2558248.4877 | 1152537.8964
42 | 2558258.6644 | 1152509.5524
43 | 2558249.1292 | 1152564.5963
44 | 2558268.1576 | 1152502.4989
45 | 2558256.8921 | 1152470.7279
46 | 2558248.8312 | 1152446.5699
47 | 2558223.2715 | 1152412.516
48 | 2557973.203 | 1152434.8544
49 | 2557952.9074 | 1152405.2579
50 | 2557986.3559 | 1152452.2925
51 | 2557933.9451 | 1152371.2999
52 | 2557972.5577 | 1152476.6593
53 | 2558142.9353 | 1152094.7058
54 | 2558143.6334 | 1152097.6675
55 | 2558137.5462 | 1152071.842
56 | 2558147.4043 | 1152113.6659
57 | 2558136.7886 | 1152068.6281
58 | 2558151.5162 | 1152131.111
59 | 2558133.2507 | 1152053.618
60 | 2558153.5318 | 1152139.6622
61 | 2558108.114 | 1152038.6593
62 | 2558142.1624 | 1152042.6464
63 | 2558158.2017 | 1152159.4745
64 | 2558101.1668 | 1152034.525
65 | 2558083.3875 | 1152442.4252
66 | 2558119.322 | 1152437.1402
67 | 2558142.9716 | 1152448.5975
68 | 2558156.4015 | 1152429.4701
69 | 2558187.0487 | 1152404.4791
70 | 2558181.3265 | 1152388.5127
71 | 2558220.3984 | 1152410.9841
72 | 2558154.2821 | 1152471.2013
73 | 2558169.4295 | 1152344.0527
74 | 2558166.1137 | 1152521.4786
75 | 2558169.1245 | 1152337.8766
76 | 2558113.1841 | 1152405.8272
77 | 2558169.5479 | 1152544.4905
78 | 2558167.1175 | 1152297.2294
79 | 2558111.5528 | 1152393.4012
80 | 2558172.9262 | 1152563.5602
81 | 2558177.4264 | 1152584.77
82 | 2558182.7492 | 1152605.6539
83 | 2558138.1004 | 1152555.5477
84 | 2558125.3173 | 1152526.4382
85 | 2558121.9984 | 1152511.376
86 | 2558138.6276 | 1152501.3215
87 | 2558107.2072 | 1152359.84
88 | 2558105.5897 | 1152353.4402
89 | 2558103.9029 | 1152346.766
90 | 2558083.1543 | 1152434.1718
91 | 2558101.8497 | 1152338.6426
92 | 2558159.1242 | 1152163.3886
93 | 2558164.6558 | 1152186.8567
94 | 2558074.904 | 1152020.0945
95 | 2558061.1139 | 1152017.9942
96 | 2558059.085 | 1152058.4444
97 | 2558174.0088 | 1152280.4931
98 | 2558181.8906 | 1152259.9767
99 | 2558177.1001 | 1152239.6525
100 | 2558292.8973 | 1152266.6398
101 | 2558176.7259 | 1152238.0651
102 | 2558317.9535 | 1152291.7659
103 | 2558327.545 | 1152302.5952
104 | 2558170.6721 | 1152212.3813
105 | 2558170.0615 | 1152209.7908
106 | 2558324.0407 | 1152320.9581
107 | 2558331.3948 | 1152352.6243
108 | 2558295.8812 | 1152440.3321
109 | 2558297.2033 | 1152446.9246
110 | 2558054.7896 | 1152036.134
111 | 2558056.2103 | 1152043.5131
112 | 2558057.6138 | 1152050.8027
113 | 2558057.6614 | 1152051.0499
114 | 2558164.9802 | 1152188.2331
115 | 2558299.7974 | 1152459.8608
116 | 2558298.5004 | 1152453.3929
117 | 2558301.0946 | 1152466.3292
118 | 2558382.4036 | 1152444.121
119 | 2558302.4159 | 1152472.9181
120 | 2558304.5504 | 1152483.5622
121 | 2558305.8717 | 1152490.1513
122 | 2558307.1688 | 1152496.6193
123 | 2558309.7642 | 1152509.5618
124 | 2558308.4659 | 1152503.0876
125 | 2558082.7898 | 1152408.3064
126 | 2558082.8184 | 1152400.6405
127 | 2558082.8513 | 1152391.8307
128 | 2558082.8728 | 1152386.0733
129 | 2558187.0487 | 1152404.4791

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97096 | -0.56021 | 0.0049515 | 0.001241
1 | 0.97055 | -0.56832 | 0.0049387 | 0.0012378
2 | 0.97167 | -0.54608 | 0.0047796 | 0.0011979
3 | 0.97041 | -0.57107 | 0.0042768 | 0.0010719
4 | 0.97176 | -0.54433 | 0.0025449 | 0.00063781
5 | 0.97015 | -0.57616 | 0.015861 | 0.0039752
6 | 0.97255 | -0.52886 | 0.004479 | 0.0011226
7 | 0.97283 | -0.52319 | 0.0040343 | 0.0010111
8 | 0.97362 | -0.50773 | 0.0034719 | 0.00087015
9 | 0.9819 | -0.34798 | 0.0020187 | 0.00050593
10 | 0.98197 | -0.34665 | 0 | 0
11 | 0.98201 | -0.3459 | 0.0034771 | 0.00087144
12 | 0.98217 | -0.34288 | 0.0022409 | 0.00056163
13 | 0.98251 | -0.3361 | 0 | 0
14 | 0.98316 | -0.32335 | 0 | 0
15 | 0.98212 | -0.34376 | 0.0044705 | 0.0011204
16 | 0.97601 | -0.46351 | 0.008548 | 0.0021423
17 | 0.97685 | -0.44682 | 0.0095041 | 0.002382
18 | 0.97686 | -0.44673 | 0 | 0
19 | 0.9782 | -0.42034 | 0 | 0
20 | 0.97871 | -0.41044 | 0.0028388 | 0.00071148
21 | 0.97404 | -0.49937 | 0.0062679 | 0.0015709
22 | 0.9747 | -0.4865 | 0.0028847 | 0.00072297
23 | 0.97514 | -0.47786 | 0.0029391 | 0.0007366
24 | 0.97558 | -0.46919 | 0.0022489 | 0.00056364
25 | 0.98472 | -0.29347 | 0.0014622 | 0.00036645
26 | 0.98468 | -0.29437 | 0.0018933 | 0.0004745
27 | 0.98478 | -0.2924 | 0.0015691 | 0.00039325
28 | 0.98465 | -0.29496 | 0.0054171 | 0.0013577
29 | 0.98484 | -0.29125 | 0.0046489 | 0.0011651
30 | 0.98493 | -0.28941 | 0.004479 | 0.0011225
31 | 0.98514 | -0.28543 | 0.0016046 | 0.00040215
32 | 0.98527 | -0.28275 | 0.0015579 | 0.00039045
33 | 0.98596 | -0.269 | 0 | 0
34 | 0.98185 | -0.34903 | 0.0032005 | 0.00080211
35 | 0.98208 | -0.34463 | 0.0027349 | 0.00068542
36 | 0.98557 | -0.27669 | 0.0037667 | 0.00094402
37 | 0.98953 | -0.20008 | 0 | 0
38 | 0.98107 | -0.3642 | 0.002473 | 0.0006198
39 | 0.98179 | -0.35013 | 0 | 0
40 | 0.99256 | -0.14234 | 0.0064323 | 0.0016121
41 | 0.99253 | -0.14307 | 0.0054272 | 0.0013602
42 | 0.99299 | -0.13418 | 0.001395 | 0.00034962
43 | 0.99242 | -0.14518 | 0.0044629 | 0.0011185
44 | 0.99318 | -0.13048 | 0 | 0
45 | 0.99372 | -0.11992 | 0.0013345 | 0.00033445
46 | 0.99417 | -0.11136 | 0.0012988 | 0.00032552
47 | 0.99498 | -0.095593 | 0.004259 | 0.0010674
48 | 0.97928 | -0.39922 | 0.0029352 | 0.00073562
49 | 0.979 | -0.40472 | 0.0028295 | 0.00070914
50 | 0.97951 | -0.39472 | 0 | 0
51 | 0.9788 | -0.40867 | 0.0055818 | 0.0013989
52 | 0.97889 | -0.4069 | 0.0028557 | 0.00071571
53 | 0.98402 | -0.30469 | 0.0044942 | 0.0011264
54 | 0.98412 | -0.30275 | 0.0024099 | 0.00060398
55 | 0.98328 | -0.31906 | 0.0031031 | 0.0007777
56 | 0.98468 | -0.29202 | 0.0045448 | 0.001139
57 | 0.98318 | -0.32102 | 0.002705 | 0.00067794
58 | 0.98531 | -0.27986 | 0.00363 | 0.00090976
59 | 0.98272 | -0.32993 | 0 | 0
60 | 0.98563 | -0.27371 | 0.0041176 | 0.001032
61 | 0.98187 | -0.34634 | 0.0037109 | 0.00093004
62 | 0.98268 | -0.33066 | 0.0028802 | 0.00072185
63 | 0.98639 | -0.25898 | 0.0021649 | 0.00054258
64 | 0.98165 | -0.3507 | 0.002737 | 0.00068595
65 | 0.98523 | -0.28329 | 0.0034982 | 0.00087674
66 | 0.98838 | -0.2224 | 0.0048654 | 0.0012194
67 | 0.99217 | -0.14935 | 0 | 0
68 | 0.99386 | -0.11685 | 0.004904 | 0.0012291
69 | 0.99587 | -0.078477 | 0 | 0
70 | 0.99685 | -0.059802 | 0.006215 | 0.0015576
71 | 0.99506 | -0.094182 | 0.0012774 | 0.00032015
72 | 0.99159 | -0.16042 | 0.0057273 | 0.0014354
73 | 0.99962 | -0.0071847 | 0.0055428 | 0.0013892
74 | 0.99071 | -0.17765 | 0.0041191 | 0.0010323
75 | 1 | 0 | -0.58899 | -0.15117
76 | 0.98724 | -0.24452 | 0.0018473 | 0.00046297
77 | 0.99039 | -0.1837 | 0.0028051 | 0.00070304
78 | 0.99525 | -0.08962 | 0.0049673 | 0.0012449
79 | 0.98681 | -0.25281 | 0.0084464 | 0.0021169
80 | 0.99018 | -0.18777 | 0.0012897 | 0.00032322
81 | 0.98997 | -0.19183 | 0.0070908 | 0.0017771
82 | 0.98991 | -0.19316 | 0.0034505 | 0.00086477
83 | 0.98157 | -0.35461 | 0.0040178 | 0.001007
84 | 0.98168 | -0.3523 | 0.0041126 | 0.0010307
85 | 0.98178 | -0.35051 | 0.0032329 | 0.00081024
86 | 0.98171 | -0.35179 | 0.0036568 | 0.00091647
87 | 0.98592 | -0.27014 | 0.0014079 | 0.00035286
88 | 0.98576 | -0.27335 | 0.0015207 | 0.00038111
89 | 0.98559 | -0.27651 | 0.0015645 | 0.0003921
90 | 0.98514 | -0.28494 | 0.0033778 | 0.00084655
91 | 0.98541 | -0.28012 | 0.0013819 | 0.00034635
92 | 0.98654 | -0.25602 | 0.0025676 | 0.0006435
93 | 0.98748 | -0.23793 | 0.0027094 | 0.00067905
94 | 0.98044 | -0.37427 | 0.004677 | 0.0011722
95 | 0.97922 | -0.39802 | 0.0017669 | 0.00044284
96 | 0.97602 | -0.46061 | 0.0021773 | 0.00054569
97 | 0.99316 | -0.12922 | 0.0033713 | 0.00084493
98 | 0.99063 | -0.17745 | 0.001918 | 0.00048071
99 | 0.98972 | -0.19496 | 0.003465 | 0.00086841
100 | 0.98287 | -0.3271 | 0.044213 | 0.011081
101 | 0.98965 | -0.19629 | 0.002917 | 0.00073106
102 | 0.98088 | -0.36593 | 0.0023526 | 0.00058961
103 | 0.98008 | -0.38157 | 0 | 0
104 | 0.98855 | -0.21746 | 0.0018118 | 0.00045409
105 | 0.98844 | -0.21956 | 0.002147 | 0.00053809
106 | 0.97843 | -0.4137 | 0.08157 | 0.020443
107 | 0.97542 | -0.47285 | 0.063212 | 0.015842
108 | 0.9724 | -0.53224 | 0.0024269 | 0.00060824
109 | 0.9722 | -0.53617 | 0.0023451 | 0.00058775
110 | 0.97757 | -0.43025 | 0.0022585 | 0.00056605
111 | 0.97702 | -0.44095 | 0.0022676 | 0.0005683
112 | 0.97649 | -0.45123 | 0.0076888 | 0.001927
113 | 0.97648 | -0.45154 | 0.0022212 | 0.00055667
114 | 0.98754 | -0.23685 | 0.0025658 | 0.00064304
115 | 0.97186 | -0.54304 | 0.0023455 | 0.00058785
116 | 0.97202 | -0.53975 | 0.0023459 | 0.00058793
117 | 0.97176 | -0.54493 | 0.0023458 | 0.00058792
118 | 0.97113 | -0.55731 | 0.0091903 | 0.0023033
119 | 0.97168 | -0.54656 | 0.0024327 | 0.00060968
120 | 0.97157 | -0.54871 | 0.002433 | 0.00060977
121 | 0.97152 | -0.54974 | 0.002346 | 0.00058797
122 | 0.97148 | -0.55046 | 0.0023457 | 0.00058789
123 | 0.97145 | -0.55112 | 0.0017986 | 0.00045077
124 | 0.97146 | -0.5509 | 0.0017957 | 0.00045004
125 | 0.98496 | -0.28856 | 0.002672 | 0.00066967
126 | 0.98492 | -0.28926 | 0.0015057 | 0.00037736
127 | 0.98489 | -0.28983 | 0.0015149 | 0.00037967
128 | 0.98488 | -0.29005 | 0.0020881 | 0.00052334
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.025093 | 0.0062947 | -0.025083 | -0.0062887 | 9.6913e-06 | 5.9864e-06 | 0.038458 | 0.038458 | 0.038458 | 0.97096 | -0.56021 | 0.97055 | -0.56832 | 10.5653
1 | -0.030045 | -0.0075357 | 0.030065 | 0.0075483 | 2.0253e-05 | 1.2646e-05 | 0.046046 | 0.046046 | 0.046046 | 0.97096 | -0.56021 | 0.97167 | -0.54608 | 12.65
2 | 0.020145 | 0.0050509 | -0.020142 | -0.0050493 | 2.6447e-06 | 1.6012e-06 | 0.030886 | 0.030886 | 0.030886 | 0.97055 | -0.56832 | 0.97041 | -0.57107 | 8.4852
3 | -0.034844 | -0.0087462 | 0.034847 | 0.008748 | 2.9169e-06 | 1.833e-06 | 0.053365 | 0.053365 | 0.053365 | 0.97167 | -0.54608 | 0.97176 | -0.54433 | 14.6608
4 | 0.015865 | 0.0039775 | -0.015861 | -0.0039752 | 3.8441e-06 | 2.2463e-06 | 0.024328 | 0.024328 | 0.024328 | 0.97041 | -0.57107 | 0.97015 | -0.57616 | 6.6835
5 | -0.037392 | -0.0093858 | 0.03742 | 0.0094032 | 2.76e-05 | 1.7386e-05 | 0.057262 | 0.057262 | 0.057262 | 0.97176 | -0.54433 | 0.97255 | -0.52886 | 15.7314
6 | -0.041899 | -0.010526 | 0.04191 | 0.010533 | 1.1349e-05 | 7.1723e-06 | 0.064115 | 0.064115 | 0.064115 | 0.97255 | -0.52886 | 0.97283 | -0.52319 | 17.614
7 | -0.045944 | -0.011544 | 0.045978 | 0.011565 | 3.3929e-05 | 2.1487e-05 | 0.070286 | 0.070286 | 0.070286 | 0.97283 | -0.52319 | 0.97362 | -0.50773 | 19.3092
8 | -0.04945 | -0.012436 | 0.04947 | 0.012448 | 1.9763e-05 | 1.2533e-05 | 0.075592 | 0.075592 | 0.075592 | 0.97362 | -0.50773 | 0.97404 | -0.49937 | 20.767
9 | -0.0020187 | -0.00050593 | 0.0020188 | 0.00050555 | 1.2818e-07 | -3.8002e-07 | 0.0030592 | 0.003059 | 0.0030592 | 0.9819 | -0.34798 | 0.98197 | -0.34665 | 0.84043
10 | -0.0020188 | -0.00050555 | 0.0020189 | 0.00050534 | 7.1309e-08 | -2.1145e-07 | 0.003059 | 0.0030589 | 0.003059 | 0.98197 | -0.34665 | 0.98201 | -0.3459 | 0.84039
11 | -0.005496 | -0.0013768 | 0.0054968 | 0.0013769 | 7.9188e-07 | 1.215e-07 | 0.0083277 | 0.0083275 | 0.0083277 | 0.98201 | -0.3459 | 0.98217 | -0.34288 | 2.2878
12 | -0.0077377 | -0.0019385 | 0.0077402 | 0.0019395 | 2.4973e-06 | 9.8475e-07 | 0.011723 | 0.011722 | 0.011723 | 0.98217 | -0.34288 | 0.98251 | -0.3361 | 3.2205
13 | -0.02998 | -0.0075175 | 0.029998 | 0.0075289 | 1.8234e-05 | 1.1371e-05 | 0.045406 | 0.045406 | 0.045406 | 0.98251 | -0.3361 | 0.98316 | -0.32335 | 12.4742
14 | 0.02224 | 0.005578 | -0.022232 | -0.0055731 | 8.1193e-06 | 4.9548e-06 | 0.033684 | 0.033684 | 0.033684 | 0.98251 | -0.3361 | 0.98212 | -0.34376 | 9.2538
15 | -0.070955 | -0.017862 | 0.07114 | 0.01798 | 0.00018485 | 0.00011776 | 0.10742 | 0.10742 | 0.10742 | 0.98316 | -0.32335 | 0.98596 | -0.269 | 29.5106
16 | 0.040957 | 0.010333 | -0.040906 | -0.010301 | 5.0286e-05 | 3.1741e-05 | 0.062012 | 0.062013 | 0.062013 | 0.98316 | -0.32335 | 0.98185 | -0.34903 | 17.0364
17 | 0.017761 | 0.0044527 | -0.01776 | -0.0044522 | 7.2948e-07 | 4.3287e-07 | 0.026911 | 0.026911 | 0.026911 | 0.98212 | -0.34376 | 0.98208 | -0.34463 | 7.393
18 | -0.008548 | -0.0021423 | 0.0085548 | 0.0021453 | 6.8003e-06 | 3.0166e-06 | 0.013032 | 0.013032 | 0.013032 | 0.97601 | -0.46351 | 0.97685 | -0.44682 | 3.5803
19 | -0.018059 | -0.0045273 | 0.018059 | 0.0045274 | 7.9395e-08 | 4.731e-08 | 0.027509 | 0.027509 | 0.027509 | 0.97685 | -0.44682 | 0.97686 | -0.44673 | 7.5575
20 | -0.018059 | -0.0045274 | 0.018082 | 0.0045409 | 2.2741e-05 | 1.355e-05 | 0.027509 | 0.027509 | 0.027509 | 0.97686 | -0.44673 | 0.9782 | -0.42034 | 7.5575
21 | -0.018082 | -0.0045409 | 0.01809 | 0.004546 | 8.5435e-06 | 5.0897e-06 | 0.027509 | 0.027509 | 0.027509 | 0.9782 | -0.42034 | 0.97871 | -0.41044 | 7.5574
22 | -0.020929 | -0.0052575 | 0.020933 | 0.0052596 | 3.5306e-06 | 2.1427e-06 | 0.031825 | 0.031825 | 0.031825 | 0.97871 | -0.41044 | 0.97889 | -0.4069 | 8.7431
23 | -0.055738 | -0.014019 | 0.055772 | 0.014041 | 3.4288e-05 | 2.1787e-05 | 0.085167 | 0.085167 | 0.085167 | 0.97404 | -0.49937 | 0.9747 | -0.4865 | 23.3975
24 | -0.058657 | -0.014764 | 0.058681 | 0.014779 | 2.422e-05 | 1.54e-05 | 0.089571 | 0.089571 | 0.089571 | 0.9747 | -0.4865 | 0.97514 | -0.47786 | 24.6074
25 | -0.06162 | -0.015516 | 0.061646 | 0.015532 | 2.5564e-05 | 1.6265e-05 | 0.094056 | 0.094056 | 0.094056 | 0.97514 | -0.47786 | 0.97558 | -0.46919 | 25.8395
26 | -0.063895 | -0.016096 | 0.063921 | 0.016112 | 2.622e-05 | 1.6689e-05 | 0.097486 | 0.097486 | 0.097486 | 0.97558 | -0.46919 | 0.97602 | -0.46061 | 26.7818
27 | 0.0073109 | 0.0018323 | -0.0073106 | -0.0018322 | 3.1548e-07 | 1.1422e-07 | 0.011047 | 0.011048 | 0.011048 | 0.98472 | -0.29347 | 0.98468 | -0.29437 | 3.035
28 | -0.008773 | -0.0021987 | 0.0087735 | 0.0021989 | 4.4851e-07 | 2.0047e-07 | 0.013257 | 0.013257 | 0.013257 | 0.98472 | -0.29347 | 0.98478 | -0.2924 | 3.642
29 | 0.0054173 | 0.0013577 | -0.0054171 | -0.0013577 | 1.5168e-07 | 2.0305e-08 | 0.0081864 | 0.0081865 | 0.0081865 | 0.98468 | -0.29437 | 0.98465 | -0.29496 | 2.249
30 | -0.010343 | -0.0025922 | 0.010343 | 0.0025925 | 5.6529e-07 | 2.8325e-07 | 0.015628 | 0.015628 | 0.015628 | 0.98478 | -0.2924 | 0.98484 | -0.29125 | 4.2934
31 | -0.014992 | -0.0037576 | 0.014993 | 0.0037584 | 1.313e-06 | 7.5348e-07 | 0.022652 | 0.022652 | 0.022652 | 0.98484 | -0.29125 | 0.98493 | -0.28941 | 6.223
32 | -0.019472 | -0.0048809 | 0.019476 | 0.0048831 | 3.6931e-06 | 2.2187e-06 | 0.029419 | 0.029419 | 0.029419 | 0.98493 | -0.28941 | 0.98514 | -0.28543 | 8.0821
33 | -0.021081 | -0.0052853 | 0.021083 | 0.0052869 | 2.6957e-06 | 1.635e-06 | 0.031842 | 0.031842 | 0.031842 | 0.98514 | -0.28543 | 0.98527 | -0.28275 | 8.7479
34 | -0.022641 | -0.0056774 | 0.022644 | 0.0056791 | 2.8328e-06 | 1.7307e-06 | 0.034195 | 0.034195 | 0.034195 | 0.98527 | -0.28275 | 0.98541 | -0.28012 | 9.3943
35 | 0.018437 | 0.0046249 | -0.018431 | -0.0046209 | 6.7565e-06 | 4.0275e-06 | 0.027827 | 0.027827 | 0.027827 | 0.98596 | -0.269 | 0.98557 | -0.27669 | 7.6448
36 | -0.089577 | -0.022605 | 0.089874 | 0.022794 | 0.00029671 | 0.00018934 | 0.13525 | 0.13525 | 0.13525 | 0.98596 | -0.269 | 0.98953 | -0.20008 | 37.1553
37 | 0.037706 | 0.0094992 | -0.037679 | -0.009482 | 2.7343e-05 | 1.7218e-05 | 0.057162 | 0.057162 | 0.057162 | 0.98185 | -0.34903 | 0.98107 | -0.3642 | 15.7039
38 | 0.015026 | 0.0037668 | -0.015022 | -0.0037646 | 3.9396e-06 | 2.265e-06 | 0.022767 | 0.022767 | 0.022767 | 0.98208 | -0.34463 | 0.98179 | -0.35013 | 6.2546
39 | 0.014664 | 0.0036768 | -0.014659 | -0.0036742 | 4.6079e-06 | 2.6298e-06 | 0.02214 | 0.02214 | 0.02214 | 0.98557 | -0.27669 | 0.98523 | -0.28329 | 6.0825
40 | 0.043816 | 0.011038 | -0.04377 | -0.011008 | 4.6706e-05 | 2.9524e-05 | 0.065909 | 0.06591 | 0.06591 | 0.98953 | -0.20008 | 0.98838 | -0.2224 | 18.107
41 | -0.13369 | -0.033831 | 0.13402 | 0.03404 | 0.0003264 | 0.00020862 | 0.20115 | 0.20115 | 0.20115 | 0.98953 | -0.20008 | 0.99217 | -0.14935 | 55.2622
42 | 0.035206 | 0.0088622 | -0.035154 | -0.0088299 | 5.1278e-05 | 3.2213e-05 | 0.053411 | 0.053412 | 0.053412 | 0.98107 | -0.3642 | 0.97951 | -0.39472 | 14.6735
43 | 0.00689 | 0.0017266 | -0.0068899 | -0.0017266 | 1.2444e-07 | 4.1158e-08 | 0.010442 | 0.010443 | 0.010443 | 0.98179 | -0.35013 | 0.98178 | -0.35051 | 2.8688
44 | 0.0081317 | 0.0020379 | -0.0081308 | -0.0020376 | 8.3907e-07 | 3.5074e-07 | 0.012324 | 0.012324 | 0.012324 | 0.98179 | -0.35013 | 0.98168 | -0.3523 | 3.3858
45 | 0.0098909 | 0.0024788 | -0.0098906 | -0.0024786 | 3.4786e-07 | 1.681e-07 | 0.014828 | 0.014828 | 0.014828 | 0.99256 | -0.14234 | 0.99253 | -0.14307 | 4.0737
46 | -0.016323 | -0.0040909 | 0.01633 | 0.0040946 | 6.345e-06 | 3.6954e-06 | 0.024471 | 0.024471 | 0.024471 | 0.99256 | -0.14234 | 0.99299 | -0.13418 | 6.7229
47 | 0.0044634 | 0.0011185 | -0.0044629 | -0.0011185 | 4.4846e-07 | -5.8117e-08 | 0.0066915 | 0.0066916 | 0.0066916 | 0.99253 | -0.14307 | 0.99242 | -0.14518 | 1.8384
48 | -0.017725 | -0.0044442 | 0.017728 | 0.0044461 | 3.129e-06 | 1.8495e-06 | 0.026562 | 0.026561 | 0.026562 | 0.99299 | -0.13418 | 0.99318 | -0.13048 | 7.2971
49 | -0.017728 | -0.0044461 | 0.017737 | 0.0044514 | 8.9251e-06 | 5.2753e-06 | 0.026561 | 0.026561 | 0.026561 | 0.99318 | -0.13048 | 0.99372 | -0.11992 | 7.2971
50 | -0.019071 | -0.0047858 | 0.019079 | 0.0047905 | 7.7897e-06 | 4.6553e-06 | 0.02856 | 0.028559 | 0.02856 | 0.99372 | -0.11992 | 0.99417 | -0.11136 | 7.846
51 | -0.020378 | -0.005116 | 0.020393 | 0.0051252 | 1.5335e-05 | 9.2439e-06 | 0.030503 | 0.030503 | 0.030503 | 0.99417 | -0.11136 | 0.99498 | -0.095593 | 8.3801
52 | -0.024652 | -0.0061926 | 0.024654 | 0.0061936 | 1.66e-06 | 1.0201e-06 | 0.036873 | 0.036873 | 0.036873 | 0.99498 | -0.095593 | 0.99506 | -0.094182 | 10.1299
53 | 0.0084146 | 0.0021092 | -0.0084124 | -0.0021083 | 2.2047e-06 | 9.587e-07 | 0.012786 | 0.012786 | 0.012786 | 0.97928 | -0.39922 | 0.979 | -0.40472 | 3.5127
54 | -0.01135 | -0.0028448 | 0.011352 | 0.0028461 | 2.4362e-06 | 1.2843e-06 | 0.017246 | 0.017246 | 0.017246 | 0.97928 | -0.39922 | 0.97951 | -0.39472 | 4.7379
55 | 0.0055829 | 0.0013991 | -0.0055818 | -0.0013989 | 1.0502e-06 | 1.8319e-07 | 0.0084856 | 0.0084857 | 0.0084857 | 0.979 | -0.40472 | 0.9788 | -0.40867 | 2.3312
56 | 0.023802 | 0.0059838 | -0.023788 | -0.0059753 | 1.3841e-05 | 8.5031e-06 | 0.036166 | 0.036166 | 0.036166 | 0.97951 | -0.39472 | 0.97889 | -0.4069 | 9.9356
57 | -0.10725 | -0.027216 | 0.10726 | 0.027222 | 1.0019e-05 | 6.2963e-06 | 0.1623 | 0.1623 | 0.1623 | 0.98402 | -0.30469 | 0.98412 | -0.30275 | 14.8626
58 | 0.10275 | 0.026089 | -0.10268 | -0.026045 | 7.1004e-05 | 4.4548e-05 | 0.1555 | 0.1555 | 0.1555 | 0.98402 | -0.30469 | 0.98328 | -0.31906 | 14.2403
59 | -0.10967 | -0.027826 | 0.10973 | 0.027862 | 5.6578e-05 | 3.5583e-05 | 0.16594 | 0.16594 | 0.16594 | 0.98412 | -0.30275 | 0.98468 | -0.29202 | 15.1963
60 | 0.09958 | 0.025267 | -0.099571 | -0.025261 | 9.387e-06 | 5.882e-06 | 0.15081 | 0.15081 | 0.15081 | 0.98328 | -0.31906 | 0.98318 | -0.32102 | 13.8102
61 | -0.11427 | -0.029001 | 0.11434 | 0.029043 | 6.6906e-05 | 4.2135e-05 | 0.17281 | 0.17281 | 0.17281 | 0.98468 | -0.29202 | 0.98531 | -0.27986 | 15.8252
62 | 0.096866 | 0.024583 | -0.096824 | -0.024557 | 4.1493e-05 | 2.5969e-05 | 0.14671 | 0.14671 | 0.14671 | 0.98318 | -0.32102 | 0.98272 | -0.32993 | 13.4354
63 | -0.11797 | -0.029953 | 0.118 | 0.029975 | 3.491e-05 | 2.2006e-05 | 0.17829 | 0.17829 | 0.17829 | 0.98531 | -0.27986 | 0.98563 | -0.27371 | 16.3272
64 | 0.093944 | 0.023836 | -0.09387 | -0.023789 | 7.4094e-05 | 4.6309e-05 | 0.14235 | 0.14235 | 0.14235 | 0.98272 | -0.32993 | 0.98187 | -0.34634 | 13.036
65 | 0.0028803 | 0.00072173 | -0.0028802 | -0.00072185 | 1.0082e-07 | -1.1455e-07 | 0.0043612 | 0.0043613 | 0.0043613 | 0.98272 | -0.32993 | 0.98268 | -0.33066 | 1.1982
66 | -0.12212 | -0.031007 | 0.12221 | 0.031061 | 8.662e-05 | 5.4658e-05 | 0.18451 | 0.18451 | 0.18451 | 0.98563 | -0.27371 | 0.98639 | -0.25898 | 16.8964
67 | 0.090159 | 0.022859 | -0.09014 | -0.022848 | 1.8892e-05 | 1.1784e-05 | 0.13673 | 0.13673 | 0.13673 | 0.98187 | -0.34634 | 0.98165 | -0.3507 | 12.521
68 | -0.12437 | -0.031604 | 0.12439 | 0.031615 | 1.7723e-05 | 1.1189e-05 | 0.18777 | 0.18777 | 0.18777 | 0.98639 | -0.25898 | 0.98654 | -0.25602 | 17.1955
69 | 0.087403 | 0.022162 | -0.087304 | -0.022099 | 9.8886e-05 | 6.2529e-05 | 0.13258 | 0.13258 | 0.13258 | 0.98165 | -0.3507 | 0.98044 | -0.37427 | 18.2117
70 | 0.011161 | 0.0027975 | -0.01116 | -0.002797 | 8.7981e-07 | 4.5794e-07 | 0.016857 | 0.016857 | 0.016857 | 0.98523 | -0.28329 | 0.98514 | -0.28494 | 4.631
71 | 0.038904 | 0.0097886 | -0.038863 | -0.0097627 | 4.1078e-05 | 2.5881e-05 | 0.058585 | 0.058585 | 0.058585 | 0.98838 | -0.2224 | 0.98724 | -0.24452 | 16.0947
72 | 0.02452 | 0.0061576 | -0.024507 | -0.0061496 | 1.2946e-05 | 7.9558e-06 | 0.036778 | 0.036778 | 0.036778 | 0.99217 | -0.14935 | 0.99159 | -0.16042 | 10.1039
73 | -0.15854 | -0.040198 | 0.15878 | 0.040356 | 0.00024808 | 0.00015817 | 0.23793 | 0.23793 | 0.23793 | 0.99217 | -0.14935 | 0.99386 | -0.11685 | 32.683
74 | -0.16369 | -0.041585 | 0.16399 | 0.041777 | 0.00030299 | 0.00019234 | 0.24527 | 0.24527 | 0.24527 | 0.99386 | -0.11685 | 0.99587 | -0.078477 | 22.461
75 | -0.18994 | -0.048303 | 0.19011 | 0.048412 | 0.00017107 | 0.00010882 | 0.28406 | 0.28406 | 0.28406 | 0.99587 | -0.078477 | 0.99685 | -0.059802 | 26.0125
76 | 0.025951 | 0.0065258 | -0.025931 | -0.0065138 | 1.945e-05 | 1.2e-05 | 0.038783 | 0.038783 | 0.038783 | 0.99587 | -0.078477 | 0.99506 | -0.094182 | 10.6547
77 | -0.19633 | -0.049969 | 0.19683 | 0.050287 | 0.00049939 | 0.00031779 | 0.29333 | 0.29333 | 0.29333 | 0.99685 | -0.059802 | 0.99962 | -0.0071847 | 26.862
78 | 0.018779 | 0.0047142 | -0.018764 | -0.004705 | 1.5415e-05 | 9.1986e-06 | 0.028184 | 0.028184 | 0.028184 | 0.99159 | -0.16042 | 0.99071 | -0.17765 | 7.7428
79 | -0.20237 | -0.051676 | 0.20244 | 0.051721 | 7.0302e-05 | 4.475e-05 | 0.30158 | 0.30158 | 0.30158 | 0.99962 | -0.0071847 | 1 | 0 | 27.6176
80 | 0.014645 | 0.0036727 | -0.014641 | -0.0036703 | 4.2218e-06 | 2.4025e-06 | 0.021997 | 0.021997 | 0.021997 | 0.99071 | -0.17765 | 0.99039 | -0.1837 | 6.0432
81 | 0.3849 | 0.099445 | -0.38322 | -0.098375 | 0.0016749 | 0.0010703 | 0.57379 | 0.5738 | 0.5738 | 1 | 0 | 0.99525 | -0.08962 | 52.5453
82 | 0.037016 | 0.0092998 | -0.037001 | -0.0092905 | 1.4638e-05 | 9.2082e-06 | 0.0558 | 0.055801 | 0.055801 | 0.98724 | -0.24452 | 0.98681 | -0.25281 | 15.3298
83 | 0.011836 | 0.0029672 | -0.011833 | -0.002966 | 2.2976e-06 | 1.2212e-06 | 0.017783 | 0.017783 | 0.017783 | 0.99039 | -0.1837 | 0.99018 | -0.18777 | 4.8854
84 | 0.37826 | 0.09713 | -0.37753 | -0.096666 | 0.00072573 | 0.00046377 | 0.56637 | 0.56637 | 0.56637 | 0.99525 | -0.08962 | 0.99316 | -0.12922 | 51.8653
85 | 0.028555 | 0.0071737 | -0.028531 | -0.007159 | 2.36e-05 | 1.4671e-05 | 0.043064 | 0.043064 | 0.043064 | 0.98681 | -0.25281 | 0.98592 | -0.27014 | 11.8309
86 | 0.010544 | 0.0026428 | -0.010542 | -0.0026418 | 2.0413e-06 | 1.0276e-06 | 0.015845 | 0.015845 | 0.015845 | 0.99018 | -0.18777 | 0.98997 | -0.19183 | 4.353
87 | 0.0034507 | 0.00086463 | -0.0034505 | -0.00086477 | 2.1759e-07 | -1.3805e-07 | 0.0051866 | 0.0051867 | 0.0051867 | 0.98997 | -0.19183 | 0.98991 | -0.19316 | 1.4249
88 | -0.0040178 | -0.001007 | 0.0040182 | 0.0010068 | 4.4228e-07 | -1.1885e-07 | 0.0060908 | 0.0060907 | 0.0060908 | 0.98157 | -0.35461 | 0.98168 | -0.3523 | 1.6733
89 | 0.003657 | 0.00091637 | -0.0036568 | -0.00091647 | 2.2387e-07 | -1.0244e-07 | 0.0055426 | 0.0055427 | 0.0055427 | 0.98178 | -0.35051 | 0.98171 | -0.35179 | 1.5227
90 | 0.027123 | 0.0068061 | -0.027119 | -0.0068036 | 4.1488e-06 | 2.5711e-06 | 0.040939 | 0.040939 | 0.040939 | 0.98592 | -0.27014 | 0.98576 | -0.27335 | 11.2471
91 | 0.025599 | 0.0064225 | -0.025595 | -0.0064201 | 3.8551e-06 | 2.3795e-06 | 0.038644 | 0.038644 | 0.038644 | 0.98576 | -0.27335 | 0.98559 | -0.27651 | 10.6165
92 | 0.02403 | 0.006028 | -0.024026 | -0.0060254 | 4.1361e-06 | 2.5404e-06 | 0.036282 | 0.036282 | 0.036282 | 0.98559 | -0.27651 | 0.98541 | -0.28012 | 9.9676
93 | 0.0077824 | 0.0019505 | -0.007781 | -0.0019499 | 1.3406e-06 | 5.2863e-07 | 0.011755 | 0.011755 | 0.011755 | 0.98514 | -0.28494 | 0.98496 | -0.28856 | 3.2294
94 | -0.12696 | -0.032258 | 0.12707 | 0.032328 | 0.0001107 | 6.9921e-05 | 0.19165 | 0.19165 | 0.19165 | 0.98654 | -0.25602 | 0.98748 | -0.23793 | 17.5501
95 | -0.12978 | -0.033007 | 0.12978 | 0.033012 | 6.7721e-06 | 4.2798e-06 | 0.19573 | 0.19573 | 0.19573 | 0.98748 | -0.23793 | 0.98754 | -0.23685 | 17.924
96 | 0.082627 | 0.020927 | -0.082533 | -0.020867 | 9.4125e-05 | 6.0039e-05 | 0.12548 | 0.12548 | 0.12548 | 0.98044 | -0.37427 | 0.97922 | -0.39802 | 34.4733
97 | 0.080766 | 0.020424 | -0.080642 | -0.020344 | 0.00012467 | 7.951e-05 | 0.1228 | 0.1228 | 0.1228 | 0.97922 | -0.39802 | 0.97757 | -0.43025 | 33.7357
98 | -0.066098 | -0.016658 | 0.066127 | 0.016676 | 2.8695e-05 | 1.8271e-05 | 0.10081 | 0.10081 | 0.10081 | 0.97602 | -0.46061 | 0.97648 | -0.45154 | 27.6938
99 | 0.37416 | 0.095822 | -0.37329 | -0.095264 | 0.00087199 | 0.00055722 | 0.56132 | 0.56132 | 0.56132 | 0.99316 | -0.12922 | 0.99063 | -0.17745 | 51.4028
100 | 0.14308 | 0.036495 | -0.14296 | -0.036419 | 0.00012082 | 7.652e-05 | 0.21515 | 0.21515 | 0.21515 | 0.99063 | -0.17745 | 0.98972 | -0.19496 | 19.7023
101 | 0.22829 | 0.058288 | -0.22665 | -0.057244 | 0.0016382 | 0.0010442 | 0.34329 | 0.34329 | 0.34329 | 0.99063 | -0.17745 | 0.98287 | -0.3271 | 31.4367
102 | 0.1395 | 0.03555 | -0.13949 | -0.035545 | 8.9853e-06 | 5.6877e-06 | 0.20994 | 0.20994 | 0.20994 | 0.98972 | -0.19496 | 0.98965 | -0.19629 | 19.2253
103 | 0.18243 | 0.046163 | -0.18209 | -0.045948 | 0.00033928 | 0.00021579 | 0.27635 | 0.27635 | 0.27635 | 0.98287 | -0.3271 | 0.98088 | -0.36593 | 25.3071
104 | 0.13657 | 0.034814 | -0.13643 | -0.034725 | 0.00013937 | 8.818e-05 | 0.20555 | 0.20555 | 0.20555 | 0.98965 | -0.19629 | 0.98855 | -0.21746 | 18.8237
105 | 0.17974 | 0.045358 | -0.17961 | -0.045272 | 0.00013456 | 8.557e-05 | 0.27279 | 0.27279 | 0.27279 | 0.98088 | -0.36593 | 0.98008 | -0.38157 | 24.9803
106 | 0.17961 | 0.045272 | -0.17933 | -0.045097 | 0.0002756 | 0.00017589 | 0.27279 | 0.27279 | 0.27279 | 0.98008 | -0.38157 | 0.97843 | -0.4137 | 37.4705
107 | 0.13462 | 0.034271 | -0.13461 | -0.034263 | 1.3686e-05 | 8.6569e-06 | 0.20283 | 0.20283 | 0.20283 | 0.98855 | -0.21746 | 0.98844 | -0.21956 | 18.5739
108 | 0.13246 | 0.033725 | -0.13235 | -0.033655 | 0.00011029 | 6.9738e-05 | 0.1996 | 0.1996 | 0.1996 | 0.98844 | -0.21956 | 0.98754 | -0.23685 | 18.278
109 | 0.097762 | 0.024653 | -0.097486 | -0.024477 | 0.00027594 | 0.00017618 | 0.14873 | 0.14873 | 0.14873 | 0.97843 | -0.4137 | 0.97542 | -0.47285 | 40.8606
110 | 0.034274 | 0.0086346 | -0.034177 | -0.0085736 | 9.7067e-05 | 6.0946e-05 | 0.052302 | 0.052302 | 0.052302 | 0.97542 | -0.47285 | 0.9724 | -0.53224 | 14.3687
111 | 0.03175 | 0.0079654 | -0.031744 | -0.0079617 | 5.9526e-06 | 3.7262e-06 | 0.048588 | 0.048588 | 0.048588 | 0.9724 | -0.53224 | 0.9722 | -0.53617 | 13.3485
112 | 0.029399 | 0.0073739 | -0.029394 | -0.0073708 | 5.0094e-06 | 3.1243e-06 | 0.044999 | 0.044999 | 0.044999 | 0.9722 | -0.53617 | 0.97202 | -0.53975 | 12.3624
113 | 0.078383 | 0.019778 | -0.078343 | -0.019753 | 4.0147e-05 | 2.56e-05 | 0.11936 | 0.11936 | 0.11936 | 0.97757 | -0.43025 | 0.97702 | -0.44095 | 32.7912
114 | 0.076075 | 0.019185 | -0.076038 | -0.019161 | 3.7398e-05 | 2.3842e-05 | 0.11591 | 0.11591 | 0.11591 | 0.97702 | -0.44095 | 0.97649 | -0.45123 | 31.8425
115 | 0.068349 | 0.017234 | -0.068348 | -0.017233 | 1.0249e-06 | 6.5279e-07 | 0.10419 | 0.10419 | 0.10419 | 0.97649 | -0.45123 | 0.97648 | -0.45154 | 28.6236
116 | -0.027044 | -0.0067802 | 0.027048 | 0.0067829 | 4.2416e-06 | 2.6329e-06 | 0.041408 | 0.041408 | 0.041408 | 0.97186 | -0.54304 | 0.97202 | -0.53975 | 11.3758
117 | 0.015502 | 0.0038861 | -0.0155 | -0.0038853 | 1.3937e-06 | 8.1023e-07 | 0.023735 | 0.023735 | 0.023735 | 0.97186 | -0.54304 | 0.97176 | -0.54493 | 6.5207
118 | 0.0091966 | 0.0023063 | -0.0091903 | -0.0023033 | 6.2531e-06 | 2.9608e-06 | 0.014081 | 0.014082 | 0.014082 | 0.97186 | -0.54304 | 0.97113 | -0.55731 | 3.8686
119 | 0.013155 | 0.0032974 | -0.013153 | -0.0032968 | 1.0225e-06 | 5.7115e-07 | 0.020143 | 0.020143 | 0.020143 | 0.97176 | -0.54493 | 0.97168 | -0.54656 | 5.5338
120 | 0.010721 | 0.0026871 | -0.01072 | -0.0026866 | 1.0973e-06 | 5.6783e-07 | 0.016418 | 0.016418 | 0.016418 | 0.97168 | -0.54656 | 0.97157 | -0.54871 | 4.5104
121 | 0.0082867 | 0.0020768 | -0.0082863 | -0.0020766 | 4.0593e-07 | 1.7658e-07 | 0.012692 | 0.012692 | 0.012692 | 0.97157 | -0.54871 | 0.97152 | -0.54974 | 3.4867
122 | 0.0059403 | 0.0014886 | -0.0059401 | -0.0014886 | 2.0478e-07 | 4.9377e-08 | 0.0090983 | 0.0090984 | 0.0090984 | 0.97152 | -0.54974 | 0.97148 | -0.55046 | 2.4995
123 | 0.0035944 | 0.00090071 | -0.0035943 | -0.00090074 | 7.4985e-08 | -3.3691e-08 | 0.0055054 | 0.0055055 | 0.0055055 | 0.97148 | -0.55046 | 0.97146 | -0.5509 | 1.5125
124 | -0.0017986 | -0.00045077 | 0.0017986 | 0.0004507 | 1.8794e-08 | -6.9725e-08 | 0.002755 | 0.002755 | 0.002755 | 0.97145 | -0.55112 | 0.97146 | -0.5509 | 0.75686
125 | 0.005109 | 0.0012803 | -0.0051088 | -0.0012803 | 1.7126e-07 | 1.2038e-08 | 0.0077183 | 0.0077184 | 0.0077184 | 0.98496 | -0.28856 | 0.98492 | -0.28926 | 2.1204
126 | 0.0036032 | 0.0009029 | -0.0036031 | -0.00090295 | 9.7898e-08 | -4.9462e-08 | 0.0054436 | 0.0054436 | 0.0054436 | 0.98492 | -0.28926 | 0.98489 | -0.28983 | 1.4955
127 | 0.0020882 | 0.00052328 | -0.0020881 | -0.00052334 | 2.149e-08 | -5.9515e-08 | 0.0031549 | 0.0031549 | 0.0031549 | 0.98489 | -0.28983 | 0.98488 | -0.29005 | 0.86673

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60015 | 0.15396

## res_load
| p_mw | q_mvar
0 | 0.0049515 | 0.001241
1 | 0.0049387 | 0.0012378
2 | 0.0047796 | 0.0011979
3 | 0.0042768 | 0.0010719
4 | 0.0025449 | 0.00063781
5 | 0.015861 | 0.0039752
6 | 0.004479 | 0.0011226
7 | 0.0040343 | 0.0010111
8 | 0.0034719 | 0.00087015
9 | 0.0020187 | 0.00050593
10 | 0.0034771 | 0.00087144
11 | 0.0022409 | 0.00056163
12 | 0.0044705 | 0.0011204
13 | 0.008548 | 0.0021423
14 | 0.0095041 | 0.002382
15 | 0.0028388 | 0.00071148
16 | 0.0062679 | 0.0015709
17 | 0.0028847 | 0.00072297
18 | 0.0029391 | 0.0007366
19 | 0.0022489 | 0.00056364
20 | 0.0014622 | 0.00036645
21 | 0.0018933 | 0.0004745
22 | 0.0015691 | 0.00039325
23 | 0.0054171 | 0.0013577
24 | 0.0046489 | 0.0011651
25 | 0.004479 | 0.0011225
26 | 0.0016046 | 0.00040215
27 | 0.0015579 | 0.00039045
28 | 0.0032005 | 0.00080211
29 | 0.0027349 | 0.00068542
30 | 0.0037667 | 0.00094402
31 | 0.002473 | 0.0006198
32 | 0.0064323 | 0.0016121
33 | 0.0054272 | 0.0013602
34 | 0.001395 | 0.00034962
35 | 0.0044629 | 0.0011185
36 | 0.0013345 | 0.00033445
37 | 0.0012988 | 0.00032552
38 | 0.004259 | 0.0010674
39 | 0.0029352 | 0.00073562
40 | 0.0028295 | 0.00070914
41 | 0.0055818 | 0.0013989
42 | 0.0028557 | 0.00071571
43 | 0.0044942 | 0.0011264
44 | 0.0024099 | 0.00060398
45 | 0.0031031 | 0.0007777
46 | 0.0045448 | 0.001139
47 | 0.002705 | 0.00067794
48 | 0.00363 | 0.00090976
49 | 0.0041176 | 0.001032
50 | 0.0037109 | 0.00093004
51 | 0.0028802 | 0.00072185
52 | 0.0021649 | 0.00054258
53 | 0.002737 | 0.00068595
54 | 0.0034982 | 0.00087674
55 | 0.0048654 | 0.0012194
56 | 0.004904 | 0.0012291
57 | 0.006215 | 0.0015576
58 | 0.0012774 | 0.00032015
59 | 0.0057273 | 0.0014354
60 | 0.0055428 | 0.0013892
61 | 0.0041191 | 0.0010323
62 | 0.011157 | 0.0027963
63 | 0.0018473 | 0.00046297
64 | 0.0028051 | 0.00070304
65 | 0.0049673 | 0.0012449
66 | 0.0084464 | 0.0021169
67 | 0.0012897 | 0.00032322
68 | 0.0070908 | 0.0017771
69 | 0.0034505 | 0.00086477
70 | 0.0040178 | 0.001007
71 | 0.0041126 | 0.0010307
72 | 0.0032329 | 0.00081024
73 | 0.0036568 | 0.00091647
74 | 0.0014079 | 0.00035286
75 | 0.0015207 | 0.00038111
76 | 0.0015645 | 0.0003921
77 | 0.0033778 | 0.00084655
78 | 0.0013819 | 0.00034635
79 | 0.0025676 | 0.0006435
80 | 0.0027094 | 0.00067905
81 | 0.004677 | 0.0011722
82 | 0.0017669 | 0.00044284
83 | 0.0021773 | 0.00054569
84 | 0.0033713 | 0.00084493
85 | 0.001918 | 0.00048071
86 | 0.003465 | 0.00086841
87 | 0.044213 | 0.011081
88 | 0.002917 | 0.00073106
89 | 0.0023526 | 0.00058961
90 | 0.0018118 | 0.00045409
91 | 0.002147 | 0.00053809
92 | 0.08157 | 0.020443
93 | 0.063212 | 0.015842
94 | 0.0024269 | 0.00060824
95 | 0.0023451 | 0.00058775
96 | 0.0022585 | 0.00056605
97 | 0.0022676 | 0.0005683
98 | 0.0076888 | 0.001927
99 | 0.0022212 | 0.00055667
100 | 0.0025658 | 0.00064304
101 | 0.0023455 | 0.00058785
102 | 0.0023459 | 0.00058793
103 | 0.0023458 | 0.00058792
104 | 0.0091903 | 0.0023033
105 | 0.0024327 | 0.00060968
106 | 0.002433 | 0.00060977
107 | 0.002346 | 0.00058797
108 | 0.0023457 | 0.00058789
109 | 0.0017986 | 0.00045077
110 | 0.0017957 | 0.00045004
111 | 0.002672 | 0.00066967
112 | 0.0015057 | 0.00037736
113 | 0.0015149 | 0.00037967
114 | 0.0020881 | 0.00052334

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1