## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2325-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2325-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2325-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2325-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2325-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2325-8_0_4_node_102 | 0.4 | n |  | TRUE
6 | bus_LV_2325-8_0_4_node_103 | 0.4 | n |  | TRUE
7 | bus_LV_2325-8_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2325-8_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2325-8_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2325-8_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2325-8_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2325-8_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2325-8_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2325-8_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_2325-8_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_2325-8_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2325-8_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2325-8_0_4_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_2325-8_0_4_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_2325-8_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_2325-8_0_4_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_2325-8_0_4_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_2325-8_0_4_node_78 | 0.4 | n |  | TRUE
24 | bus_LV_2325-8_0_4_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_2325-8_0_4_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_2325-8_0_4_node_79 | 0.4 | n |  | TRUE
27 | bus_LV_2325-8_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2325-8_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_2325-8_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_2325-8_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2325-8_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_2325-8_0_4_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_2325-8_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2325-8_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_2325-8_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_2325-8_0_4_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_2325-8_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2325-8_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_2325-8_0_4_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_2325-8_0_4_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_2325-8_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2325-8_0_4_node_119 | 0.4 | n |  | TRUE
43 | bus_LV_2325-8_0_4_node_121 | 0.4 | n |  | TRUE
44 | bus_LV_2325-8_0_4_node_117 | 0.4 | n |  | TRUE
45 | bus_LV_2325-8_0_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_2325-8_0_4_node_120 | 0.4 | n |  | TRUE
47 | bus_LV_2325-8_0_4_node_64 | 0.4 | n |  | TRUE
48 | bus_LV_2325-8_0_4_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_2325-8_0_4_node_127 | 0.4 | n |  | TRUE
50 | bus_LV_2325-8_0_4_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_2325-8_0_4_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2325-8_0_4_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_2325-8_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_2325-8_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_2325-8_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_2325-8_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_2325-8_0_4_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2325-8_0_4_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_2325-8_0_4_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2325-8_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_2325-8_0_4_node_41 | 0.4 | n |  | TRUE
62 | bus_LV_2325-8_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_2325-8_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_2325-8_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2325-8_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_2325-8_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2325-8_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2325-8_0_4_node_128 | 0.4 | n |  | TRUE
69 | bus_LV_2325-8_0_4_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_2325-8_0_4_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_2325-8_0_4_node_89 | 0.4 | n |  | TRUE
72 | bus_LV_2325-8_0_4_node_130 | 0.4 | n |  | TRUE
73 | bus_LV_2325-8_0_4_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_2325-8_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2325-8_0_4_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_2325-8_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_2325-8_0_4_node_80 | 0.4 | n |  | TRUE
78 | bus_LV_2325-8_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_2325-8_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2325-8_0_4_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_2325-8_0_4_node_87 | 0.4 | n |  | TRUE
82 | bus_LV_2325-8_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_2325-8_0_4_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_2325-8_0_4_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_2325-8_0_4_node_116 | 0.4 | n |  | TRUE
86 | bus_LV_2325-8_0_4_node_118 | 0.4 | n |  | TRUE
87 | bus_LV_2325-8_0_4_node_115 | 0.4 | n |  | TRUE
88 | bus_LV_2325-8_0_4_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_2325-8_0_4_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_2325-8_0_4_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_2325-8_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_2325-8_0_4_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_2325-8_0_4_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2325-8_0_4_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_2325-8_0_4_node_98 | 0.4 | n |  | TRUE
96 | bus_LV_2325-8_0_4_node_112 | 0.4 | n |  | TRUE
97 | bus_LV_2325-8_0_4_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_2325-8_0_4_node_81 | 0.4 | n |  | TRUE
99 | bus_LV_2325-8_0_4_node_82 | 0.4 | n |  | TRUE
100 | bus_LV_2325-8_0_4_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_2325-8_0_4_node_84 | 0.4 | n |  | TRUE
102 | bus_LV_2325-8_0_4_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_2325-8_0_4_node_131 | 0.4 | n |  | TRUE
104 | bus_LV_2325-8_0_4_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_2325-8_0_4_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_2325-8_0_4_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_2325-8_0_4_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_2325-8_0_4_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_2325-8_0_4_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_2325-8_0_4_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_2325-8_0_4_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_2325-8_0_4_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_2325-8_0_4_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_2325-8_0_4_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_2325-8_0_4_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_2325-8_0_4_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2325-8_0_4_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_2325-8_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_2325-8_0_4_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_2325-8_0_4_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_2325-8_0_4_node_106 | 0.4 | n |  | TRUE
122 | bus_LV_2325-8_0_4_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_2325-8_0_4_node_123 | 0.4 | n |  | TRUE
124 | bus_LV_2325-8_0_4_node_122 | 0.4 | n |  | TRUE
125 | bus_LV_2325-8_0_4_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_2325-8_0_4_node_125 | 0.4 | n |  | TRUE
127 | bus_LV_2325-8_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_2325-8_0_4_node_126 | 0.4 | n |  | TRUE
129 | bus_MV_37_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2325-8_0_4_load_0 | 0 | 0.0044029 | 0.0011035 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2325-8_0_4_load_1 | 1 | 0.0025429 | 0.00063732 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2325-8_0_4_load_2 | 2 | 0.0012484 | 0.00031288 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2325-8_0_4_load_3 | 3 | 0.0039262 | 0.00098399 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2325-8_0_4_load_4 | 4 | 0.0018353 | 0.00045998 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2325-8_0_4_load_102 | 5 | 0.0033504 | 0.00083968 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2325-8_0_4_load_5 | 7 | 0.0025457 | 0.00063801 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2325-8_0_4_load_6 | 8 | 0.0025814 | 0.00064695 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2325-8_0_4_load_8 | 10 | 0.0019157 | 0.00048012 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2325-8_0_4_load_10 | 12 | 0.0016626 | 0.00041668 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2325-8_0_4_load_11 | 13 | 0.0042337 | 0.0010611 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2325-8_0_4_load_12 | 14 | 0.0030197 | 0.00075681 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2325-8_0_4_load_13 | 15 | 0.001111 | 0.00027843 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2325-8_0_4_load_15 | 17 | 0.0015181 | 0.00038047 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2325-8_0_4_load_31 | 18 | 0.0070997 | 0.0017793 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2325-8_0_4_load_30 | 19 | 0.00425 | 0.0010652 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2325-8_0_4_load_45 | 20 | 0.0025372 | 0.00063588 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2325-8_0_4_load_59 | 21 | 0.0022628 | 0.00056712 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2325-8_0_4_load_38 | 22 | 0.0083521 | 0.0020932 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2325-8_0_4_load_78 | 23 | 0.0020674 | 0.00051813 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2325-8_0_4_load_47 | 24 | 0.0024539 | 0.00061502 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2325-8_0_4_load_44 | 25 | 0.0027041 | 0.00067772 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2325-8_0_4_load_79 | 26 | 0.0055919 | 0.0014015 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2325-8_0_4_load_36 | 27 | 0.0065351 | 0.0016379 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2325-8_0_4_load_16 | 28 | 0.00104 | 0.00026065 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2325-8_0_4_load_17 | 29 | 0.0015383 | 0.00038553 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2325-8_0_4_load_18 | 30 | 0.0033799 | 0.0008471 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2325-8_0_4_load_19 | 31 | 0.0061238 | 0.0015348 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2325-8_0_4_load_20 | 32 | 0.0013289 | 0.00033306 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2325-8_0_4_load_21 | 33 | 0.0039998 | 0.0010024 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2325-8_0_4_load_22 | 34 | 0.0062868 | 0.0015756 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2325-8_0_4_load_25 | 38 | 0.0025909 | 0.00064934 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2325-8_0_4_load_58 | 39 | 0.0033697 | 0.00084453 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2325-8_0_4_load_57 | 40 | 0.0025796 | 0.00064651 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2325-8_0_4_load_26 | 41 | 0.0017301 | 0.0004336 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2325-8_0_4_load_119 | 42 | 0.00057748 | 0.00014473 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2325-8_0_4_load_121 | 43 | 0.0029689 | 0.00074407 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2325-8_0_4_load_117 | 44 | 0.00060728 | 0.0001522 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2325-8_0_4_load_66 | 45 | 0.00027306 | 6.8436e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2325-8_0_4_load_120 | 46 | 0.00067794 | 0.00016991 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2325-8_0_4_load_64 | 47 | 0.00040588 | 0.00010172 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2325-8_0_4_load_29 | 48 | 0.0021289 | 0.00053356 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2325-8_0_4_load_127 | 49 | 0.0023026 | 0.00057709 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2325-8_0_4_load_96 | 50 | 0.0021345 | 0.00053495 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2325-8_0_4_load_32 | 52 | 0.0025566 | 0.00064074 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2325-8_0_4_load_33 | 53 | 0.0033875 | 0.00084898 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2325-8_0_4_load_34 | 54 | 0.0054133 | 0.0013567 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2325-8_0_4_load_35 | 55 | 0.0028554 | 0.00071564 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2325-8_0_4_load_37 | 56 | 0.054035 | 0.013543 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2325-8_0_4_load_43 | 57 | 0.0018245 | 0.00045727 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2325-8_0_4_load_42 | 58 | 0.0014404 | 0.00036099 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2325-8_0_4_load_39 | 59 | 0.0018128 | 0.00045434 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2325-8_0_4_load_40 | 60 | 0.0023684 | 0.00059357 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2325-8_0_4_load_41 | 61 | 0.001516 | 0.00037996 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2325-8_0_4_load_50 | 63 | 0.0090659 | 0.0022721 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2325-8_0_4_load_51 | 64 | 0.0030405 | 0.00076202 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2325-8_0_4_load_52 | 65 | 0.033241 | 0.008331 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2325-8_0_4_load_53 | 66 | 0.0022753 | 0.00057024 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2325-8_0_4_load_54 | 67 | 0.0018541 | 0.00046469 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2325-8_0_4_load_128 | 68 | 0.028609 | 0.0071702 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2325-8_0_4_load_60 | 70 | 0.0023672 | 0.00059327 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2325-8_0_4_load_89 | 71 | 0.00089046 | 0.00022317 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2325-8_0_4_load_130 | 72 | 0.027178 | 0.0068116 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2325-8_0_4_load_61 | 74 | 0.0014291 | 0.00035816 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2325-8_0_4_load_55 | 75 | 0.0031342 | 0.00078551 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2325-8_0_4_load_56 | 76 | 0.00147 | 0.00036841 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2325-8_0_4_load_62 | 78 | 0.0021281 | 0.00053336 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2325-8_0_4_load_63 | 79 | 0.00080562 | 0.00020191 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2325-8_0_4_load_86 | 80 | 0.0020338 | 0.00050973 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2325-8_0_4_load_87 | 81 | 0.0018153 | 0.00045497 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2325-8_0_4_load_65 | 82 | 0.0013283 | 0.0003329 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2325-8_0_4_load_67 | 83 | 0.0034025 | 0.00085275 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2325-8_0_4_load_68 | 84 | 0.0033215 | 0.00083245 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2325-8_0_4_load_116 | 85 | 0.00072086 | 0.00018066 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2325-8_0_4_load_118 | 86 | 0.00059418 | 0.00014892 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2325-8_0_4_load_115 | 87 | 0.0030621 | 0.00076744 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2325-8_0_4_load_69 | 88 | 0.0049921 | 0.0012511 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2325-8_0_4_load_70 | 89 | 0.0021137 | 0.00052975 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2325-8_0_4_load_71 | 90 | 0.0017635 | 0.00044197 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2325-8_0_4_load_72 | 91 | 0.0017661 | 0.00044264 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2325-8_0_4_load_73 | 92 | 0.0036369 | 0.0009115 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2325-8_0_4_load_75 | 93 | 0.0032201 | 0.00080702 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2325-8_0_4_load_77 | 94 | 0.0023238 | 0.0005824 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2325-8_0_4_load_98 | 95 | 0.0023252 | 0.00058275 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2325-8_0_4_load_112 | 96 | 0.00081034 | 0.00020309 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2325-8_0_4_load_99 | 97 | 0.0012139 | 0.00030424 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2325-8_0_4_load_81 | 98 | 0.0013992 | 0.00035066 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2325-8_0_4_load_82 | 99 | 0.0021794 | 0.00054622 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2325-8_0_4_load_83 | 100 | 0.0032865 | 0.00082369 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2325-8_0_4_load_84 | 101 | 0.0044537 | 0.0011162 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2325-8_0_4_load_85 | 102 | 0.0016218 | 0.00040647 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2325-8_0_4_load_131 | 103 | 0.0049323 | 0.0012362 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2325-8_0_4_load_90 | 104 | 0.002016 | 0.00050525 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2325-8_0_4_load_91 | 105 | 0.0028325 | 0.0007099 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2325-8_0_4_load_88 | 106 | 0.0034706 | 0.00086981 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2325-8_0_4_load_113 | 107 | 0.0010138 | 0.00025408 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2325-8_0_4_load_92 | 108 | 0.0015536 | 0.00038938 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2325-8_0_4_load_93 | 109 | 0.0026594 | 0.0006665 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2325-8_0_4_load_94 | 110 | 0.0025662 | 0.00064315 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2325-8_0_4_load_95 | 111 | 0.0026689 | 0.00066889 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2325-8_0_4_load_97 | 112 | 0.0010955 | 0.00027456 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2325-8_0_4_load_104 | 113 | 0.0012433 | 0.00031161 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2325-8_0_4_load_100 | 115 | 0.0012849 | 0.00032203 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2325-8_0_4_load_101 | 116 | 0.0010407 | 0.00026083 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2325-8_0_4_load_110 | 118 | 0.0045138 | 0.0011313 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2325-8_0_4_load_107 | 120 | 0.004507 | 0.0011296 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2325-8_0_4_load_106 | 121 | 0.00088503 | 0.00022181 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2325-8_0_4_load_108 | 122 | 0.00082707 | 0.00020728 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2325-8_0_4_load_122 | 124 | 0.0043706 | 0.0010954 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2325-8_0_4_load_124 | 125 | 0.00097959 | 0.00024551 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2325-8_0_4_load_125 | 126 | 0.00083202 | 0.00020852 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2325-8_0_4_load_114 | 127 | 0.0013722 | 0.00034391 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2325-8_0_4_load_126 | 128 | 0.0038467 | 0.00096407 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2325-8_0_4_line_0 |  | 0 | 1 | 0.0074608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2325-8_0_4_line_1 |  | 0 | 2 | 0.021625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2325-8_0_4_line_2 |  | 2 | 3 | 0.0069478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2325-8_0_4_line_3 |  | 3 | 4 | 0.020421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2325-8_0_4_line_4 |  | 4 | 5 | 0.012086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2325-8_0_4_line_5 |  | 5 | 6 | 0.018028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2325-8_0_4_line_6 |  | 6 | 120 | 0.0082196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2325-8_0_4_line_7 |  | 7 | 8 | 0.028742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2325-8_0_4_line_8 |  | 7 | 9 | 0.012626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2325-8_0_4_line_9 |  | 8 | 10 | 0.010996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_2325-8_0_4_line_10 |  | 9 | 11 | 0.035273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2325-8_0_4_line_11 |  | 9 | 12 | 0.018369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2325-8_0_4_line_12 |  | 10 | 13 | 0.001927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2325-8_0_4_line_13 |  | 10 | 14 | 0.033161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2325-8_0_4_line_14 |  | 11 | 15 | 0.018323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2325-8_0_4_line_15 |  | 11 | 16 | 0.028406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2325-8_0_4_line_16 |  | 12 | 17 | 0.0059917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2325-8_0_4_line_17 |  | 13 | 18 | 0.018624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2325-8_0_4_line_18 |  | 14 | 19 | 0.0017189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2325-8_0_4_line_19 |  | 15 | 20 | 0.0031603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2325-8_0_4_line_20 |  | 16 | 21 | 0.015182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2325-8_0_4_line_21 |  | 16 | 22 | 0.0083029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2325-8_0_4_line_22 |  | 17 | 23 | 0.01089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2325-8_0_4_line_23 |  | 18 | 24 | 0.023836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2325-8_0_4_line_24 |  | 20 | 25 | 0.019853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2325-8_0_4_line_25 |  | 21 | 26 | 0.0127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2325-8_0_4_line_26 |  | 22 | 27 | 0.027132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2325-8_0_4_line_27 |  | 24 | 51 | 0.040486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_2325-8_0_4_line_28 |  | 25 | 36 | 0.0098572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2325-8_0_4_line_29 |  | 26 | 77 | 0.013872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2325-8_0_4_line_30 |  | 27 | 54 | 0.016924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2325-8_0_4_line_31 |  | 28 | 29 | 0.031142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2325-8_0_4_line_32 |  | 28 | 30 | 0.0046782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2325-8_0_4_line_33 |  | 29 | 31 | 0.015413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2325-8_0_4_line_34 |  | 30 | 32 | 0.012149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2325-8_0_4_line_35 |  | 31 | 33 | 0.00055712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2325-8_0_4_line_36 |  | 32 | 34 | 0.0058097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2325-8_0_4_line_37 |  | 33 | 35 | 0.030641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2325-8_0_4_line_38 |  | 34 | 36 | 0.035927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2325-8_0_4_line_39 |  | 35 | 37 | 0.051966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2325-8_0_4_line_40 |  | 37 | 38 | 0.025152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2325-8_0_4_line_41 |  | 38 | 39 | 0.0032239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2325-8_0_4_line_42 |  | 39 | 40 | 0.023398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2325-8_0_4_line_43 |  | 40 | 76 | 0.02331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2325-8_0_4_line_44 |  | 41 | 42 | 0.12205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2325-8_0_4_line_45 |  | 42 | 43 | 0.024078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2325-8_0_4_line_46 |  | 42 | 44 | 0.0088598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2325-8_0_4_line_47 |  | 43 | 48 | 0.023097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2325-8_0_4_line_48 |  | 44 | 87 | 0.0029402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2325-8_0_4_line_49 |  | 45 | 46 | 0.035127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2325-8_0_4_line_50 |  | 45 | 47 | 0.0026203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2325-8_0_4_line_51 |  | 46 | 86 | 0.015709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2325-8_0_4_line_52 |  | 47 | 82 | 0.0020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2325-8_0_4_line_53 |  | 49 | 50 | 0.038241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2325-8_0_4_line_54 |  | 50 | 110 | 0.00051737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2325-8_0_4_line_55 |  | 51 | 62 | 0.026006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2325-8_0_4_line_56 |  | 51 | 63 | 0.035774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_2325-8_0_4_line_57 |  | 51 | 64 | 0.029928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2325-8_0_4_line_58 |  | 52 | 53 | 0.0040342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2325-8_0_4_line_59 |  | 52 | 54 | 0.011776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2325-8_0_4_line_60 |  | 53 | 55 | 0.021503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2325-8_0_4_line_61 |  | 55 | 56 | 0.021761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2325-8_0_4_line_62 |  | 56 | 57 | 0.0038242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2325-8_0_4_line_63 |  | 57 | 58 | 0.011894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2325-8_0_4_line_64 |  | 58 | 60 | 0.0055188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2325-8_0_4_line_65 |  | 59 | 60 | 0.006939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2325-8_0_4_line_66 |  | 59 | 61 | 0.0085706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2325-8_0_4_line_67 |  | 62 | 65 | 0.0075424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2325-8_0_4_line_68 |  | 63 | 66 | 0.0085618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_2325-8_0_4_line_69 |  | 64 | 67 | 0.0025751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2325-8_0_4_line_70 |  | 65 | 68 | 0.02061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2325-8_0_4_line_71 |  | 66 | 69 | 0.035619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2325-8_0_4_line_72 |  | 67 | 70 | 0.034375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2325-8_0_4_line_73 |  | 69 | 71 | 0.032698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2325-8_0_4_line_74 |  | 69 | 72 | 0.025324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2325-8_0_4_line_75 |  | 69 | 73 | 0.058357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2325-8_0_4_line_76 |  | 70 | 74 | 0.0021314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2325-8_0_4_line_77 |  | 71 | 96 | 0.0091909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2325-8_0_4_line_78 |  | 73 | 93 | 0.019515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2325-8_0_4_line_79 |  | 73 | 92 | 0.021495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2325-8_0_4_line_80 |  | 74 | 78 | 0.02015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2325-8_0_4_line_81 |  | 75 | 76 | 0.018777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2325-8_0_4_line_82 |  | 77 | 98 | 0.016271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2325-8_0_4_line_83 |  | 77 | 99 | 0.011759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2325-8_0_4_line_84 |  | 78 | 79 | 0.0073489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2325-8_0_4_line_85 |  | 79 | 80 | 0.0073029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2325-8_0_4_line_86 |  | 80 | 81 | 0.022675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2325-8_0_4_line_87 |  | 81 | 106 | 0.02391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2325-8_0_4_line_88 |  | 82 | 83 | 0.039623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2325-8_0_4_line_89 |  | 83 | 84 | 0.036951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2325-8_0_4_line_90 |  | 84 | 88 | 0.0059501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2325-8_0_4_line_91 |  | 85 | 86 | 0.010729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2325-8_0_4_line_92 |  | 85 | 87 | 0.011752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2325-8_0_4_line_93 |  | 88 | 89 | 0.01706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2325-8_0_4_line_94 |  | 89 | 90 | 0.010064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2325-8_0_4_line_95 |  | 90 | 91 | 0.006802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2325-8_0_4_line_96 |  | 91 | 92 | 0.016563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2325-8_0_4_line_97 |  | 93 | 94 | 0.0035145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2325-8_0_4_line_98 |  | 94 | 95 | 0.021194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2325-8_0_4_line_99 |  | 95 | 97 | 0.0039604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2325-8_0_4_line_100 |  | 96 | 107 | 0.014431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2325-8_0_4_line_101 |  | 97 | 115 | 0.027993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2325-8_0_4_line_102 |  | 98 | 100 | 0.0074042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2325-8_0_4_line_103 |  | 99 | 101 | 0.034814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2325-8_0_4_line_104 |  | 100 | 102 | 0.037982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2325-8_0_4_line_105 |  | 100 | 103 | 0.055975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2325-8_0_4_line_106 |  | 101 | 104 | 0.0029092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2325-8_0_4_line_107 |  | 104 | 105 | 0.025278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2325-8_0_4_line_108 |  | 107 | 127 | 0.036454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2325-8_0_4_line_109 |  | 108 | 109 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2325-8_0_4_line_110 |  | 108 | 110 | 0.017059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2325-8_0_4_line_111 |  | 109 | 111 | 0.01953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2325-8_0_4_line_112 |  | 111 | 112 | 0.010999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2325-8_0_4_line_113 |  | 112 | 113 | 0.0038221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2325-8_0_4_line_114 |  | 113 | 114 | 0.026375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2325-8_0_4_line_115 |  | 114 | 121 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2325-8_0_4_line_116 |  | 114 | 122 | 0.021368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2325-8_0_4_line_117 |  | 114 | 120 | 0.05158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2325-8_0_4_line_118 |  | 115 | 116 | 0.037255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2325-8_0_4_line_119 |  | 116 | 117 | 0.041627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2325-8_0_4_line_120 |  | 117 | 118 | 0.010123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2325-8_0_4_line_121 |  | 117 | 119 | 0.022613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2325-8_0_4_line_122 |  | 118 | 124 | 0.023804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2325-8_0_4_line_123 |  | 119 | 125 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2325-8_0_4_line_124 |  | 119 | 123 | 0.002281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2325-8_0_4_line_125 |  | 122 | 123 | 0.017517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2325-8_0_4_line_126 |  | 125 | 126 | 0.0026857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2325-8_0_4_line_127 |  | 126 | 128 | 0.025706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2325-8_0_4_trafo_47 | 0.63 MVA 20/0.4 kV | 129 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2559140.6924 | 1152946.1502 | 2559143.6038 | 1152953.0196
1 | 2559140.6924 | 1152946.1502 | 2559132.2538 | 1152926.2393
2 | 2559129.5427 | 1152919.8423 | 2559132.2538 | 1152926.2393
3 | 2559121.5739 | 1152901.04 | 2559129.5427 | 1152919.8423
4 | 2559121.5739 | 1152901.04 | 2559116.8579 | 1152889.9125
5 | 2559109.8228 | 1152873.3132 | 2559116.8579 | 1152889.9125
6 | 2559109.8228 | 1152873.3132 | 2559117.8977 | 1152871.7772
7 | 2558933.2204 | 1152789.5503 | 2558941.605 | 1152779.9793 | 2558952.8421 | 1152768.565
8 | 2558924.9005 | 1152799.0477 | 2558933.2204 | 1152789.5503
9 | 2558960.5566 | 1152760.7288 | 2558952.8421 | 1152768.565
10 | 2558924.9005 | 1152799.0477 | 2558917.0948 | 1152808.8394 | 2558905.0036 | 1152828.1431
11 | 2558924.9005 | 1152799.0477 | 2558938.4123 | 1152811.4912
12 | 2558960.5566 | 1152760.7288 | 2558962.1394 | 1152759.6297
13 | 2558960.5566 | 1152760.7288 | 2558982.1731 | 1152785.8757
14 | 2558905.0036 | 1152828.1431 | 2558900.4809 | 1152842.2479 | 2558899.2896 | 1152845.5508
15 | 2558897.833 | 1152800.6669 | 2558900.8817 | 1152811.1292 | 2558905.0036 | 1152828.1431
16 | 2558942.8198 | 1152815.5501 | 2558938.4123 | 1152811.4912
17 | 2558977.4368 | 1152749.0066 | 2558962.1394 | 1152759.6297
18 | 2558983.2936 | 1152787.1792 | 2558982.1731 | 1152785.8757
19 | 2558898.2173 | 1152848.5236 | 2558899.2896 | 1152845.5508
20 | 2558897.833 | 1152800.6669 | 2558883.0874 | 1152804.2805
21 | 2558897.833 | 1152800.6669 | 2558895.7829 | 1152792.6211
22 | 2558950.8302 | 1152822.9271 | 2558942.8198 | 1152815.5501
23 | 2558997.8266 | 1152736.7068 | 2558983.7731 | 1152744.6064 | 2558977.4368 | 1152749.0066
24 | 2558889.9467 | 1152866.4176 | 2558893.8242 | 1152860.7029 | 2558898.2173 | 1152848.5236
25 | 2558870.7525 | 1152807.3034 | 2558883.0874 | 1152804.2805
26 | 2558895.7829 | 1152792.6211 | 2558894.5134 | 1152787.6385 | 2558887.3021 | 1152766.8647
27 | 2559031.6176 | 1152714.5201 | 2559011.681 | 1152728.9191 | 2558997.8266 | 1152736.7068
28 | 2558884.4122 | 1152874.5744 | 2558889.9467 | 1152866.4176
29 | 2558857.2793 | 1152810.6052 | 2558870.7525 | 1152807.3034
30 | 2558887.3021 | 1152766.8647 | 2558881.7522 | 1152750.877
31 | 2558969.8316 | 1152888.0196 | 2558968.2534 | 1152886.5741 | 2558941.4967 | 1152875.3846
32 | 2558937.1807 | 1152873.5797 | 2558941.4967 | 1152875.3846
33 | 2558969.8316 | 1152888.0196 | 2558981.1975 | 1152898.4296
34 | 2558937.1807 | 1152873.5797 | 2558937.1807 | 1152873.5797 | 2558926.2834 | 1152871.1085 | 2558925.308 | 1152871.1091
35 | 2558981.6083 | 1152898.8059 | 2558981.1975 | 1152898.4296
36 | 2558919.4984 | 1152871.1128 | 2558925.308 | 1152871.1091
37 | 2559004.2039 | 1152919.5011 | 2558981.6083 | 1152898.8059
38 | 2558884.4122 | 1152874.5744 | 2558892.9391 | 1152872.6373 | 2558906.3397 | 1152874.2687 | 2558915.5489 | 1152871.1152 | 2558919.4984 | 1152871.1128
39 | 2559046.2796 | 1152889.81 | 2559034.9207 | 1152893.8896 | 2559004.2039 | 1152919.5011
40 | 2559046.2796 | 1152889.81 | 2559056.9832 | 1152912.5708
41 | 2559056.9832 | 1152912.5708 | 2559058.3551 | 1152915.4882
42 | 2559058.3551 | 1152915.4882 | 2559068.3124 | 1152936.6621
43 | 2559078.8791 | 1152957.4373 | 2559070.011 | 1152940.2742 | 2559068.3124 | 1152936.6621
44 | 2559246.1256 | 1152782.2858 | 2559356.3034 | 1152729.7888
45 | 2559246.1256 | 1152782.2858 | 2559257.2409 | 1152803.6445
46 | 2559242.0355 | 1152774.4265 | 2559246.1256 | 1152782.2858
47 | 2559257.2409 | 1152803.6445 | 2559267.9036 | 1152824.1335
48 | 2559242.0355 | 1152774.4265 | 2559240.6782 | 1152771.8184
49 | 2559192.3769 | 1152720.8182 | 2559223.0481 | 1152737.941
50 | 2559192.3769 | 1152720.8182 | 2559191.2659 | 1152718.4451
51 | 2559223.0481 | 1152737.941 | 2559230.3001 | 1152751.8762
52 | 2559191.2659 | 1152718.4451 | 2559190.3921 | 1152716.5786
53 | 2559230.8142 | 1152895.1577 | 2559268.9113 | 1152891.8421
54 | 2559230.3036 | 1152895.241 | 2559230.8142 | 1152895.1577
55 | 2559031.6176 | 1152714.5201 | 2559023.1893 | 1152698.336 | 2559020.7603 | 1152690.9599
56 | 2559031.6176 | 1152714.5201 | 2559065.0398 | 1152701.7636 | 2559065.0398 | 1152701.7636
57 | 2559031.6176 | 1152714.5201 | 2559043.0173 | 1152742.1921
58 | 2558876.5652 | 1152735.9415 | 2558877.0735 | 1152737.3988 | 2558877.8903 | 1152739.7519
59 | 2558881.7522 | 1152750.877 | 2558877.8903 | 1152739.7519
60 | 2558876.5652 | 1152735.9415 | 2558869.484 | 1152715.6382
61 | 2558869.484 | 1152715.6382 | 2558862.3176 | 1152695.0908
62 | 2558862.3176 | 1152695.0908 | 2558861.0582 | 1152691.4799
63 | 2558855.4635 | 1152681.1589 | 2558859.1027 | 1152685.8732 | 2558861.0582 | 1152691.4799
64 | 2558852.0912 | 1152676.7904 | 2558855.4635 | 1152681.1589
65 | 2558847.851 | 1152671.2977 | 2558852.0912 | 1152676.7904
66 | 2558847.851 | 1152671.2977 | 2558842.6137 | 1152664.5133
67 | 2559020.7603 | 1152690.9599 | 2559018.2607 | 1152683.8437
68 | 2559065.0398 | 1152701.7636 | 2559071.4816 | 1152696.1238
69 | 2559043.9982 | 1152744.5731 | 2559043.0173 | 1152742.1921
70 | 2559011.4303 | 1152664.3983 | 2559018.2607 | 1152683.8437
71 | 2559091.9767 | 1152667.3958 | 2559085.951 | 1152679.4653 | 2559075.444 | 1152692.6547 | 2559071.4816 | 1152696.1238
72 | 2559052.6497 | 1152777.2852 | 2559052.3876 | 1152764.9377 | 2559043.9982 | 1152744.5731
73 | 2559091.9767 | 1152667.3958 | 2559096.7974 | 1152681.1812 | 2559097.1219 | 1152691.6399 | 2559099.4594 | 1152698.9033
74 | 2559091.9767 | 1152667.3958 | 2559088.4175 | 1152642.3231
75 | 2559091.9767 | 1152667.3958 | 2559095.1485 | 1152661.0377 | 2559098.9057 | 1152644.8593 | 2559130.2142 | 1152659.6872
76 | 2559052.6497 | 1152777.2852 | 2559052.6949 | 1152779.4161
77 | 2559099.4594 | 1152698.9033 | 2559102.2751 | 1152707.6523
78 | 2559130.2142 | 1152659.6872 | 2559137.9974 | 1152677.5829
79 | 2559130.2142 | 1152659.6872 | 2559135.6439 | 1152638.8897
80 | 2559053.1224 | 1152799.5616 | 2559052.6949 | 1152779.4161
81 | 2559087.4985 | 1152974.1193 | 2559078.8791 | 1152957.4373
82 | 2558857.2793 | 1152810.6052 | 2558858.3357 | 1152818.0795 | 2558849.9736 | 1152820.5599
83 | 2558857.2793 | 1152810.6052 | 2558854.0096 | 1152799.3097
84 | 2559056.429 | 1152806.1246 | 2559053.1224 | 1152799.5616 | 2559053.1224 | 1152799.5616
85 | 2559056.429 | 1152806.1246 | 2559059.7149 | 1152812.6465
86 | 2559059.7149 | 1152812.6465 | 2559069.9172 | 1152832.8963
87 | 2559055.6854 | 1152843.9859 | 2559072.6306 | 1152838.2818 | 2559069.9172 | 1152832.8963
88 | 2559190.3921 | 1152716.5786 | 2559178.5873 | 1152691.3635 | 2559174.8571 | 1152680.1882
89 | 2559163.1576 | 1152645.138 | 2559174.8571 | 1152680.1882
90 | 2559163.1576 | 1152645.138 | 2559161.2737 | 1152639.4941
91 | 2559230.3001 | 1152751.8762 | 2559235.2532 | 1152761.3939
92 | 2559235.2532 | 1152761.3939 | 2559240.6782 | 1152771.8184
93 | 2559161.2737 | 1152639.4941 | 2559155.9032 | 1152623.405 | 2559155.8114 | 1152623.37
94 | 2559146.4096 | 1152619.7788 | 2559146.4096 | 1152619.7788 | 2559155.8114 | 1152623.37
95 | 2559146.4096 | 1152619.7788 | 2559140.7186 | 1152623.5043
96 | 2559135.6439 | 1152638.8897 | 2559139.4425 | 1152624.3397 | 2559140.7186 | 1152623.5043
97 | 2559139.3991 | 1152680.8057 | 2559137.9974 | 1152677.5829
98 | 2559147.8518 | 1152700.2409 | 2559139.3991 | 1152680.8057
99 | 2559147.8518 | 1152700.2409 | 2559149.4314 | 1152703.8727
100 | 2559102.2751 | 1152707.6523 | 2559102.4839 | 1152708.3008 | 2559108.1803 | 1152720.8154
101 | 2559160.5958 | 1152729.5426 | 2559149.4314 | 1152703.8727
102 | 2558842.8751 | 1152822.6656 | 2558849.9736 | 1152820.5599
103 | 2558834.9142 | 1152775.0092 | 2558838.1407 | 1152789.0696 | 2558852.6739 | 1152794.6952 | 2558854.0096 | 1152799.3097
104 | 2558848.3734 | 1152860.2472 | 2558842.8751 | 1152822.6656
105 | 2558842.8751 | 1152822.6656 | 2558786.9039 | 1152823.294
106 | 2558834.9142 | 1152775.0092 | 2558834.2635 | 1152772.1737
107 | 2558828.6098 | 1152747.5359 | 2558834.2635 | 1152772.1737
108 | 2559123.2825 | 1152753.9938 | 2559108.1803 | 1152720.8154
109 | 2559213.4669 | 1152897.9878 | 2559195.4106 | 1152900.9335
110 | 2559230.3036 | 1152895.241 | 2559213.4669 | 1152897.9878
111 | 2559176.1354 | 1152904.078 | 2559195.4106 | 1152900.9335
112 | 2559174.1772 | 1152893.2552 | 2559176.1354 | 1152904.078 | 2559176.1354 | 1152904.078
113 | 2559174.1772 | 1152893.2552 | 2559173.4966 | 1152889.4943
114 | 2559168.8006 | 1152863.5404 | 2559173.4966 | 1152889.4943
115 | 2559168.8006 | 1152863.5404 | 2559183.3575 | 1152861.1463
116 | 2559168.8006 | 1152863.5404 | 2559162.678 | 1152843.0681
117 | 2559168.8006 | 1152863.5404 | 2559139.9467 | 1152867.5831 | 2559117.8977 | 1152871.7772
118 | 2559160.5958 | 1152729.5426 | 2559163.2503 | 1152735.646 | 2559169.3633 | 1152752.2018 | 2559169.3013 | 1152760.0062 | 2559168.0389 | 1152764.9956
119 | 2559150.9054 | 1152802.3974 | 2559152.0647 | 1152795.7306 | 2559155.1017 | 1152787.5946 | 2559159.6161 | 1152780.0823 | 2559163.9031 | 1152774.0946 | 2559167.4332 | 1152767.3893 | 2559168.0389 | 1152764.9956
120 | 2559150.9054 | 1152802.3974 | 2559143.9438 | 1152804.3458 | 2559141.0644 | 1152804.0541 | 2559141.0644 | 1152804.0541
121 | 2559157.0074 | 1152824.1004 | 2559155.9866 | 1152820.6722 | 2559152.2237 | 1152810.0702 | 2559150.9054 | 1152802.3974
122 | 2559141.0644 | 1152804.0541 | 2559139.0862 | 1152800.8881 | 2559132.8477 | 1152781.8114
123 | 2559157.0074 | 1152824.1004 | 2559170.3962 | 1152820.9856
124 | 2559157.0074 | 1152824.1004 | 2559157.6591 | 1152826.286
125 | 2559157.6591 | 1152826.286 | 2559162.678 | 1152843.0681
126 | 2559170.3962 | 1152820.9856 | 2559173.0121 | 1152820.3771
127 | 2559198.0498 | 1152814.5523 | 2559173.0121 | 1152820.3771

## bus_geodata
| x | y | coords
0 | 2559140.6924 | 1152946.1502
1 | 2559143.6038 | 1152953.0196
2 | 2559132.2538 | 1152926.2393
3 | 2559129.5427 | 1152919.8423
4 | 2559121.5739 | 1152901.04
5 | 2559116.8579 | 1152889.9125
6 | 2559109.8228 | 1152873.3132
7 | 2558933.2204 | 1152789.5503
8 | 2558952.8421 | 1152768.565
9 | 2558924.9005 | 1152799.0477
10 | 2558960.5566 | 1152760.7288
11 | 2558905.0036 | 1152828.1431
12 | 2558938.4123 | 1152811.4912
13 | 2558962.1394 | 1152759.6297
14 | 2558982.1731 | 1152785.8757
15 | 2558899.2896 | 1152845.5508
16 | 2558897.833 | 1152800.6669
17 | 2558942.8198 | 1152815.5501
18 | 2558977.4368 | 1152749.0066
19 | 2558983.2936 | 1152787.1792
20 | 2558898.2173 | 1152848.5236
21 | 2558883.0874 | 1152804.2805
22 | 2558895.7829 | 1152792.6211
23 | 2558950.8302 | 1152822.9271
24 | 2558997.8266 | 1152736.7068
25 | 2558889.9467 | 1152866.4176
26 | 2558870.7525 | 1152807.3034
27 | 2558887.3021 | 1152766.8647
28 | 2558941.4967 | 1152875.3846
29 | 2558969.8316 | 1152888.0196
30 | 2558937.1807 | 1152873.5797
31 | 2558981.1975 | 1152898.4296
32 | 2558925.308 | 1152871.1091
33 | 2558981.6083 | 1152898.8059
34 | 2558919.4984 | 1152871.1128
35 | 2559004.2039 | 1152919.5011
36 | 2558884.4122 | 1152874.5744
37 | 2559046.2796 | 1152889.81
38 | 2559056.9832 | 1152912.5708
39 | 2559058.3551 | 1152915.4882
40 | 2559068.3124 | 1152936.6621
41 | 2559356.3034 | 1152729.7888
42 | 2559246.1256 | 1152782.2858
43 | 2559257.2409 | 1152803.6445
44 | 2559242.0355 | 1152774.4265
45 | 2559192.3769 | 1152720.8182
46 | 2559223.0481 | 1152737.941
47 | 2559191.2659 | 1152718.4451
48 | 2559267.9036 | 1152824.1335
49 | 2559268.9113 | 1152891.8421
50 | 2559230.8142 | 1152895.1577
51 | 2559031.6176 | 1152714.5201
52 | 2558877.8903 | 1152739.7519
53 | 2558876.5652 | 1152735.9415
54 | 2558881.7522 | 1152750.877
55 | 2558869.484 | 1152715.6382
56 | 2558862.3176 | 1152695.0908
57 | 2558861.0582 | 1152691.4799
58 | 2558855.4635 | 1152681.1589
59 | 2558847.851 | 1152671.2976
60 | 2558852.0912 | 1152676.7904
61 | 2558842.6137 | 1152664.5133
62 | 2559020.7603 | 1152690.9599
63 | 2559065.0398 | 1152701.7636
64 | 2559043.0173 | 1152742.1921
65 | 2559018.2607 | 1152683.8437
66 | 2559071.4816 | 1152696.1238
67 | 2559043.9982 | 1152744.5731
68 | 2559011.4303 | 1152664.3983
69 | 2559091.9767 | 1152667.3958
70 | 2559052.6497 | 1152777.2852
71 | 2559099.4594 | 1152698.9033
72 | 2559088.4175 | 1152642.3231
73 | 2559130.2142 | 1152659.6872
74 | 2559052.6949 | 1152779.4161
75 | 2559087.4985 | 1152974.1193
76 | 2559078.8791 | 1152957.4373
77 | 2558857.2793 | 1152810.6052
78 | 2559053.1224 | 1152799.5616
79 | 2559056.429 | 1152806.1246
80 | 2559059.7149 | 1152812.6465
81 | 2559069.9172 | 1152832.8963
82 | 2559190.3921 | 1152716.5786
83 | 2559174.8571 | 1152680.1882
84 | 2559163.1576 | 1152645.138
85 | 2559235.2532 | 1152761.3939
86 | 2559230.3001 | 1152751.8762
87 | 2559240.6782 | 1152771.8184
88 | 2559161.2737 | 1152639.4941
89 | 2559155.8114 | 1152623.37
90 | 2559146.4096 | 1152619.7788
91 | 2559140.7186 | 1152623.5043
92 | 2559135.6439 | 1152638.8897
93 | 2559137.9974 | 1152677.5829
94 | 2559139.3991 | 1152680.8057
95 | 2559147.8518 | 1152700.2409
96 | 2559102.2751 | 1152707.6523
97 | 2559149.4314 | 1152703.8727
98 | 2558849.9736 | 1152820.5599
99 | 2558854.0096 | 1152799.3097
100 | 2558842.8751 | 1152822.6656
101 | 2558834.9142 | 1152775.0092
102 | 2558848.3734 | 1152860.2472
103 | 2558786.9039 | 1152823.294
104 | 2558834.2635 | 1152772.1737
105 | 2558828.6098 | 1152747.5359
106 | 2559055.6854 | 1152843.9859
107 | 2559108.1803 | 1152720.8154
108 | 2559213.4669 | 1152897.9878
109 | 2559195.4106 | 1152900.9335
110 | 2559230.3036 | 1152895.241
111 | 2559176.1354 | 1152904.078
112 | 2559174.1772 | 1152893.2553
113 | 2559173.4966 | 1152889.4943
114 | 2559168.8006 | 1152863.5404
115 | 2559160.5958 | 1152729.5426
116 | 2559168.0389 | 1152764.9956
117 | 2559150.9054 | 1152802.3974
118 | 2559141.0644 | 1152804.0541
119 | 2559157.0074 | 1152824.1004
120 | 2559117.8977 | 1152871.7772
121 | 2559183.3575 | 1152861.1463
122 | 2559162.678 | 1152843.0681
123 | 2559157.6591 | 1152826.286
124 | 2559132.8477 | 1152781.8114
125 | 2559170.3962 | 1152820.9856
126 | 2559173.0121 | 1152820.3771
127 | 2559123.2825 | 1152753.9938
128 | 2559198.0498 | 1152814.5523
129 | 2559031.6176 | 1152714.5201

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9701 | -0.57788 | 0.0044029 | 0.0011035
1 | 0.97008 | -0.57823 | 0.0025429 | 0.00063732
2 | 0.97024 | -0.5751 | 0.0012484 | 0.00031288
3 | 0.9703 | -0.57405 | 0.0039262 | 0.00098399
4 | 0.97053 | -0.56947 | 0.0018353 | 0.00045998
5 | 0.97068 | -0.56634 | 0.0033504 | 0.00083968
6 | 0.97098 | -0.56057 | 0 | 0
7 | 0.99284 | -0.13615 | 0.0025457 | 0.00063801
8 | 0.99515 | -0.092121 | 0.0025814 | 0.00064695
9 | 0.99184 | -0.15528 | 0 | 0
10 | 0.99604 | -0.075079 | 0.0019157 | 0.00048012
11 | 0.98914 | -0.20726 | 0 | 0
12 | 0.99175 | -0.15699 | 0.0016626 | 0.00041668
13 | 0.99621 | -0.07194 | 0.0042337 | 0.0010611
14 | 0.99582 | -0.079316 | 0.0030197 | 0.00075681
15 | 0.98841 | -0.22137 | 0.001111 | 0.00027843
16 | 0.98591 | -0.26954 | 0 | 0
17 | 0.99173 | -0.15737 | 0.0015181 | 0.00038047
18 | 0.99784 | -0.040968 | 0.0070997 | 0.0017793
19 | 0.99581 | -0.079444 | 0.00425 | 0.0010652
20 | 0.98829 | -0.22374 | 0.0025372 | 0.00063588
21 | 0.98549 | -0.27787 | 0.0022628 | 0.00056712
22 | 0.98521 | -0.28326 | 0.0083521 | 0.0020932
23 | 0.99171 | -0.15777 | 0.0020674 | 0.00051813
24 | 1 | 0 | -0.42971 | -0.10963
25 | 0.98756 | -0.23777 | 0.0027041 | 0.00067772
26 | 0.98516 | -0.28433 | 0.0055919 | 0.0014015
27 | 0.9831 | -0.32415 | 0.0065351 | 0.0016379
28 | 0.98541 | -0.27969 | 0.00104 | 0.00026065
29 | 0.9847 | -0.29357 | 0.0015383 | 0.00038553
30 | 0.98552 | -0.27752 | 0.0033799 | 0.0008471
31 | 0.98436 | -0.30002 | 0.0061238 | 0.0015348
32 | 0.98585 | -0.27115 | 0.0013289 | 0.00033306
33 | 0.98436 | -0.3002 | 0.0039998 | 0.0010024
34 | 0.98601 | -0.26797 | 0.0062868 | 0.0015756
35 | 0.98398 | -0.30745 | 0 | 0
36 | 0.98723 | -0.24426 | 0 | 0
37 | 0.98335 | -0.31975 | 0 | 0
38 | 0.98305 | -0.32572 | 0.0025909 | 0.00064934
39 | 0.98302 | -0.32633 | 0.0033697 | 0.00084453
40 | 0.98286 | -0.32936 | 0.0025796 | 0.00064651
41 | 0.97836 | -0.41612 | 0.0017301 | 0.0004336
42 | 0.97856 | -0.41227 | 0.00057748 | 0.00014473
43 | 0.97844 | -0.41451 | 0.0029689 | 0.00074407
44 | 0.97862 | -0.41108 | 0.00060728 | 0.0001522
45 | 0.97948 | -0.39408 | 0.00027306 | 6.8436e-05
46 | 0.97906 | -0.40243 | 0.00067794 | 0.00016991
47 | 0.97951 | -0.39345 | 0.00040588 | 0.00010172
48 | 0.9784 | -0.4154 | 0.0021289 | 0.00053356
49 | 0.97102 | -0.55976 | 0.0023026 | 0.00057709
50 | 0.9711 | -0.55813 | 0.0021345 | 0.00053495
51 | 0.9958 | -0.079799 | 0 | 0
52 | 0.98111 | -0.36305 | 0.0025566 | 0.00064074
53 | 0.98085 | -0.36811 | 0.0033875 | 0.00084898
54 | 0.98189 | -0.34775 | 0.0054133 | 0.0013567
55 | 0.97954 | -0.39379 | 0.0028554 | 0.00071564
56 | 0.97827 | -0.41873 | 0.054035 | 0.013543
57 | 0.97823 | -0.41935 | 0.0018245 | 0.00045727
58 | 0.97816 | -0.4209 | 0.0014404 | 0.00036099
59 | 0.9781 | -0.42189 | 0.0018128 | 0.00045434
60 | 0.97813 | -0.42147 | 0.0023684 | 0.00059357
61 | 0.97809 | -0.42213 | 0.001516 | 0.00037996
62 | 0.99433 | -0.10811 | 0 | 0
63 | 0.9934 | -0.12531 | 0.0090659 | 0.0022721
64 | 0.99528 | -0.089772 | 0.0030405 | 0.00076202
65 | 0.9939 | -0.11634 | 0.033241 | 0.008331
66 | 0.99287 | -0.13555 | 0.0022753 | 0.00057024
67 | 0.99524 | -0.090493 | 0.0018541 | 0.00046469
68 | 0.99337 | -0.12675 | 0.028609 | 0.0071702
69 | 0.98847 | -0.21973 | 0 | 0
70 | 0.9948 | -0.098997 | 0.0023672 | 0.00059327
71 | 0.98835 | -0.22212 | 0.00089046 | 0.00022317
72 | 0.98784 | -0.23202 | 0.027178 | 0.0068116
73 | 0.98295 | -0.32631 | 0 | 0
74 | 0.99478 | -0.099436 | 0.0014291 | 0.00035816
75 | 0.98271 | -0.33236 | 0.0031342 | 0.00078551
76 | 0.98276 | -0.3313 | 0.00147 | 0.00036841
77 | 0.98487 | -0.28999 | 0 | 0
78 | 0.99459 | -0.10308 | 0.0021281 | 0.00053336
79 | 0.99454 | -0.10413 | 0.00080562 | 0.00020191
80 | 0.99449 | -0.10507 | 0.0020338 | 0.00050973
81 | 0.99438 | -0.10718 | 0.0018153 | 0.00045497
82 | 0.97954 | -0.39293 | 0.0013283 | 0.0003329
83 | 0.98009 | -0.38208 | 0.0034025 | 0.00085275
84 | 0.98073 | -0.36969 | 0.0033215 | 0.00083245
85 | 0.97876 | -0.40828 | 0.00072086 | 0.00018066
86 | 0.97888 | -0.40597 | 0.00059418 | 0.00014892
87 | 0.97864 | -0.41065 | 0.0030621 | 0.00076744
88 | 0.98085 | -0.36734 | 0.0049921 | 0.0012511
89 | 0.98127 | -0.35906 | 0.0021137 | 0.00052975
90 | 0.98154 | -0.3538 | 0.0017635 | 0.00044197
91 | 0.98173 | -0.35002 | 0.0017661 | 0.00044264
92 | 0.98223 | -0.34031 | 0.0036369 | 0.0009115
93 | 0.98175 | -0.34947 | 0.0032201 | 0.00080702
94 | 0.98155 | -0.35344 | 0.0023238 | 0.0005824
95 | 0.98036 | -0.37654 | 0.0023252 | 0.00058275
96 | 0.98832 | -0.22264 | 0.00081034 | 0.00020309
97 | 0.98014 | -0.3807 | 0.0012139 | 0.00030424
98 | 0.9847 | -0.29328 | 0.0013992 | 0.00035066
99 | 0.98474 | -0.29242 | 0.0021794 | 0.00054622
100 | 0.98463 | -0.29459 | 0.0032865 | 0.00082369
101 | 0.98444 | -0.29824 | 0.0044537 | 0.0011162
102 | 0.98457 | -0.2957 | 0.0016218 | 0.00040647
103 | 0.98438 | -0.29956 | 0.0049323 | 0.0012362
104 | 0.98443 | -0.2985 | 0.002016 | 0.00050525
105 | 0.98436 | -0.29978 | 0.0028325 | 0.0007099
106 | 0.9943 | -0.10865 | 0.0034706 | 0.00086981
107 | 0.98829 | -0.22326 | 0.0010138 | 0.00025408
108 | 0.97121 | -0.55588 | 0.0015536 | 0.00038938
109 | 0.97136 | -0.55299 | 0.0026594 | 0.0006665
110 | 0.9711 | -0.55809 | 0.0025662 | 0.00064315
111 | 0.97156 | -0.54894 | 0.0026689 | 0.00066889
112 | 0.97171 | -0.54612 | 0.0010955 | 0.00027456
113 | 0.97176 | -0.54506 | 0.0012433 | 0.00031161
114 | 0.97216 | -0.53717 | 0 | 0
115 | 0.97866 | -0.4095 | 0.0012849 | 0.00032203
116 | 0.97674 | -0.4471 | 0.0010407 | 0.00026083
117 | 0.97463 | -0.48849 | 0 | 0
118 | 0.97455 | -0.49014 | 0.0045138 | 0.0011313
119 | 0.97367 | -0.50736 | 0 | 0
120 | 0.97111 | -0.55794 | 0.004507 | 0.0011296
121 | 0.97215 | -0.53741 | 0.00088503 | 0.00022181
122 | 0.97294 | -0.52184 | 0.00082707 | 0.00020728
123 | 0.97359 | -0.50902 | 0 | 0
124 | 0.97445 | -0.49205 | 0.0043706 | 0.0010954
125 | 0.9736 | -0.50879 | 0.00097959 | 0.00024551
126 | 0.97359 | -0.50902 | 0.00083202 | 0.00020852
127 | 0.98824 | -0.22415 | 0.0013722 | 0.00034391
128 | 0.9735 | -0.51084 | 0.0038467 | 0.00096407
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.002543 | 0.00063726 | -0.0025429 | -0.00063732 | 4.2568e-08 | -6.487e-08 | 0.0039006 | 0.0039006 | 0.0039006 | 0.9701 | -0.57788 | 0.97008 | -0.57823 | 1.0716
1 | -0.0069459 | -0.0017407 | 0.0069468 | 0.0017411 | 9.2051e-07 | 3.2209e-07 | 0.010654 | 0.010654 | 0.010654 | 0.9701 | -0.57788 | 0.97024 | -0.5751 | 2.927
2 | -0.0081952 | -0.0020539 | 0.0081957 | 0.0020541 | 4.1158e-07 | 1.776e-07 | 0.012569 | 0.012569 | 0.012569 | 0.97024 | -0.5751 | 0.9703 | -0.57405 | 3.4529
3 | -0.012122 | -0.0030381 | 0.012124 | 0.0030395 | 2.6464e-06 | 1.4414e-06 | 0.01859 | 0.01859 | 0.01859 | 0.9703 | -0.57405 | 0.97053 | -0.56947 | 5.1071
4 | -0.01396 | -0.0034995 | 0.013962 | 0.0035007 | 2.0762e-06 | 1.1794e-06 | 0.021404 | 0.021404 | 0.021404 | 0.97053 | -0.56947 | 0.97068 | -0.56634 | 5.8801
5 | -0.017312 | -0.0043404 | 0.017317 | 0.0043432 | 4.7618e-06 | 2.8246e-06 | 0.026539 | 0.026539 | 0.026539 | 0.97068 | -0.56634 | 0.97098 | -0.56057 | 7.2911
6 | -0.017317 | -0.0043432 | 0.017319 | 0.0043445 | 2.171e-06 | 1.2878e-06 | 0.026539 | 0.026539 | 0.026539 | 0.97098 | -0.56057 | 0.97111 | -0.55794 | 7.291
7 | -0.17535 | -0.044596 | 0.17573 | 0.044834 | 0.00037288 | 0.00023789 | 0.26304 | 0.26304 | 0.26304 | 0.99284 | -0.13615 | 0.99515 | -0.092121 | 36.1321
8 | 0.17281 | 0.043958 | -0.17265 | -0.043856 | 0.00015909 | 0.00010149 | 0.25923 | 0.25923 | 0.25923 | 0.99284 | -0.13615 | 0.99184 | -0.15528 | 35.6081
9 | -0.17831 | -0.045481 | 0.17846 | 0.045574 | 0.00014688 | 9.3715e-05 | 0.2669 | 0.2669 | 0.2669 | 0.99515 | -0.092121 | 0.99604 | -0.075079 | 36.6623
10 | 0.1674 | 0.042541 | -0.16698 | -0.042275 | 0.00041784 | 0.00026651 | 0.25135 | 0.25135 | 0.25135 | 0.99184 | -0.15528 | 0.98914 | -0.20726 | 34.5265
11 | 0.0052486 | 0.0013152 | -0.0052481 | -0.0013151 | 4.2709e-07 | 3.6289e-08 | 0.0078741 | 0.0078742 | 0.0078742 | 0.99184 | -0.15528 | 0.99175 | -0.15699 | 2.1632
12 | -0.18764 | -0.047877 | 0.18767 | 0.047895 | 2.8453e-05 | 1.816e-05 | 0.28063 | 0.28063 | 0.28063 | 0.99604 | -0.075079 | 0.99621 | -0.07194 | 38.5475
13 | 0.0072712 | 0.0018225 | -0.0072698 | -0.001822 | 1.4674e-06 | 5.0762e-07 | 0.010863 | 0.010863 | 0.010863 | 0.99604 | -0.075079 | 0.99582 | -0.079316 | 2.9843
14 | 0.043366 | 0.010931 | -0.043337 | -0.010913 | 2.9264e-05 | 1.8494e-05 | 0.06526 | 0.06526 | 0.06526 | 0.98914 | -0.20726 | 0.98841 | -0.22137 | 17.9287
15 | 0.12362 | 0.031343 | -0.12325 | -0.031108 | 0.00036889 | 0.00023573 | 0.18609 | 0.18609 | 0.18609 | 0.98914 | -0.20726 | 0.98591 | -0.26954 | 51.1244
16 | 0.0035856 | 0.00089845 | -0.0035855 | -0.00089849 | 6.5028e-08 | -3.5697e-08 | 0.0053797 | 0.0053797 | 0.0053797 | 0.99175 | -0.15699 | 0.99173 | -0.15737 | 1.4779
17 | -0.1919 | -0.048956 | 0.19219 | 0.04914 | 0.00028753 | 0.00018354 | 0.28695 | 0.28695 | 0.28695 | 0.99621 | -0.07194 | 0.99784 | -0.040968 | 39.4162
18 | 0.0042501 | 0.0010652 | -0.00425 | -0.0010652 | 2.5997e-08 | -5.7242e-09 | 0.0063507 | 0.0063507 | 0.0063507 | 0.99582 | -0.079316 | 0.99581 | -0.079444 | 1.7447
19 | 0.042226 | 0.010634 | -0.042221 | -0.010631 | 4.792e-06 | 3.0264e-06 | 0.063588 | 0.063588 | 0.063588 | 0.98841 | -0.22137 | 0.98829 | -0.22374 | 17.4692
20 | 0.030611 | 0.0076824 | -0.030599 | -0.0076748 | 1.2154e-05 | 7.585e-06 | 0.046204 | 0.046204 | 0.046204 | 0.98591 | -0.26954 | 0.98549 | -0.27787 | 12.6935
21 | 0.092637 | 0.023425 | -0.092576 | -0.023386 | 6.0929e-05 | 3.8889e-05 | 0.13989 | 0.13989 | 0.13989 | 0.98591 | -0.26954 | 0.98521 | -0.28326 | 38.431
22 | 0.0020674 | 0.00051801 | -0.0020674 | -0.00051813 | 3.9293e-08 | -1.1536e-07 | 0.0031019 | 0.003102 | 0.003102 | 0.99173 | -0.15737 | 0.99171 | -0.15777 | 0.85219
23 | -0.19929 | -0.050919 | 0.19969 | 0.051172 | 0.00039565 | 0.00025259 | 0.29754 | 0.29754 | 0.29754 | 0.99784 | -0.040968 | 1 | 0 | 40.8704
24 | 0.039684 | 0.0099954 | -0.039657 | -0.0099786 | 2.6595e-05 | 1.6767e-05 | 0.059768 | 0.059768 | 0.059768 | 0.98829 | -0.22374 | 0.98756 | -0.23777 | 16.4198
25 | 0.028336 | 0.0071077 | -0.028327 | -0.0071023 | 8.7189e-06 | 5.4184e-06 | 0.042787 | 0.042788 | 0.042788 | 0.98549 | -0.27787 | 0.98516 | -0.28433 | 11.7548
26 | 0.084224 | 0.021293 | -0.084059 | -0.021188 | 0.00016481 | 0.00010514 | 0.12727 | 0.12727 | 0.12727 | 0.98521 | -0.28326 | 0.9831 | -0.32415 | 34.9655
27 | 0.22837 | 0.058458 | -0.22749 | -0.057897 | 0.00087882 | 0.00056139 | 0.34025 | 0.34025 | 0.34025 | 1 | 0 | 0.9958 | -0.079799 | 46.7376
28 | 0.036953 | 0.0093009 | -0.036942 | -0.0092937 | 1.1466e-05 | 7.2118e-06 | 0.055693 | 0.055694 | 0.055694 | 0.98756 | -0.23777 | 0.98723 | -0.24426 | 15.3004
29 | 0.022735 | 0.0057008 | -0.022729 | -0.0056971 | 6.1348e-06 | 3.7497e-06 | 0.034341 | 0.034341 | 0.034341 | 0.98516 | -0.28433 | 0.98487 | -0.28999 | 9.4345
30 | 0.077524 | 0.01955 | -0.077436 | -0.019494 | 8.7445e-05 | 5.575e-05 | 0.11738 | 0.11738 | 0.11738 | 0.9831 | -0.32415 | 0.98189 | -0.34775 | 32.2481
31 | 0.024848 | 0.0062409 | -0.024832 | -0.0062308 | 1.6446e-05 | 1.0129e-05 | 0.037527 | 0.037527 | 0.037527 | 0.98541 | -0.27969 | 0.9847 | -0.29357 | 10.3095
32 | -0.025888 | -0.0065015 | 0.025891 | 0.0065032 | 2.6816e-06 | 1.6566e-06 | 0.039097 | 0.039097 | 0.039097 | 0.98541 | -0.27969 | 0.98552 | -0.27752 | 10.7409
33 | 0.023293 | 0.0058452 | -0.023286 | -0.0058408 | 7.1622e-06 | 4.3878e-06 | 0.035202 | 0.035202 | 0.035202 | 0.9847 | -0.29357 | 0.98436 | -0.30002 | 9.6709
34 | -0.029271 | -0.0073503 | 0.02928 | 0.0073558 | 8.901e-06 | 5.5418e-06 | 0.0442 | 0.0442 | 0.0442 | 0.98552 | -0.27752 | 0.98585 | -0.27115 | 12.1429
35 | 0.017162 | 0.0043061 | -0.017162 | -0.004306 | 1.4064e-07 | 8.2924e-08 | 0.025945 | 0.025945 | 0.025945 | 0.98436 | -0.30002 | 0.98436 | -0.3002 | 7.1278
36 | -0.030608 | -0.0076889 | 0.030613 | 0.0076918 | 4.6514e-06 | 2.9028e-06 | 0.046206 | 0.046206 | 0.046206 | 0.98585 | -0.27115 | 0.98601 | -0.26797 | 12.694
37 | 0.013162 | 0.0033035 | -0.013158 | -0.003301 | 4.5497e-06 | 2.5225e-06 | 0.019899 | 0.019899 | 0.019899 | 0.98436 | -0.3002 | 0.98398 | -0.30745 | 5.4667
38 | -0.0369 | -0.0092674 | 0.036942 | 0.0092937 | 4.1789e-05 | 2.6286e-05 | 0.055694 | 0.055694 | 0.055694 | 0.98601 | -0.26797 | 0.98723 | -0.24426 | 15.3005
39 | 0.013158 | 0.003301 | -0.01315 | -0.0032967 | 7.7164e-06 | 4.2788e-06 | 0.019899 | 0.019899 | 0.019899 | 0.98398 | -0.30745 | 0.98335 | -0.31975 | 5.4668
40 | 0.01315 | 0.0032967 | -0.013146 | -0.0032947 | 3.7348e-06 | 2.0713e-06 | 0.019899 | 0.019899 | 0.019899 | 0.98335 | -0.31975 | 0.98305 | -0.32572 | 5.4668
41 | 0.010555 | 0.0026453 | -0.010555 | -0.0026452 | 3.0862e-07 | 1.5665e-07 | 0.015977 | 0.015977 | 0.015977 | 0.98305 | -0.32572 | 0.98302 | -0.32633 | 4.3894
42 | 0.0071854 | 0.0018006 | -0.0071844 | -0.0018003 | 1.038e-06 | 3.6775e-07 | 0.010877 | 0.010877 | 0.010877 | 0.98302 | -0.32633 | 0.98286 | -0.32936 | 2.9881
43 | 0.0046048 | 0.0011538 | -0.0046043 | -0.0011538 | 4.2483e-07 | -2.3502e-08 | 0.0069713 | 0.0069714 | 0.0069714 | 0.98286 | -0.32936 | 0.98276 | -0.3313 | 1.9152
44 | -0.0017301 | -0.0004336 | 0.0017304 | 0.00043227 | 3.1683e-07 | -1.3301e-06 | 0.0026314 | 0.0026308 | 0.0026314 | 0.97836 | -0.41612 | 0.97856 | -0.41227 | 0.7229
45 | 0.0050985 | 0.0012774 | -0.0050979 | -0.0012774 | 5.427e-07 | 4.4883e-08 | 0.0077527 | 0.0077528 | 0.0077528 | 0.97856 | -0.41227 | 0.97844 | -0.41451 | 2.1299
46 | -0.0074064 | -0.0018545 | 0.0074068 | 0.0018546 | 4.2137e-07 | 1.5836e-07 | 0.011262 | 0.011262 | 0.011262 | 0.97856 | -0.41227 | 0.97862 | -0.41108 | 3.0939
47 | 0.002129 | 0.00053333 | -0.0021289 | -0.00053356 | 9.0802e-08 | -2.3197e-07 | 0.0032377 | 0.0032378 | 0.0032378 | 0.97844 | -0.41451 | 0.9784 | -0.4154 | 0.88952
48 | -0.0080141 | -0.0020068 | 0.0080142 | 0.0020069 | 1.637e-07 | 6.7828e-08 | 0.012185 | 0.012185 | 0.012185 | 0.97862 | -0.41108 | 0.97864 | -0.41065 | 3.3475
49 | 0.013079 | 0.0032792 | -0.013074 | -0.0032763 | 5.2009e-06 | 2.8866e-06 | 0.01987 | 0.01987 | 0.01987 | 0.97948 | -0.39408 | 0.97906 | -0.40243 | 5.4589
50 | -0.013352 | -0.0033476 | 0.013353 | 0.0033478 | 4.0433e-07 | 2.2579e-07 | 0.020285 | 0.020285 | 0.020285 | 0.97948 | -0.39408 | 0.97951 | -0.39345 | 5.5728
51 | 0.012396 | 0.0031064 | -0.012394 | -0.0031052 | 2.091e-06 | 1.1407e-06 | 0.01884 | 0.01884 | 0.01884 | 0.97906 | -0.40243 | 0.97888 | -0.40597 | 5.1758
52 | -0.013758 | -0.0034496 | 0.013759 | 0.0034497 | 3.3763e-07 | 1.9014e-07 | 0.020902 | 0.020901 | 0.020902 | 0.97951 | -0.39345 | 0.97954 | -0.39293 | 5.7422
53 | -0.0023026 | -0.00057709 | 0.0023028 | 0.00057673 | 1.7854e-07 | -3.5881e-07 | 0.0035286 | 0.0035284 | 0.0035286 | 0.97102 | -0.55976 | 0.9711 | -0.55813 | 0.9694
54 | -0.0044373 | -0.0011117 | 0.0044373 | 0.0011117 | 8.9688e-09 | -6.6097e-10 | 0.0067991 | 0.0067991 | 0.0067991 | 0.9711 | -0.55813 | 0.9711 | -0.55809 | 1.8679
55 | 0.061973 | 0.015579 | -0.061889 | -0.015525 | 8.3663e-05 | 5.3206e-05 | 0.092622 | 0.092622 | 0.092622 | 0.9958 | -0.079799 | 0.99433 | -0.10811 | 25.4456
56 | 0.14655 | 0.03756 | -0.14623 | -0.037355 | 0.00032256 | 0.00020551 | 0.21929 | 0.21929 | 0.21929 | 0.9958 | -0.079799 | 0.9934 | -0.12531 | 30.1224
57 | 0.018963 | 0.004758 | -0.018954 | -0.0047526 | 9.013e-06 | 5.3791e-06 | 0.028339 | 0.028339 | 0.028339 | 0.9958 | -0.079799 | 0.99528 | -0.089772 | 7.7853
58 | 0.069414 | 0.017463 | -0.069397 | -0.017453 | 1.6775e-05 | 1.0685e-05 | 0.1053 | 0.1053 | 0.1053 | 0.98111 | -0.36305 | 0.98085 | -0.36811 | 28.9291
59 | -0.071971 | -0.018104 | 0.072023 | 0.018138 | 5.2641e-05 | 3.3541e-05 | 0.10918 | 0.10918 | 0.10918 | 0.98111 | -0.36305 | 0.98189 | -0.34775 | 29.9943
60 | 0.06601 | 0.016604 | -0.065929 | -0.016552 | 8.0898e-05 | 5.1504e-05 | 0.10016 | 0.10016 | 0.10016 | 0.98085 | -0.36811 | 0.97954 | -0.39379 | 27.5173
61 | 0.063073 | 0.015837 | -0.062998 | -0.015789 | 7.4934e-05 | 4.7684e-05 | 0.095825 | 0.095825 | 0.095825 | 0.97954 | -0.39379 | 0.97827 | -0.41873 | 26.3257
62 | 0.0089632 | 0.0022463 | -0.0089629 | -0.0022462 | 2.6656e-07 | 1.2259e-07 | 0.013634 | 0.013634 | 0.013634 | 0.97827 | -0.41873 | 0.97823 | -0.41935 | 3.7455
63 | 0.0071384 | 0.0017889 | -0.0071379 | -0.0017887 | 5.2586e-07 | 1.8725e-07 | 0.010858 | 0.010858 | 0.010858 | 0.97823 | -0.41935 | 0.97816 | -0.4209 | 2.9831
64 | 0.0056975 | 0.0014278 | -0.0056973 | -0.0014277 | 1.5547e-07 | 3.0227e-08 | 0.0086673 | 0.0086673 | 0.0086673 | 0.97816 | -0.4209 | 0.97813 | -0.42147 | 2.3811
65 | -0.0033289 | -0.0008342 | 0.003329 | 0.00083415 | 6.6736e-08 | -4.4382e-08 | 0.0050643 | 0.0050643 | 0.0050643 | 0.9781 | -0.42189 | 0.97813 | -0.42147 | 1.3913
66 | 0.0015161 | 0.00037986 | -0.001516 | -0.00037996 | 1.7097e-08 | -9.6627e-08 | 0.0023064 | 0.0023064 | 0.0023064 | 0.9781 | -0.42189 | 0.97809 | -0.42213 | 0.63363
67 | 0.061889 | 0.015525 | -0.061865 | -0.01551 | 2.4264e-05 | 1.5431e-05 | 0.092622 | 0.092622 | 0.092622 | 0.99433 | -0.10811 | 0.9939 | -0.11634 | 25.4456
68 | 0.13717 | 0.035083 | -0.1371 | -0.03504 | 6.7934e-05 | 4.3256e-05 | 0.20571 | 0.20571 | 0.20571 | 0.9934 | -0.12531 | 0.99287 | -0.13555 | 28.2571
69 | 0.015914 | 0.0039906 | -0.015913 | -0.0039903 | 5.4666e-07 | 3.164e-07 | 0.023793 | 0.023793 | 0.023793 | 0.99528 | -0.089772 | 0.99524 | -0.090493 | 6.5365
70 | 0.028624 | 0.007179 | -0.028609 | -0.0071702 | 1.4195e-05 | 8.8176e-06 | 0.042855 | 0.042855 | 0.042855 | 0.9939 | -0.11634 | 0.99337 | -0.12675 | 11.7735
71 | 0.13482 | 0.034469 | -0.13428 | -0.03412 | 0.00054666 | 0.0003494 | 0.2023 | 0.2023 | 0.2023 | 0.99287 | -0.13555 | 0.98847 | -0.21973 | 55.5774
72 | 0.014059 | 0.0035256 | -0.014053 | -0.0035224 | 5.6961e-06 | 3.199e-06 | 0.021021 | 0.021021 | 0.021021 | 0.99524 | -0.090493 | 0.9948 | -0.098997 | 5.775
73 | 0.0040875 | 0.0010235 | -0.004087 | -0.0010236 | 4.6421e-07 | -1.2199e-07 | 0.0061528 | 0.006153 | 0.006153 | 0.98847 | -0.21973 | 0.98835 | -0.22212 | 1.6904
74 | 0.027194 | 0.0068214 | -0.027178 | -0.0068116 | 1.5917e-05 | 9.8624e-06 | 0.04094 | 0.04094 | 0.04094 | 0.98847 | -0.21973 | 0.98784 | -0.23202 | 11.2472
75 | 0.10299 | 0.026275 | -0.10247 | -0.025938 | 0.00052718 | 0.00033665 | 0.15521 | 0.15521 | 0.15521 | 0.98847 | -0.21973 | 0.98295 | -0.32631 | 42.64
76 | 0.011686 | 0.0029291 | -0.011686 | -0.002929 | 2.4422e-07 | 1.2863e-07 | 0.01748 | 0.01748 | 0.01748 | 0.9948 | -0.098997 | 0.99478 | -0.099436 | 4.8022
77 | 0.0031965 | 0.00080044 | -0.0031965 | -0.00080051 | 7.9819e-08 | -6.6697e-08 | 0.0048123 | 0.0048124 | 0.0048124 | 0.98835 | -0.22212 | 0.98832 | -0.22264 | 1.3221
78 | 0.066299 | 0.016842 | -0.066225 | -0.016795 | 7.3837e-05 | 4.7008e-05 | 0.10045 | 0.10045 | 0.10045 | 0.98295 | -0.32631 | 0.98175 | -0.34947 | 27.5953
79 | 0.036167 | 0.0090966 | -0.036143 | -0.0090814 | 2.4173e-05 | 1.5199e-05 | 0.054763 | 0.054763 | 0.054763 | 0.98295 | -0.32631 | 0.98223 | -0.34031 | 15.0448
80 | 0.010257 | 0.0025708 | -0.010255 | -0.0025699 | 1.7787e-06 | 8.768e-07 | 0.015342 | 0.015343 | 0.015343 | 0.99478 | -0.099436 | 0.99459 | -0.10308 | 4.215
81 | -0.0031342 | -0.00078551 | 0.0031344 | 0.00078537 | 1.5859e-07 | -1.3641e-07 | 0.0047458 | 0.0047457 | 0.0047458 | 0.98271 | -0.33236 | 0.98276 | -0.3313 | 1.3038
82 | 0.011243 | 0.0028178 | -0.011242 | -0.0028169 | 1.7608e-06 | 9.1988e-07 | 0.016987 | 0.016988 | 0.016988 | 0.98487 | -0.28999 | 0.9847 | -0.29328 | 4.6669
83 | 0.011486 | 0.0028793 | -0.011484 | -0.0028786 | 1.328e-06 | 7.0031e-07 | 0.017354 | 0.017354 | 0.017354 | 0.98487 | -0.28999 | 0.98474 | -0.29242 | 4.7676
84 | 0.0081269 | 0.0020366 | -0.0081265 | -0.0020364 | 4.074e-07 | 1.6537e-07 | 0.012159 | 0.012159 | 0.012159 | 0.99459 | -0.10308 | 0.99454 | -0.10413 | 3.3403
85 | 0.0073208 | 0.0018345 | -0.0073205 | -0.0018344 | 3.2856e-07 | 1.1552e-07 | 0.010953 | 0.010953 | 0.010953 | 0.99454 | -0.10413 | 0.99449 | -0.10507 | 3.0092
86 | 0.0052867 | 0.0013247 | -0.0052862 | -0.0013246 | 5.3205e-07 | 4.6336e-08 | 0.0079102 | 0.0079103 | 0.0079103 | 0.99449 | -0.10507 | 0.99438 | -0.10718 | 2.1732
87 | 0.0034708 | 0.00086965 | -0.0034706 | -0.00086981 | 2.4187e-07 | -1.5535e-07 | 0.0051937 | 0.0051939 | 0.0051939 | 0.99438 | -0.10718 | 0.9943 | -0.10865 | 1.4269
88 | -0.015087 | -0.0037827 | 0.015095 | 0.0037871 | 7.8051e-06 | 4.4962e-06 | 0.022919 | 0.022919 | 0.022919 | 0.97954 | -0.39293 | 0.98009 | -0.38208 | 6.2965
89 | -0.018497 | -0.0046399 | 0.018508 | 0.0046464 | 1.093e-05 | 6.529e-06 | 0.028085 | 0.028085 | 0.028085 | 0.98009 | -0.38208 | 0.98073 | -0.36969 | 7.7156
90 | -0.02183 | -0.0054789 | 0.021832 | 0.0054804 | 2.4482e-06 | 1.4918e-06 | 0.033124 | 0.033124 | 0.033124 | 0.98073 | -0.36969 | 0.98085 | -0.36734 | 9.1001
91 | -0.011798 | -0.0029556 | 0.0118 | 0.0029563 | 1.2945e-06 | 6.9361e-07 | 0.017937 | 0.017937 | 0.017937 | 0.97876 | -0.40828 | 0.97888 | -0.40597 | 4.9277
92 | 0.011078 | 0.002775 | -0.011076 | -0.0027743 | 1.2499e-06 | 6.5223e-07 | 0.016841 | 0.016841 | 0.016841 | 0.97876 | -0.40828 | 0.97864 | -0.41065 | 4.6266
93 | -0.026824 | -0.0067315 | 0.026835 | 0.0067381 | 1.0596e-05 | 6.5661e-06 | 0.040698 | 0.040698 | 0.040698 | 0.98085 | -0.36734 | 0.98127 | -0.35906 | 11.1807
94 | -0.028949 | -0.0072678 | 0.028956 | 0.0072724 | 7.2745e-06 | 4.5285e-06 | 0.043903 | 0.043903 | 0.043903 | 0.98127 | -0.35906 | 0.98154 | -0.3538 | 12.0613
95 | -0.03072 | -0.0077143 | 0.030725 | 0.0077178 | 5.5335e-06 | 3.4555e-06 | 0.046576 | 0.046576 | 0.046576 | 0.98154 | -0.3538 | 0.98173 | -0.35002 | 12.7957
96 | -0.032491 | -0.0081604 | 0.032506 | 0.0081699 | 1.5067e-05 | 9.4336e-06 | 0.049253 | 0.049253 | 0.049253 | 0.98173 | -0.35002 | 0.98223 | -0.34031 | 13.5311
97 | 0.063005 | 0.015988 | -0.062993 | -0.01598 | 1.2036e-05 | 7.6589e-06 | 0.095566 | 0.095566 | 0.095566 | 0.98175 | -0.34947 | 0.98155 | -0.35344 | 26.2545
98 | 0.060669 | 0.015398 | -0.060602 | -0.015355 | 6.7333e-05 | 4.2825e-05 | 0.092044 | 0.092044 | 0.092044 | 0.98155 | -0.35344 | 0.98036 | -0.37654 | 25.2867
99 | 0.058277 | 0.014772 | -0.058265 | -0.014765 | 1.1636e-05 | 7.3971e-06 | 0.088514 | 0.088514 | 0.088514 | 0.98036 | -0.37654 | 0.98014 | -0.3807 | 24.3171
100 | 0.0023861 | 0.00059742 | -0.0023861 | -0.00059756 | 6.9839e-08 | -1.4023e-07 | 0.0035923 | 0.0035924 | 0.0035924 | 0.98832 | -0.22264 | 0.98829 | -0.22326 | 0.98692
101 | 0.057051 | 0.014461 | -0.056972 | -0.01441 | 7.8855e-05 | 5.0115e-05 | 0.086671 | 0.086672 | 0.086672 | 0.98014 | -0.3807 | 0.97866 | -0.4095 | 23.8109
102 | 0.0098425 | 0.0024662 | -0.0098419 | -0.0024659 | 6.1422e-07 | 2.9892e-07 | 0.014873 | 0.014873 | 0.014873 | 0.9847 | -0.29328 | 0.98463 | -0.29459 | 4.0861
103 | 0.009305 | 0.0023324 | -0.0093025 | -0.0023311 | 2.5811e-06 | 1.2091e-06 | 0.014061 | 0.014061 | 0.014061 | 0.98474 | -0.29242 | 0.98444 | -0.29824 | 3.8629
104 | 0.0016219 | 0.00040604 | -0.0016218 | -0.00040647 | 8.5565e-08 | -4.283e-07 | 0.0024509 | 0.0024511 | 0.0024511 | 0.98463 | -0.29459 | 0.98457 | -0.2957 | 0.67338
105 | 0.0049335 | 0.0012362 | -0.0049323 | -0.0012362 | 1.1668e-06 | 3.4993e-08 | 0.0074556 | 0.0074558 | 0.0074558 | 0.98463 | -0.29459 | 0.98438 | -0.29956 | 2.0483
106 | 0.0048487 | 0.0012149 | -0.0048486 | -0.0012149 | 5.8598e-08 | 5.145e-10 | 0.0073289 | 0.0073289 | 0.0073289 | 0.98444 | -0.29824 | 0.98443 | -0.2985 | 2.0134
107 | 0.0028327 | 0.00070969 | -0.0028325 | -0.0007099 | 1.7379e-07 | -2.1014e-07 | 0.0042817 | 0.0042818 | 0.0042818 | 0.98443 | -0.2985 | 0.98436 | -0.29978 | 1.1763
108 | 0.0013723 | 0.00034348 | -0.0013722 | -0.00034391 | 5.8355e-08 | -4.2975e-07 | 0.002066 | 0.0020662 | 0.0020662 | 0.98829 | -0.22326 | 0.98824 | -0.22415 | 0.56763
109 | -0.0085578 | -0.0021445 | 0.008559 | 0.002145 | 1.1794e-06 | 5.284e-07 | 0.013112 | 0.013111 | 0.013112 | 0.97121 | -0.55588 | 0.97136 | -0.55299 | 3.6021
110 | 0.0070042 | 0.0017551 | -0.0070035 | -0.0017548 | 7.3669e-07 | 2.604e-07 | 0.010731 | 0.010731 | 0.010731 | 0.97121 | -0.55588 | 0.9711 | -0.55809 | 2.9481
111 | -0.011218 | -0.0028115 | 0.011221 | 0.0028126 | 2.1629e-06 | 1.1425e-06 | 0.017185 | 0.017185 | 0.017185 | 0.97136 | -0.55299 | 0.97156 | -0.54894 | 4.7212
112 | -0.013889 | -0.0034815 | 0.013891 | 0.0034826 | 1.8664e-06 | 1.0583e-06 | 0.021273 | 0.021273 | 0.021273 | 0.97156 | -0.54894 | 0.97171 | -0.54612 | 5.8442
113 | -0.014987 | -0.0037571 | 0.014988 | 0.0037576 | 7.5493e-07 | 4.3581e-07 | 0.02295 | 0.02295 | 0.02295 | 0.97171 | -0.54612 | 0.97176 | -0.54506 | 6.305
114 | -0.016231 | -0.0040692 | 0.016237 | 0.0040728 | 6.1097e-06 | 3.5833e-06 | 0.024854 | 0.024854 | 0.024854 | 0.97176 | -0.54506 | 0.97216 | -0.53717 | 6.8281
115 | 0.00088504 | 0.00022163 | -0.00088503 | -0.00022181 | 1.0152e-08 | -1.7642e-07 | 0.0013546 | 0.0013547 | 0.0013547 | 0.97216 | -0.53717 | 0.97215 | -0.53741 | 0.37216
116 | -0.03897 | -0.0097817 | 0.038998 | 0.0097996 | 2.8515e-05 | 1.7985e-05 | 0.059654 | 0.059654 | 0.059654 | 0.97216 | -0.53717 | 0.97294 | -0.52184 | 16.3884
117 | 0.021848 | 0.0054873 | -0.021826 | -0.0054741 | 2.1636e-05 | 1.3208e-05 | 0.033445 | 0.033445 | 0.033445 | 0.97216 | -0.53717 | 0.97111 | -0.55794 | 9.1883
118 | 0.055688 | 0.014088 | -0.055587 | -0.014025 | 0.00010027 | 6.3706e-05 | 0.084718 | 0.084718 | 0.084718 | 0.97866 | -0.4095 | 0.97674 | -0.4471 | 23.2742
119 | 0.054547 | 0.013764 | -0.054439 | -0.013695 | 0.00010788 | 6.8524e-05 | 0.083133 | 0.083133 | 0.083133 | 0.97674 | -0.4471 | 0.97463 | -0.48849 | 22.8387
120 | 0.0088855 | 0.0022269 | -0.0088848 | -0.0022266 | 6.9865e-07 | 3.2099e-07 | 0.013566 | 0.013566 | 0.013566 | 0.97463 | -0.48849 | 0.97455 | -0.49014 | 3.7269
121 | 0.045553 | 0.011468 | -0.045512 | -0.011442 | 4.1039e-05 | 2.5983e-05 | 0.069567 | 0.069567 | 0.069567 | 0.97463 | -0.48849 | 0.97367 | -0.50736 | 19.1118
122 | 0.004371 | 0.0010953 | -0.0043706 | -0.0010954 | 3.9761e-07 | -4.2098e-08 | 0.0066739 | 0.0066741 | 0.0066741 | 0.97455 | -0.49014 | 0.97445 | -0.49205 | 1.8335
123 | 0.0056591 | 0.0014181 | -0.0056587 | -0.001418 | 3.8556e-07 | 7.5801e-08 | 0.0086484 | 0.0086485 | 0.0086485 | 0.97367 | -0.50736 | 0.9736 | -0.50879 | 2.376
124 | 0.039853 | 0.010024 | -0.03985 | -0.010022 | 3.1744e-06 | 2.0032e-06 | 0.060919 | 0.060919 | 0.060919 | 0.97367 | -0.50736 | 0.97359 | -0.50902 | 16.7359
125 | -0.039825 | -0.010007 | 0.03985 | 0.010022 | 2.4377e-05 | 1.5384e-05 | 0.060919 | 0.060919 | 0.060919 | 0.97294 | -0.52184 | 0.97359 | -0.50902 | 16.7359
126 | 0.0046791 | 0.0011725 | -0.004679 | -0.0011725 | 5.1506e-08 | -4.3425e-10 | 0.0071513 | 0.0071513 | 0.0071513 | 0.9736 | -0.50879 | 0.97359 | -0.50902 | 1.9646
127 | 0.003847 | 0.00096396 | -0.0038467 | -0.00096407 | 3.3326e-07 | -1.0635e-07 | 0.0058797 | 0.0058798 | 0.0058798 | 0.97359 | -0.50902 | 0.9735 | -0.51084 | 1.6153

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43216 | 0.11025

## res_load
| p_mw | q_mvar
0 | 0.0044029 | 0.0011035
1 | 0.0025429 | 0.00063732
2 | 0.0012484 | 0.00031288
3 | 0.0039262 | 0.00098399
4 | 0.0018353 | 0.00045998
5 | 0.0033504 | 0.00083968
6 | 0.0025457 | 0.00063801
7 | 0.0025814 | 0.00064695
8 | 0.0019157 | 0.00048012
9 | 0.0016626 | 0.00041668
10 | 0.0042337 | 0.0010611
11 | 0.0030197 | 0.00075681
12 | 0.001111 | 0.00027843
13 | 0.0015181 | 0.00038047
14 | 0.0070997 | 0.0017793
15 | 0.00425 | 0.0010652
16 | 0.0025372 | 0.00063588
17 | 0.0022628 | 0.00056712
18 | 0.0083521 | 0.0020932
19 | 0.0020674 | 0.00051813
20 | 0.0024539 | 0.00061502
21 | 0.0027041 | 0.00067772
22 | 0.0055919 | 0.0014015
23 | 0.0065351 | 0.0016379
24 | 0.00104 | 0.00026065
25 | 0.0015383 | 0.00038553
26 | 0.0033799 | 0.0008471
27 | 0.0061238 | 0.0015348
28 | 0.0013289 | 0.00033306
29 | 0.0039998 | 0.0010024
30 | 0.0062868 | 0.0015756
31 | 0.0025909 | 0.00064934
32 | 0.0033697 | 0.00084453
33 | 0.0025796 | 0.00064651
34 | 0.0017301 | 0.0004336
35 | 0.00057748 | 0.00014473
36 | 0.0029689 | 0.00074407
37 | 0.00060728 | 0.0001522
38 | 0.00027306 | 6.8436e-05
39 | 0.00067794 | 0.00016991
40 | 0.00040588 | 0.00010172
41 | 0.0021289 | 0.00053356
42 | 0.0023026 | 0.00057709
43 | 0.0021345 | 0.00053495
44 | 0.0025566 | 0.00064074
45 | 0.0033875 | 0.00084898
46 | 0.0054133 | 0.0013567
47 | 0.0028554 | 0.00071564
48 | 0.054035 | 0.013543
49 | 0.0018245 | 0.00045727
50 | 0.0014404 | 0.00036099
51 | 0.0018128 | 0.00045434
52 | 0.0023684 | 0.00059357
53 | 0.001516 | 0.00037996
54 | 0.0090659 | 0.0022721
55 | 0.0030405 | 0.00076202
56 | 0.033241 | 0.008331
57 | 0.0022753 | 0.00057024
58 | 0.0018541 | 0.00046469
59 | 0.028609 | 0.0071702
60 | 0.0023672 | 0.00059327
61 | 0.00089046 | 0.00022317
62 | 0.027178 | 0.0068116
63 | 0.0014291 | 0.00035816
64 | 0.0031342 | 0.00078551
65 | 0.00147 | 0.00036841
66 | 0.0021281 | 0.00053336
67 | 0.00080562 | 0.00020191
68 | 0.0020338 | 0.00050973
69 | 0.0018153 | 0.00045497
70 | 0.0013283 | 0.0003329
71 | 0.0034025 | 0.00085275
72 | 0.0033215 | 0.00083245
73 | 0.00072086 | 0.00018066
74 | 0.00059418 | 0.00014892
75 | 0.0030621 | 0.00076744
76 | 0.0049921 | 0.0012511
77 | 0.0021137 | 0.00052975
78 | 0.0017635 | 0.00044197
79 | 0.0017661 | 0.00044264
80 | 0.0036369 | 0.0009115
81 | 0.0032201 | 0.00080702
82 | 0.0023238 | 0.0005824
83 | 0.0023252 | 0.00058275
84 | 0.00081034 | 0.00020309
85 | 0.0012139 | 0.00030424
86 | 0.0013992 | 0.00035066
87 | 0.0021794 | 0.00054622
88 | 0.0032865 | 0.00082369
89 | 0.0044537 | 0.0011162
90 | 0.0016218 | 0.00040647
91 | 0.0049323 | 0.0012362
92 | 0.002016 | 0.00050525
93 | 0.0028325 | 0.0007099
94 | 0.0034706 | 0.00086981
95 | 0.0010138 | 0.00025408
96 | 0.0015536 | 0.00038938
97 | 0.0026594 | 0.0006665
98 | 0.0025662 | 0.00064315
99 | 0.0026689 | 0.00066889
100 | 0.0010955 | 0.00027456
101 | 0.0012433 | 0.00031161
102 | 0.0012849 | 0.00032203
103 | 0.0010407 | 0.00026083
104 | 0.0045138 | 0.0011313
105 | 0.004507 | 0.0011296
106 | 0.00088503 | 0.00022181
107 | 0.00082707 | 0.00020728
108 | 0.0043706 | 0.0010954
109 | 0.00097959 | 0.00024551
110 | 0.00083202 | 0.00020852
111 | 0.0013722 | 0.00034391
112 | 0.0038467 | 0.00096407

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1