## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3002-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3002-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3002-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3002-1_0_6_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_3002-1_0_6_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_3002-1_0_6_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_3002-1_0_6_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_3002-1_0_6_node_54 | 0.4 | n |  | TRUE
8 | bus_LV_3002-1_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_3002-1_0_6_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_3002-1_0_6_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_3002-1_0_6_node_56 | 0.4 | n |  | TRUE
12 | bus_LV_3002-1_0_6_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_3002-1_0_6_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_3002-1_0_6_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_3002-1_0_6_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_3002-1_0_6_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_3002-1_0_6_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_3002-1_0_6_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_3002-1_0_6_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_3002-1_0_6_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_3002-1_0_6_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_3002-1_0_6_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_3002-1_0_6_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_3002-1_0_6_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_3002-1_0_6_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_3002-1_0_6_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_3002-1_0_6_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_3002-1_0_6_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_3002-1_0_6_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_3002-1_0_6_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_3002-1_0_6_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_3002-1_0_6_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_3002-1_0_6_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_3002-1_0_6_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_3002-1_0_6_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_3002-1_0_6_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_3002-1_0_6_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_3002-1_0_6_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_3002-1_0_6_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_3002-1_0_6_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_3002-1_0_6_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_3002-1_0_6_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_3002-1_0_6_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_3002-1_0_6_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_3002-1_0_6_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_3002-1_0_6_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_3002-1_0_6_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_3002-1_0_6_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_3002-1_0_6_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_3002-1_0_6_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_3002-1_0_6_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_3002-1_0_6_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_3002-1_0_6_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_3002-1_0_6_node_52 | 0.4 | n |  | TRUE
55 | bus_MV_38_0_node_119 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3002-1_0_6_load_0 | 0 | 0.039662 | 0.0099402 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3002-1_0_6_load_33 | 5 | 0.00071833 | 0.00018003 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3002-1_0_6_load_54 | 7 | 0.00073049 | 0.00018308 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3002-1_0_6_load_56 | 11 | 0.0036338 | 0.0009107 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3002-1_0_6_load_55 | 12 | 0.0034903 | 0.00087475 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3002-1_0_6_load_53 | 13 | 0.017923 | 0.0044919 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3002-1_0_6_load_7 | 15 | 0.003466 | 0.00086867 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3002-1_0_6_load_25 | 16 | 0.0025102 | 0.00062912 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3002-1_0_6_load_12 | 17 | 0.00081634 | 0.00020459 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3002-1_0_6_load_14 | 19 | 0.00038877 | 9.7435e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3002-1_0_6_load_21 | 22 | 0.0006135 | 0.00015376 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3002-1_0_6_load_19 | 23 | 0.00033716 | 8.45e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3002-1_0_6_load_22 | 24 | 0.017099 | 0.0042854 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3002-1_0_6_load_31 | 25 | 0.00042195 | 0.00010575 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3002-1_0_6_load_18 | 26 | 0.00093123 | 0.00023339 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3002-1_0_6_load_20 | 29 | 0.00094537 | 0.00023693 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3002-1_0_6_load_30 | 30 | 0.00050809 | 0.00012734 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3002-1_0_6_load_40 | 32 | 0.00031696 | 7.9438e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3002-1_0_6_load_41 | 33 | 0.00058458 | 0.00014651 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3002-1_0_6_load_34 | 36 | 0.00039399 | 9.8744e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3002-1_0_6_load_26 | 37 | 0.00084722 | 0.00021233 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3002-1_0_6_load_27 | 38 | 0.00034459 | 8.6363e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3002-1_0_6_load_28 | 39 | 0.0011467 | 0.00028739 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3002-1_0_6_load_35 | 41 | 0.00048127 | 0.00012062 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3002-1_0_6_load_43 | 44 | 6.0855e-05 | 1.5252e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3002-1_0_6_load_39 | 45 | 8.9455e-05 | 2.242e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3002-1_0_6_load_47 | 46 | 0.00019122 | 4.7925e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3002-1_0_6_load_45 | 48 | 0.00021098 | 5.2876e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3002-1_0_6_load_46 | 49 | 6.4486e-05 | 1.6162e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3002-1_0_6_load_50 | 50 | 0.00015662 | 3.9252e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3002-1_0_6_load_48 | 51 | 7.2931e-05 | 1.8278e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3002-1_0_6_load_49 | 52 | 0.00012058 | 3.0219e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3002-1_0_6_load_51 | 53 | 7.2382e-05 | 1.8141e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3002-1_0_6_load_52 | 54 | 7.4065e-05 | 1.8563e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3002-1_0_6_line_0 |  | 0 | 1 | 0.0094504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3002-1_0_6_line_1 |  | 0 | 2 | 0.45448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_3002-1_0_6_line_2 |  | 1 | 3 | 0.086626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3002-1_0_6_line_3 |  | 2 | 4 | 1.0088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_3002-1_0_6_line_4 |  | 3 | 13 | 0.049676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3002-1_0_6_line_5 |  | 3 | 8 | 0.065951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3002-1_0_6_line_6 |  | 4 | 5 | 0.31193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_3002-1_0_6_line_7 |  | 5 | 27 | 0.24714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_3002-1_0_6_line_8 |  | 6 | 7 | 0.029193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3002-1_0_6_line_9 |  | 6 | 8 | 0.35814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3002-1_0_6_line_10 |  | 6 | 9 | 0.46878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3002-1_0_6_line_11 |  | 8 | 12 | 0.051403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3002-1_0_6_line_12 |  | 8 | 10 | 0.37718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3002-1_0_6_line_13 |  | 9 | 14 | 0.055279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3002-1_0_6_line_14 |  | 9 | 15 | 0.016343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3002-1_0_6_line_15 |  | 10 | 11 | 0.098654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3002-1_0_6_line_16 |  | 14 | 16 | 0.013535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3002-1_0_6_line_17 |  | 17 | 18 | 0.04264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3002-1_0_6_line_18 |  | 17 | 19 | 0.0067082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3002-1_0_6_line_19 |  | 18 | 20 | 0.16897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_3002-1_0_6_line_20 |  | 18 | 21 | 1.2025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_3002-1_0_6_line_21 |  | 20 | 22 | 0.18753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_3002-1_0_6_line_22 |  | 20 | 23 | 0.54268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3002-1_0_6_line_23 |  | 21 | 24 | 0.24235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_3002-1_0_6_line_24 |  | 22 | 25 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_3002-1_0_6_line_25 |  | 23 | 26 | 0.0034301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3002-1_0_6_line_26 |  | 24 | 28 | 0.28769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_3002-1_0_6_line_27 |  | 25 | 30 | 0.033387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_3002-1_0_6_line_28 |  | 26 | 29 | 0.0046479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3002-1_0_6_line_29 |  | 27 | 40 | 0.48601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_3002-1_0_6_line_30 |  | 28 | 31 | 0.75952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_3002-1_0_6_line_31 |  | 30 | 39 | 0.016729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_3002-1_0_6_line_32 |  | 31 | 32 | 0.0049051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3002-1_0_6_line_33 |  | 32 | 33 | 0.010407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3002-1_0_6_line_34 |  | 33 | 43 | 0.77458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3002-1_0_6_line_35 |  | 33 | 42 | 0.36562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3002-1_0_6_line_36 |  | 34 | 35 | 0.73785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3002-1_0_6_line_37 |  | 34 | 36 | 0.11525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3002-1_0_6_line_38 |  | 35 | 44 | 0.45213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3002-1_0_6_line_39 |  | 36 | 41 | 0.015954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3002-1_0_6_line_40 |  | 37 | 38 | 0.0063654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_3002-1_0_6_line_41 |  | 37 | 39 | 0.087624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_3002-1_0_6_line_42 |  | 38 | 40 | 0.44115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_3002-1_0_6_line_43 |  | 41 | 42 | 0.074382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3002-1_0_6_line_44 |  | 43 | 45 | 0.53995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3002-1_0_6_line_45 |  | 44 | 47 | 0.92054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3002-1_0_6_line_46 |  | 45 | 46 | 0.55621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3002-1_0_6_line_47 |  | 47 | 48 | 0.16751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3002-1_0_6_line_48 |  | 48 | 49 | 0.020673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3002-1_0_6_line_49 |  | 49 | 50 | 0.56839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3002-1_0_6_line_50 |  | 50 | 53 | 0.054057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3002-1_0_6_line_51 |  | 50 | 52 | 0.613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3002-1_0_6_line_52 |  | 51 | 52 | 0.007316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3002-1_0_6_line_53 |  | 53 | 54 | 0.02315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3002-1_0_6_trafo_2 | 0.63 MVA 20/0.4 kV | 55 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42
0 | 2742397.742 | 1235685.649 | 2742397.487 | 1235695.096
1 | 2742319.707 | 1236069.4887 | 2742324.4939 | 1236065.2997 | 2742333.7414 | 1236052.8434 | 2742351.4196 | 1236016.857 | 2742389.5303 | 1235972.4306 | 2742410.0854 | 1235944.9876 | 2742422.7759 | 1235916.533 | 2742434.4315 | 1235900.6093 | 2742441.1515 | 1235895.3769 | 2742453.9467 | 1235887.8102 | 2742466.3107 | 1235878.0202 | 2742468.793 | 1235872.3858 | 2742468.329 | 1235867.1144 | 2742463.7958 | 1235856.3071 | 2742445.9819 | 1235834.1714 | 2742430.3652 | 1235817.3264 | 2742411.881 | 1235801.3468 | 2742401.5696 | 1235787.743 | 2742398.3367 | 1235780.1699 | 2742396.5785 | 1235772.9769 | 2742395.639 | 1235763.5348 | 2742397.487 | 1235695.096
2 | 2742337.1981 | 1235635.5536 | 2742343.0677 | 1235637.0623 | 2742348.0389 | 1235638.4604 | 2742359.3488 | 1235642.6462 | 2742365.3655 | 1235645.2816 | 2742377.0784 | 1235651.2898 | 2742383.7871 | 1235655.3765 | 2742391.9357 | 1235660.9879 | 2742392.0361 | 1235671.3217 | 2742393.3825 | 1235677.0591 | 2742397.742 | 1235685.649
3 | 2742161.4131 | 1237065.7563 | 2742319.707 | 1236069.4887
4 | 2742296.7906 | 1235648.7531 | 2742295.4149 | 1235641.3914 | 2742311.622 | 1235638.3768 | 2742322.7414 | 1235637.8761 | 2742330.0616 | 1235637.3065 | 2742337.1981 | 1235635.5536
5 | 2742271.8112 | 1235632.0511 | 2742303.3829 | 1235629.9053 | 2742307.2612 | 1235630.4653 | 2742313.2526 | 1235631.6321 | 2742318.7131 | 1235632.5192 | 2742333.7293 | 1235634.6475 | 2742337.1981 | 1235635.5536
6 | 2742161.4131 | 1237065.7563 | 2742141.5491 | 1237074.6556 | 2742087.6512 | 1237119.9511 | 2742040.0329 | 1237158.1353 | 2742016.3149 | 1237171.2132 | 2741978.011 | 1237182.3743 | 2741950.1479 | 1237182.9978 | 2741936.128 | 1237189.691 | 2741914.9765 | 1237233.1578
7 | 2741668.3391 | 1237248.7955 | 2741746.7132 | 1237242.7599 | 2741914.9765 | 1237233.1578
8 | 2741956.3811 | 1235709.3754 | 2741937.9371 | 1235719.5105 | 2741930.7406 | 1235723.4643
9 | 2741956.3811 | 1235709.3754 | 2741993.3253 | 1235685.4925 | 2742000.1506 | 1235678.3826 | 2742017.9668 | 1235669.8119 | 2742028.2849 | 1235659.1268 | 2742035.0918 | 1235654.3741 | 2742042.6512 | 1235652.0306 | 2742066.5553 | 1235651.357 | 2742073.1567 | 1235652.0266 | 2742083.3205 | 1235653.1706 | 2742089.2791 | 1235653.1798 | 2742094.4875 | 1235652.893 | 2742105.2809 | 1235650.1932 | 2742116.8932 | 1235647.4462 | 2742125.0633 | 1235644.8949 | 2742134.0438 | 1235641.073 | 2742140.8705 | 1235637.0772 | 2742145.6687 | 1235633.689 | 2742157.5085 | 1235622.7069 | 2742161.1193 | 1235620.5247 | 2742166.2314 | 1235618.89 | 2742182.7078 | 1235615.3811 | 2742227.0948 | 1235627.2763 | 2742231.0795 | 1235627.5052 | 2742234.2963 | 1235625.9697 | 2742235.5115 | 1235623.2853 | 2742234.0723 | 1235619.2028 | 2742237.5874 | 1235619.1202 | 2742240.5784 | 1235618.4801 | 2742246.9532 | 1235616.2863 | 2742252.4557 | 1235621.4226 | 2742256.4178 | 1235624.1755 | 2742262.1594 | 1235627.5493 | 2742271.8112 | 1235632.0511
10 | 2741561.2777 | 1235583.2698 | 2741568.5631 | 1235580.0294 | 2741574.5044 | 1235576.6346 | 2741578.1583 | 1235573.9082 | 2741585.2713 | 1235578.2148 | 2741591.2939 | 1235579.9821 | 2741603.008 | 1235580.8954 | 2741607.6665 | 1235581.7628 | 2741611.7601 | 1235585.3636 | 2741631.5027 | 1235600.4475 | 2741640.8413 | 1235606.3532 | 2741644.6742 | 1235610.4037 | 2741646.0247 | 1235613.4609 | 2741657.1486 | 1235618.7975 | 2741669.7757 | 1235619.5214 | 2741675.6772 | 1235621.2859 | 2741706.3675 | 1235626.8672 | 2741716.9022 | 1235624.85 | 2741733.4186 | 1235630.7492 | 2741744.5552 | 1235630.7927 | 2741756.2194 | 1235626.178 | 2741777.3046 | 1235617.996 | 2741783.2091 | 1235624.387 | 2741783.7027 | 1235630.9825 | 2741780.2969 | 1235637.5848 | 2741779.74 | 1235647.2691 | 2741787.7749 | 1235650.3747 | 2741804.243 | 1235652.9033 | 2741813.8126 | 1235651.6639 | 2741827.3189 | 1235654.5666 | 2741838.831 | 1235652.5174 | 2741853.1455 | 1235655.8176 | 2741866.099 | 1235653.9697 | 2741882.9123 | 1235656.3066 | 2741892.856 | 1235662.861 | 2741899.7556 | 1235662.4588 | 2741907.2284 | 1235665.9515 | 2741916.485 | 1235672.4227 | 2741923.6846 | 1235680.691 | 2741930.9603 | 1235685.4579 | 2741943.2811 | 1235700.2543 | 2741949.8036 | 1235702.957 | 2741956.3811 | 1235709.3754
11 | 2742271.8112 | 1235632.0511 | 2742268.3574 | 1235634.3149 | 2742259.9087 | 1235638.0604 | 2742224.8695 | 1235653.1572
12 | 2741912.9649 | 1235523.8508 | 2741916.9699 | 1235525.1365 | 2741921.0891 | 1235525.1238 | 2741926.6184 | 1235525.9899 | 2741981.2774 | 1235540.5755 | 2742023.3307 | 1235551.9462 | 2742034.0283 | 1235554.8378 | 2742230.7286 | 1235607.7014 | 2742238.598 | 1235610.1253 | 2742241.2415 | 1235611.3452 | 2742246.9532 | 1235616.2863 | 2742252.4557 | 1235621.4226 | 2742256.4178 | 1235624.1755 | 2742262.1594 | 1235627.5493 | 2742271.8112 | 1235632.0511
13 | 2741517.2566 | 1235602.3381 | 2741526.0024 | 1235599.7664 | 2741534.193 | 1235599.2054 | 2741548.0348 | 1235598.5234 | 2741551.875 | 1235598.1479 | 2741555.384 | 1235597.0528 | 2741558.4359 | 1235595.7577 | 2741560.065 | 1235594.1173 | 2741561.2577 | 1235590.776 | 2741561.2777 | 1235583.2698
14 | 2741561.2777 | 1235583.2698 | 2741557.1037 | 1235584.6271 | 2741552.7635 | 1235585.3355 | 2741546.6512 | 1235585.4233 | 2741545.2297 | 1235585.1729
15 | 2741912.9649 | 1235523.8508 | 2741907.9827 | 1235529.5591 | 2741903.6842 | 1235533.5823 | 2741898.0448 | 1235537.0062 | 2741875.6848 | 1235544.6568 | 2741862.2611 | 1235546.5269 | 2741858.0677 | 1235547.7389 | 2741854.0496 | 1235550.4899 | 2741851.7611 | 1235554.372 | 2741851.2282 | 1235558.2961 | 2741853.6632 | 1235566.6617 | 2741854.6195 | 1235581.7758
16 | 2741517.2566 | 1235602.3381 | 2741508.9631 | 1235591.6421
17 | 2742140.4346 | 1237410.0515 | 2742137.6918 | 1237415.5352 | 2742109.022 | 1237438.1385
18 | 2742103.7541 | 1237442.2916 | 2742109.022 | 1237438.1385
19 | 2741989.5522 | 1237407.0957 | 2742001.9785 | 1237395.8049 | 2742014.9571 | 1237385.7951 | 2742028.3589 | 1237379.61 | 2742042.2304 | 1237378.7854 | 2742055.7092 | 1237381.399 | 2742066.9818 | 1237388.9086 | 2742079.539 | 1237400.297 | 2742089.9763 | 1237406.9637 | 2742108.9366 | 1237411.0988 | 2742140.4346 | 1237410.0515
20 | 2742140.4346 | 1237410.0515 | 2742174.5786 | 1237409.1345 | 2742175.6536 | 1237417.3454 | 2742179.0428 | 1237427.2131 | 2742192.0194 | 1237446.6746 | 2742207.202 | 1237459.3605 | 2742227.3625 | 1237467.7285 | 2742250.1701 | 1237471.1333 | 2742259.1807 | 1237475.731 | 2742277.998 | 1237492.1297 | 2742299.3362 | 1237500.9377 | 2742305.6437 | 1237507.1499 | 2742328.4761 | 1237555.5849 | 2742347.6777 | 1237566.0433 | 2742360.8158 | 1237593.8832 | 2742444.3517 | 1237665.9173 | 2742458.299 | 1237710.7809 | 2742449.7398 | 1237779.7821 | 2742504.5928 | 1237828.8642 | 2742541.0609 | 1237899.3582 | 2742527.2253 | 1237917.6426 | 2742472.1438 | 1237928.8756 | 2742466.0752 | 1237961.9153 | 2742533.2077 | 1238074.4272 | 2742537.8777 | 1238116.6328 | 2742585.977 | 1238193.0672 | 2742652.8689 | 1238264.6936 | 2742654.3664 | 1238278.5865 | 2742663.0948 | 1238295.4892 | 2742663.7789 | 1238296.3064
21 | 2741989.5522 | 1237407.0957 | 2741988.1984 | 1237407.9975 | 2741981.1919 | 1237412.6342 | 2741970.2706 | 1237416.3876 | 2741958.9373 | 1237417.4288 | 2741879.1264 | 1237406.0784 | 2741849.1843 | 1237405.3737 | 2741817.7912 | 1237410.273 | 2741805.9731 | 1237413.4558
22 | 2741989.5522 | 1237407.0957 | 2741999.2386 | 1237409.7185 | 2742004.5888 | 1237415.4627 | 2742010.5664 | 1237437.0583 | 2742026.0008 | 1237455.0545 | 2742044.2173 | 1237468.1241 | 2742100.1752 | 1237541.4949 | 2742121.7665 | 1237557.1144 | 2742148.6067 | 1237589.33 | 2742147.9345 | 1237600.6463 | 2742101.0122 | 1237644.0402 | 2742124.9301 | 1237679.4331 | 2742148.6432 | 1237687.9749 | 2742157.0099 | 1237763.9878 | 2742138.3777 | 1237837.4262
23 | 2742663.7789 | 1238296.3064 | 2742660.1713 | 1238303.4483 | 2742659.6536 | 1238308.2958 | 2742659.4981 | 1238314.7646 | 2742663.5085 | 1238325.1814 | 2742667.7231 | 1238335.6032 | 2742668.0391 | 1238339.4587 | 2742664.9423 | 1238341.4083 | 2742638.6795 | 1238353.1213 | 2742629.7495 | 1238353.1068 | 2742622.2049 | 1238354.3379 | 2742616.0555 | 1238357.0259 | 2742604.5589 | 1238362.4103 | 2742591.9646 | 1238371.2714 | 2742578.7447 | 1238380.6625 | 2742574.671 | 1238381.3764 | 2742566.2245 | 1238377.9372 | 2742559.9442 | 1238377.575 | 2742521.7473 | 1238387.3893 | 2742520.2623 | 1238389.9782 | 2742523.6675 | 1238391.8839 | 2742535.9541 | 1238395.8268 | 2742542.3396 | 1238400.6288 | 2742544.0701 | 1238404.5183 | 2742539.9646 | 1238406.2435 | 2742538.7586 | 1238405.9496
24 | 2741805.9731 | 1237413.4558 | 2741785.051 | 1237419.0905
25 | 2742137.5342 | 1237840.751 | 2742138.3777 | 1237837.4262
26 | 2742591.6204 | 1238600.6809 | 2742594.2912 | 1238595.3513 | 2742598.3258 | 1238587.7525 | 2742596.3814 | 1238584.2693 | 2742595.6693 | 1238580.2041 | 2742589.5444 | 1238573.3842 | 2742578.1792 | 1238564.8147 | 2742567.2586 | 1238554.4321 | 2742565.4991 | 1238551.7541 | 2742562.3273 | 1238548.6418 | 2742556.895 | 1238538.1909 | 2742556.1485 | 1238527.0519 | 2742554.3766 | 1238524.5738 | 2742553.2513 | 1238520.6988 | 2742557.8204 | 1238516.6826 | 2742547.59 | 1238503.0804 | 2742540.0724 | 1238495.0038 | 2742533.5121 | 1238488.9742 | 2742527.8997 | 1238486.0146 | 2742541.1976 | 1238481.8745 | 2742532.9728 | 1238469.2102 | 2742524.9082 | 1238458.696 | 2742523.4035 | 1238453.5998 | 2742519.1258 | 1238445.8012 | 2742512.4998 | 1238442.8173 | 2742509.7045 | 1238440.7261 | 2742500.7309 | 1238434.027 | 2742497.3158 | 1238432.5326 | 2742497.1602 | 1238430.5048 | 2742500.5049 | 1238426.7372 | 2742509.3907 | 1238420.0778 | 2742523.9474 | 1238413.9438 | 2742527.0535 | 1238403.0975 | 2742538.7586 | 1238405.9496
27 | 2741752.8126 | 1237427.773 | 2741785.051 | 1237419.0905
28 | 2742136.3912 | 1237845.2561 | 2742137.5342 | 1237840.751
29 | 2741230.5682 | 1237321.4246 | 2741233.6625 | 1237314.492 | 2741239.891 | 1237310.0806 | 2741246.5224 | 1237306.2348 | 2741254.7744 | 1237302.9948 | 2741267.6242 | 1237301.2099 | 2741278.8083 | 1237298.8071 | 2741284.7648 | 1237295.0121 | 2741292.7935 | 1237287.1627 | 2741304.567 | 1237277.8122 | 2741313.6265 | 1237269.5871 | 2741315.3202 | 1237265.5348 | 2741316.4059 | 1237254.9067 | 2741387.6982 | 1237279.5252 | 2741435.0799 | 1237260.5697 | 2741456.0517 | 1237255.2977 | 2741479.6609 | 1237237.1882 | 2741532.8626 | 1237253.8483 | 2741615.7323 | 1237252.5778 | 2741668.3391 | 1237248.7955
30 | 2742591.6204 | 1238600.6809 | 2742572.4034 | 1238591.0219 | 2742547.0635 | 1238583.2733 | 2742479.1707 | 1238572.3453 | 2742350.0252 | 1238573.0378 | 2742323.3899 | 1238571.6426 | 2742216.8117 | 1238552.7613 | 2742170.6957 | 1238553.936 | 2742149.9748 | 1238560.2679 | 2742100.9632 | 1238578.0776 | 2742100.4698 | 1238586.0396 | 2742092.2874 | 1238584.5314 | 2742095.0675 | 1238591.3707 | 2742089.7883 | 1238591.5557 | 2742090.863 | 1238597.242 | 2742083.9485 | 1238598.0885 | 2742084.7348 | 1238602.5446 | 2742072.7378 | 1238602.6355 | 2742067.6219 | 1238601.3786 | 2742068.074 | 1238606.5163 | 2742074.2546 | 1238618.6195 | 2742069.1513 | 1238622.5231 | 2742067.5907 | 1238632.706 | 2742006.891 | 1238688.0151 | 2741995.5472 | 1238708.2509 | 2741959.8497 | 1238751.6364
31 | 2741736.6592 | 1237432.1234 | 2741752.8126 | 1237427.773
32 | 2741959.8497 | 1238751.6364 | 2741955.476 | 1238753.857
33 | 2741955.476 | 1238753.857 | 2741946.1968 | 1238758.5682
34 | 2741294.9534 | 1238929.005 | 2741308.7389 | 1238934.4935 | 2741324.8565 | 1238945.3201 | 2741368.5914 | 1238964.2114 | 2741471.6183 | 1238972.1721 | 2741479.033 | 1238972.538 | 2741485.2364 | 1238976.1001 | 2741541.7455 | 1238962.2565 | 2741577.6026 | 1238959.887 | 2741649.1524 | 1238962.351 | 2741690.5023 | 1238937.5263 | 2741722.427 | 1238932.2056 | 2741726.6804 | 1238929.6492 | 2741725.5925 | 1238927.3545 | 2741743.1055 | 1238927.5727 | 2741744.0959 | 1238918.1101 | 2741774.7036 | 1238928.3277 | 2741782.8291 | 1238923.0169 | 2741781.9601 | 1238887.4976 | 2741785.2997 | 1238867.4482 | 2741850.9251 | 1238806.9389 | 2741946.1968 | 1238758.5682
35 | 2741946.1968 | 1238758.5682 | 2742048.9107 | 1239109.4658
36 | 2742206.8064 | 1239200.9608 | 2742205.7539 | 1239210.1438 | 2742175.1154 | 1239244.8748 | 2742173.662 | 1239264.7913 | 2742166.7281 | 1239269.0069 | 2742159.7945 | 1239273.2113 | 2742141.7074 | 1239330.7857 | 2742135.2024 | 1239333.21 | 2742123.6278 | 1239337.5257 | 2742113.426 | 1239354.3412 | 2742057.4212 | 1239349.1074 | 2742051.5976 | 1239367.9518 | 2742030.4101 | 1239376.1968 | 2741971.8133 | 1239353.1192 | 2741960.795 | 1239355.38 | 2741955.6928 | 1239365.278 | 2741943.4442 | 1239372.4695 | 2741939.5431 | 1239378.3371 | 2741942.0149 | 1239389.8287 | 2741940.3893 | 1239415.0793 | 2741946.4837 | 1239432.018 | 2741947.2765 | 1239443.792 | 2741938.6109 | 1239451.4584 | 2741927.9691 | 1239472.1449 | 2741916.3621 | 1239490.484 | 2741910.8916 | 1239507.2461 | 2741890.4073 | 1239523.4489 | 2741876.5677 | 1239542.1351 | 2741870.4287 | 1239565.654 | 2741866.5274 | 1239588.6259 | 2741867.0764 | 1239608.0677 | 2741873.6267 | 1239627.1414 | 2741878.1534 | 1239653.9515 | 2741883.5321 | 1239671.0732 | 2741882.9618 | 1239690.4882
37 | 2742206.8064 | 1239200.9608 | 2742200.4179 | 1239197.5714 | 2742195.1519 | 1239195.0208 | 2742155.2178 | 1239175.8918 | 2742148.1759 | 1239174.8223 | 2742139.4357 | 1239174.8353 | 2742112.9084 | 1239172.5205 | 2742108.2544 | 1239167.7938 | 2742103.0336 | 1239166.5121 | 2742099.7338 | 1239167.2631
38 | 2741882.9618 | 1239690.4882 | 2741864.3589 | 1239657.1581 | 2741845.0264 | 1239599.2663 | 2741840.054 | 1239574.6364 | 2741829.2392 | 1239553.2144 | 2741820.2513 | 1239527.5321 | 2741813.9432 | 1239526.4805 | 2741807.459 | 1239533.4319 | 2741801.4852 | 1239554.486 | 2741797.7377 | 1239559.3231 | 2741791.8857 | 1239561.3518 | 2741786.9356 | 1239567.7505 | 2741781.4148 | 1239588.8487 | 2741771.3121 | 1239614.2415 | 2741758.2326 | 1239625.8397 | 2741758.0361 | 1239644.8298 | 2741756.2719 | 1239652.7949 | 2741749.418 | 1239661.2945 | 2741738.8978 | 1239666.8039 | 2741724.4017 | 1239666.4464 | 2741699.8695 | 1239700.7473 | 2741698.6298 | 1239714.9528 | 2741691.2019 | 1239724.3617 | 2741694.8618 | 1239730.1543 | 2741692.2616 | 1239741.9409
39 | 2742099.7338 | 1239167.2631 | 2742098.1261 | 1239167.629 | 2742095.4016 | 1239167.9641 | 2742092.9092 | 1239164.924 | 2742087.6298 | 1239163.8745 | 2742085.4032 | 1239164.1702
40 | 2741650.4597 | 1237442.0477 | 2741644.1089 | 1237441.6168
41 | 2741650.4597 | 1237442.0477 | 2741678.6521 | 1237443.9605 | 2741698.0279 | 1237442.1099 | 2741718.0003 | 1237437.1486 | 2741736.6592 | 1237432.1234
42 | 2741230.5682 | 1237321.4246 | 2741260.2159 | 1237330.0595 | 2741276.5855 | 1237332.7178 | 2741288.7708 | 1237333.4083 | 2741298.5199 | 1237331.5052 | 2741307.1574 | 1237329.8759 | 2741315.4622 | 1237330.1403 | 2741322.3305 | 1237331.605 | 2741332.9611 | 1237337.1852 | 2741361.007 | 1237362.8533 | 2741371.8399 | 1237369.15 | 2741408.6741 | 1237373.186 | 2741487.0831 | 1237401.7898 | 2741551.0324 | 1237431.1063 | 2741570.6863 | 1237436.6352 | 2741644.1089 | 1237441.6168
43 | 2742048.9107 | 1239109.4658 | 2742056.4852 | 1239145.8131 | 2742070.6869 | 1239162.946 | 2742079.401 | 1239164.9675 | 2742085.4032 | 1239164.1702
44 | 2741294.9534 | 1238929.005 | 2741471.2776 | 1239439.3513
45 | 2741838.0261 | 1240575.7687 | 2741850.422 | 1240540.166 | 2741851.422 | 1240498.3522 | 2741846.5175 | 1240481.6755 | 2741840.3155 | 1240471.1734 | 2741839.1571 | 1240448.1138 | 2741833.5544 | 1240419.821 | 2741823.2209 | 1240393.5282 | 2741818.7769 | 1240371.8247 | 2741809.5071 | 1240353.242 | 2741813.4235 | 1240340.057 | 2741802.8775 | 1240313.1475 | 2741791.5624 | 1240293.4039 | 2741791.7172 | 1240272.3664 | 2741786.5808 | 1240244.1738 | 2741758.1272 | 1240182.4165 | 2741696.4328 | 1240095.1651 | 2741685.047 | 1240077.077 | 2741671.0699 | 1240063.5869 | 2741659.1371 | 1240056.9962 | 2741646.0897 | 1240045.7526 | 2741633.1889 | 1240026.7833 | 2741625.6596 | 1239996.7322 | 2741631.171 | 1239989.3014 | 2741638.3291 | 1239984.2009 | 2741643.0414 | 1239970.9458 | 2741649.0049 | 1239942.3623 | 2741656.3337 | 1239922.1968 | 2741658.602 | 1239894.6928 | 2741682.2361 | 1239838.0835 | 2741682.3574 | 1239825.0858 | 2741675.6955 | 1239802.4287 | 2741675.6587 | 1239782.7434 | 2741687.0812 | 1239765.4226 | 2741692.2616 | 1239741.9409
46 | 2741260.866 | 1239911.7542 | 2741269.4102 | 1239901.8152 | 2741295.2042 | 1239861.0924 | 2741311.0442 | 1239851.7054 | 2741332.6569 | 1239825.4962 | 2741350.4937 | 1239791.0565 | 2741365.5587 | 1239775.1453 | 2741369.8568 | 1239751.3151 | 2741384.1598 | 1239738.1772 | 2741385.5956 | 1239726.8234 | 2741391.4736 | 1239724.6392 | 2741418.9582 | 1239686.7041 | 2741432.9274 | 1239677.7399 | 2741449.7223 | 1239638.171 | 2741465.1027 | 1239606.2087 | 2741468.8071 | 1239597.4557 | 2741470.0821 | 1239589.0452 | 2741469.5786 | 1239575.8881 | 2741470.5408 | 1239572.0298 | 2741470.5525 | 1239568.6826 | 2741470.5883 | 1239561.1544 | 2741468.7656 | 1239552.2363 | 2741468.3695 | 1239528.55 | 2741473.7017 | 1239522.2937 | 2741478.0863 | 1239519.6068 | 2741481.089 | 1239512.9947 | 2741474.9384 | 1239502.4831 | 2741472.9433 | 1239493.4942 | 2741474.2043 | 1239486.9405 | 2741474.0205 | 1239484.812 | 2741471.7037 | 1239481.6985 | 2741470.7206 | 1239475.0135 | 2741477.3223 | 1239460.58 | 2741474.365 | 1239455.138 | 2741472.2309 | 1239449.4376 | 2741471.2776 | 1239439.3513
47 | 2741838.0261 | 1240575.7687 | 2741839.5025 | 1240540.9169 | 2741837.6583 | 1240514.9049 | 2741831.463 | 1240501.5893 | 2741821.0799 | 1240494.1457 | 2741809.7022 | 1240491.5938 | 2741795.0013 | 1240495.4573 | 2741780.6495 | 1240506.8693 | 2741772.9049 | 1240514.0575 | 2741757.439 | 1240505.6139 | 2741751.7856 | 1240506.3531
48 | 2741751.7856 | 1240506.3531 | 2741741.5477 | 1240507.6919 | 2741731.7712 | 1240504.2998
49 | 2741731.7712 | 1240504.2998 | 2741411.5748 | 1240973.9146
50 | 2741411.5748 | 1240973.9146 | 2741401.8707 | 1240971.1764 | 2741376.6934 | 1240955.7184 | 2741365.4349 | 1240946.6915
51 | 2741729.4289 | 1241444.9686 | 2741721.9604 | 1241440.3561 | 2741717.1758 | 1241405.7105 | 2741707.874 | 1241388.5284 | 2741654.4312 | 1241358.5368 | 2741626.1098 | 1241343.3806 | 2741596.4109 | 1241315.5803 | 2741580.5991 | 1241303.6479 | 2741565.3903 | 1241286.4141 | 2741534.2131 | 1241263.4832 | 2741509.4832 | 1241231.2423 | 2741471.2711 | 1241160.7233 | 2741468.083 | 1241145.6448 | 2741441.0743 | 1241115.9856 | 2741445.0596 | 1241078.9248 | 2741443.0777 | 1241069.0909 | 2741424.2245 | 1241041.5947 | 2741427.5558 | 1241022.7571 | 2741419.8501 | 1241001.71 | 2741421.7605 | 1240976.7886 | 2741411.5748 | 1240973.9146
52 | 2741735.6535 | 1241448.8129 | 2741735.6535 | 1241448.8129 | 2741729.4289 | 1241444.9686
53 | 2741347.3732 | 1240932.2101 | 2741365.4349 | 1240946.6915

## bus_geodata
| x | y | coords
0 | 2742397.487 | 1235695.096
1 | 2742397.742 | 1235685.649
2 | 2742319.707 | 1236069.4887
3 | 2742337.1981 | 1235635.5536
4 | 2742161.4131 | 1237065.7563
5 | 2741914.9765 | 1237233.1578
6 | 2741956.3811 | 1235709.3754
7 | 2741930.7406 | 1235723.4643
8 | 2742271.8112 | 1235632.0511
9 | 2741561.2777 | 1235583.2698
10 | 2741912.9649 | 1235523.8508
11 | 2741854.6195 | 1235581.7758
12 | 2742224.8695 | 1235653.1572
13 | 2742296.7906 | 1235648.7531
14 | 2741517.2566 | 1235602.3381
15 | 2741545.2297 | 1235585.1729
16 | 2741508.9631 | 1235591.6421
17 | 2742109.022 | 1237438.1385
18 | 2742140.4346 | 1237410.0515
19 | 2742103.7541 | 1237442.2916
20 | 2741989.5522 | 1237407.0957
21 | 2742663.7789 | 1238296.3064
22 | 2741805.9731 | 1237413.4558
23 | 2742138.3777 | 1237837.4262
24 | 2742538.7586 | 1238405.9496
25 | 2741785.0511 | 1237419.0905
26 | 2742137.5342 | 1237840.751
27 | 2741668.3391 | 1237248.7955
28 | 2742591.6204 | 1238600.6809
29 | 2742136.3912 | 1237845.2561
30 | 2741752.8126 | 1237427.773
31 | 2741959.8497 | 1238751.6364
32 | 2741955.476 | 1238753.857
33 | 2741946.1968 | 1238758.5682
34 | 2742206.8064 | 1239200.9608
35 | 2741882.9618 | 1239690.4882
36 | 2742099.7338 | 1239167.2631
37 | 2741650.4597 | 1237442.0477
38 | 2741644.1089 | 1237441.6168
39 | 2741736.6592 | 1237432.1234
40 | 2741230.5682 | 1237321.4246
41 | 2742085.4032 | 1239164.1702
42 | 2742048.9107 | 1239109.4658
43 | 2741294.9534 | 1238929.005
44 | 2741692.2616 | 1239741.9409
45 | 2741471.2776 | 1239439.3512
46 | 2741260.866 | 1239911.7542
47 | 2741838.0261 | 1240575.7687
48 | 2741751.7856 | 1240506.3531
49 | 2741731.7712 | 1240504.2998
50 | 2741411.5748 | 1240973.9146
51 | 2741735.6535 | 1241448.8129
52 | 2741729.4289 | 1241444.9686
53 | 2741365.4349 | 1240946.6915
54 | 2741347.3732 | 1240932.2101
55 | 2742345.6201 | 1236096.7339

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1