## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3023-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3023-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3023-2_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3023-2_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3023-2_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3023-2_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3023-2_0_6_node_112 | 0.4 | n |  | TRUE
7 | bus_LV_3023-2_0_6_node_97 | 0.4 | n |  | TRUE
8 | bus_LV_3023-2_0_6_node_90 | 0.4 | n |  | TRUE
9 | bus_LV_3023-2_0_6_node_103 | 0.4 | n |  | TRUE
10 | bus_LV_3023-2_0_6_node_98 | 0.4 | n |  | TRUE
11 | bus_LV_3023-2_0_6_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_3023-2_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_3023-2_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_3023-2_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_3023-2_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3023-2_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_3023-2_0_6_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_3023-2_0_6_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_3023-2_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_3023-2_0_6_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_3023-2_0_6_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_3023-2_0_6_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_3023-2_0_6_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_3023-2_0_6_node_170 | 0.4 | n |  | TRUE
25 | bus_LV_3023-2_0_6_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_3023-2_0_6_node_193 | 0.4 | n |  | TRUE
27 | bus_LV_3023-2_0_6_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_3023-2_0_6_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_3023-2_0_6_node_45 | 0.4 | n |  | TRUE
30 | bus_LV_3023-2_0_6_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_3023-2_0_6_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_3023-2_0_6_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_3023-2_0_6_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_3023-2_0_6_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_3023-2_0_6_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_3023-2_0_6_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_3023-2_0_6_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_3023-2_0_6_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_3023-2_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_3023-2_0_6_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_3023-2_0_6_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_3023-2_0_6_node_172 | 0.4 | n |  | TRUE
43 | bus_LV_3023-2_0_6_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_3023-2_0_6_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_3023-2_0_6_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_3023-2_0_6_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_3023-2_0_6_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_3023-2_0_6_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_3023-2_0_6_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_3023-2_0_6_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_3023-2_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_3023-2_0_6_node_92 | 0.4 | n |  | TRUE
53 | bus_LV_3023-2_0_6_node_68 | 0.4 | n |  | TRUE
54 | bus_LV_3023-2_0_6_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_3023-2_0_6_node_93 | 0.4 | n |  | TRUE
56 | bus_LV_3023-2_0_6_node_91 | 0.4 | n |  | TRUE
57 | bus_LV_3023-2_0_6_node_176 | 0.4 | n |  | TRUE
58 | bus_LV_3023-2_0_6_node_175 | 0.4 | n |  | TRUE
59 | bus_LV_3023-2_0_6_node_155 | 0.4 | n |  | TRUE
60 | bus_LV_3023-2_0_6_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_3023-2_0_6_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_3023-2_0_6_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_3023-2_0_6_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_3023-2_0_6_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_3023-2_0_6_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_3023-2_0_6_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_3023-2_0_6_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_3023-2_0_6_node_96 | 0.4 | n |  | TRUE
69 | bus_LV_3023-2_0_6_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_3023-2_0_6_node_195 | 0.4 | n |  | TRUE
71 | bus_LV_3023-2_0_6_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_3023-2_0_6_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_3023-2_0_6_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_3023-2_0_6_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_3023-2_0_6_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_3023-2_0_6_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_3023-2_0_6_node_44 | 0.4 | n |  | TRUE
78 | bus_LV_3023-2_0_6_node_194 | 0.4 | n |  | TRUE
79 | bus_LV_3023-2_0_6_node_171 | 0.4 | n |  | TRUE
80 | bus_LV_3023-2_0_6_node_49 | 0.4 | n |  | TRUE
81 | bus_LV_3023-2_0_6_node_50 | 0.4 | n |  | TRUE
82 | bus_LV_3023-2_0_6_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_3023-2_0_6_node_53 | 0.4 | n |  | TRUE
84 | bus_LV_3023-2_0_6_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_3023-2_0_6_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_3023-2_0_6_node_123 | 0.4 | n |  | TRUE
87 | bus_LV_3023-2_0_6_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_3023-2_0_6_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_3023-2_0_6_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_3023-2_0_6_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_3023-2_0_6_node_59 | 0.4 | n |  | TRUE
92 | bus_LV_3023-2_0_6_node_105 | 0.4 | n |  | TRUE
93 | bus_LV_3023-2_0_6_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_3023-2_0_6_node_108 | 0.4 | n |  | TRUE
95 | bus_LV_3023-2_0_6_node_173 | 0.4 | n |  | TRUE
96 | bus_LV_3023-2_0_6_node_141 | 0.4 | n |  | TRUE
97 | bus_LV_3023-2_0_6_node_107 | 0.4 | n |  | TRUE
98 | bus_LV_3023-2_0_6_node_109 | 0.4 | n |  | TRUE
99 | bus_LV_3023-2_0_6_node_185 | 0.4 | n |  | TRUE
100 | bus_LV_3023-2_0_6_node_145 | 0.4 | n |  | TRUE
101 | bus_LV_3023-2_0_6_node_110 | 0.4 | n |  | TRUE
102 | bus_LV_3023-2_0_6_node_157 | 0.4 | n |  | TRUE
103 | bus_LV_3023-2_0_6_node_113 | 0.4 | n |  | TRUE
104 | bus_LV_3023-2_0_6_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_3023-2_0_6_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_3023-2_0_6_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_3023-2_0_6_node_138 | 0.4 | n |  | TRUE
108 | bus_LV_3023-2_0_6_node_189 | 0.4 | n |  | TRUE
109 | bus_LV_3023-2_0_6_node_190 | 0.4 | n |  | TRUE
110 | bus_LV_3023-2_0_6_node_191 | 0.4 | n |  | TRUE
111 | bus_LV_3023-2_0_6_node_192 | 0.4 | n |  | TRUE
112 | bus_LV_3023-2_0_6_node_74 | 0.4 | n |  | TRUE
113 | bus_LV_3023-2_0_6_node_75 | 0.4 | n |  | TRUE
114 | bus_LV_3023-2_0_6_node_135 | 0.4 | n |  | TRUE
115 | bus_LV_3023-2_0_6_node_79 | 0.4 | n |  | TRUE
116 | bus_LV_3023-2_0_6_node_78 | 0.4 | n |  | TRUE
117 | bus_LV_3023-2_0_6_node_140 | 0.4 | n |  | TRUE
118 | bus_LV_3023-2_0_6_node_139 | 0.4 | n |  | TRUE
119 | bus_LV_3023-2_0_6_node_142 | 0.4 | n |  | TRUE
120 | bus_LV_3023-2_0_6_node_80 | 0.4 | n |  | TRUE
121 | bus_LV_3023-2_0_6_node_164 | 0.4 | n |  | TRUE
122 | bus_LV_3023-2_0_6_node_147 | 0.4 | n |  | TRUE
123 | bus_LV_3023-2_0_6_node_81 | 0.4 | n |  | TRUE
124 | bus_LV_3023-2_0_6_node_163 | 0.4 | n |  | TRUE
125 | bus_LV_3023-2_0_6_node_162 | 0.4 | n |  | TRUE
126 | bus_LV_3023-2_0_6_node_134 | 0.4 | n |  | TRUE
127 | bus_LV_3023-2_0_6_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_3023-2_0_6_node_137 | 0.4 | n |  | TRUE
129 | bus_LV_3023-2_0_6_node_148 | 0.4 | n |  | TRUE
130 | bus_LV_3023-2_0_6_node_149 | 0.4 | n |  | TRUE
131 | bus_LV_3023-2_0_6_node_146 | 0.4 | n |  | TRUE
132 | bus_LV_3023-2_0_6_node_161 | 0.4 | n |  | TRUE
133 | bus_LV_3023-2_0_6_node_158 | 0.4 | n |  | TRUE
134 | bus_LV_3023-2_0_6_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_3023-2_0_6_node_188 | 0.4 | n |  | TRUE
136 | bus_LV_3023-2_0_6_node_154 | 0.4 | n |  | TRUE
137 | bus_LV_3023-2_0_6_node_116 | 0.4 | n |  | TRUE
138 | bus_LV_3023-2_0_6_node_114 | 0.4 | n |  | TRUE
139 | bus_LV_3023-2_0_6_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_3023-2_0_6_node_83 | 0.4 | n |  | TRUE
141 | bus_LV_3023-2_0_6_node_84 | 0.4 | n |  | TRUE
142 | bus_LV_3023-2_0_6_node_85 | 0.4 | n |  | TRUE
143 | bus_LV_3023-2_0_6_node_86 | 0.4 | n |  | TRUE
144 | bus_LV_3023-2_0_6_node_87 | 0.4 | n |  | TRUE
145 | bus_LV_3023-2_0_6_node_88 | 0.4 | n |  | TRUE
146 | bus_LV_3023-2_0_6_node_89 | 0.4 | n |  | TRUE
147 | bus_LV_3023-2_0_6_node_121 | 0.4 | n |  | TRUE
148 | bus_LV_3023-2_0_6_node_120 | 0.4 | n |  | TRUE
149 | bus_LV_3023-2_0_6_node_165 | 0.4 | n |  | TRUE
150 | bus_LV_3023-2_0_6_node_166 | 0.4 | n |  | TRUE
151 | bus_LV_3023-2_0_6_node_167 | 0.4 | n |  | TRUE
152 | bus_LV_3023-2_0_6_node_101 | 0.4 | n |  | TRUE
153 | bus_LV_3023-2_0_6_node_102 | 0.4 | n |  | TRUE
154 | bus_LV_3023-2_0_6_node_111 | 0.4 | n |  | TRUE
155 | bus_LV_3023-2_0_6_node_177 | 0.4 | n |  | TRUE
156 | bus_LV_3023-2_0_6_node_186 | 0.4 | n |  | TRUE
157 | bus_LV_3023-2_0_6_node_115 | 0.4 | n |  | TRUE
158 | bus_LV_3023-2_0_6_node_117 | 0.4 | n |  | TRUE
159 | bus_LV_3023-2_0_6_node_118 | 0.4 | n |  | TRUE
160 | bus_LV_3023-2_0_6_node_196 | 0.4 | n |  | TRUE
161 | bus_LV_3023-2_0_6_node_119 | 0.4 | n |  | TRUE
162 | bus_LV_3023-2_0_6_node_124 | 0.4 | n |  | TRUE
163 | bus_LV_3023-2_0_6_node_127 | 0.4 | n |  | TRUE
164 | bus_LV_3023-2_0_6_node_174 | 0.4 | n |  | TRUE
165 | bus_LV_3023-2_0_6_node_128 | 0.4 | n |  | TRUE
166 | bus_LV_3023-2_0_6_node_129 | 0.4 | n |  | TRUE
167 | bus_LV_3023-2_0_6_node_130 | 0.4 | n |  | TRUE
168 | bus_LV_3023-2_0_6_node_132 | 0.4 | n |  | TRUE
169 | bus_LV_3023-2_0_6_node_133 | 0.4 | n |  | TRUE
170 | bus_LV_3023-2_0_6_node_143 | 0.4 | n |  | TRUE
171 | bus_LV_3023-2_0_6_node_144 | 0.4 | n |  | TRUE
172 | bus_LV_3023-2_0_6_node_187 | 0.4 | n |  | TRUE
173 | bus_LV_3023-2_0_6_node_159 | 0.4 | n |  | TRUE
174 | bus_LV_3023-2_0_6_node_156 | 0.4 | n |  | TRUE
175 | bus_LV_3023-2_0_6_node_169 | 0.4 | n |  | TRUE
176 | bus_LV_3023-2_0_6_node_168 | 0.4 | n |  | TRUE
177 | bus_LV_3023-2_0_6_node_150 | 0.4 | n |  | TRUE
178 | bus_LV_3023-2_0_6_node_151 | 0.4 | n |  | TRUE
179 | bus_LV_3023-2_0_6_node_152 | 0.4 | n |  | TRUE
180 | bus_LV_3023-2_0_6_node_153 | 0.4 | n |  | TRUE
181 | bus_LV_3023-2_0_6_node_178 | 0.4 | n |  | TRUE
182 | bus_LV_3023-2_0_6_node_160 | 0.4 | n |  | TRUE
183 | bus_LV_3023-2_0_6_node_184 | 0.4 | n |  | TRUE
184 | bus_LV_3023-2_0_6_node_179 | 0.4 | n |  | TRUE
185 | bus_LV_3023-2_0_6_node_180 | 0.4 | n |  | TRUE
186 | bus_LV_3023-2_0_6_node_183 | 0.4 | n |  | TRUE
187 | bus_LV_3023-2_0_6_node_182 | 0.4 | n |  | TRUE
188 | bus_LV_3023-2_0_6_node_181 | 0.4 | n |  | TRUE
189 | bus_MV_41_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3023-2_0_6_load_0 | 0 | 0.003132 | 0.00078496 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3023-2_0_6_load_1 | 1 | 0.001367 | 0.0003426 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3023-2_0_6_load_3 | 3 | 0.0049219 | 0.0012335 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3023-2_0_6_load_4 | 4 | 0.0018831 | 0.00047196 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3023-2_0_6_load_5 | 5 | 0.003011 | 0.00075462 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3023-2_0_6_load_97 | 7 | 0.0035313 | 0.00088503 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3023-2_0_6_load_90 | 8 | 0.0030557 | 0.00076583 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3023-2_0_6_load_103 | 9 | 0.0021266 | 0.00053298 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3023-2_0_6_load_16 | 11 | 0.0015001 | 0.00037596 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3023-2_0_6_load_6 | 12 | 0.0038472 | 0.00096421 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3023-2_0_6_load_7 | 13 | 0.0025263 | 0.00063316 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3023-2_0_6_load_9 | 15 | 0.0041001 | 0.0010276 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3023-2_0_6_load_10 | 16 | 0.002116 | 0.00053031 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3023-2_0_6_load_55 | 17 | 0.0040388 | 0.0010122 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3023-2_0_6_load_48 | 18 | 0.0027575 | 0.00069109 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3023-2_0_6_load_63 | 20 | 0.0031634 | 0.00079283 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3023-2_0_6_load_170 | 24 | 0.0026237 | 0.00065757 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3023-2_0_6_load_193 | 26 | 0.0045489 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3023-2_0_6_load_21 | 27 | 0.0031851 | 0.00079826 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3023-2_0_6_load_19 | 28 | 0.0039308 | 0.00098515 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3023-2_0_6_load_27 | 30 | 0.0016741 | 0.00041957 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3023-2_0_6_load_13 | 32 | 0.0026098 | 0.00065407 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3023-2_0_6_load_14 | 33 | 0.0024964 | 0.00062565 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3023-2_0_6_load_15 | 34 | 0.0027203 | 0.00068176 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3023-2_0_6_load_17 | 35 | 0.0024171 | 0.00060579 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3023-2_0_6_load_62 | 36 | 0.0027701 | 0.00069426 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3023-2_0_6_load_18 | 37 | 0.002115 | 0.00053006 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3023-2_0_6_load_22 | 39 | 0.0021988 | 0.00055108 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3023-2_0_6_load_23 | 40 | 0.0012087 | 0.00030293 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3023-2_0_6_load_24 | 41 | 0.0021795 | 0.00054624 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3023-2_0_6_load_172 | 42 | 0.0046587 | 0.0011676 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3023-2_0_6_load_26 | 44 | 0.0030826 | 0.00077257 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3023-2_0_6_load_28 | 45 | 0.0051004 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3023-2_0_6_load_31 | 48 | 0.0067944 | 0.0017028 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3023-2_0_6_load_34 | 51 | 0.0069518 | 0.0017423 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3023-2_0_6_load_66 | 54 | 0.0017008 | 0.00042627 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3023-2_0_6_load_93 | 55 | 0.0029451 | 0.00073811 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3023-2_0_6_load_91 | 56 | 0.0036861 | 0.00092382 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3023-2_0_6_load_176 | 57 | 0.0073613 | 0.0018449 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3023-2_0_6_load_175 | 58 | 0.0035705 | 0.00089484 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3023-2_0_6_load_155 | 59 | 0.0048053 | 0.0012043 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3023-2_0_6_load_52 | 60 | 0.0071423 | 0.00179 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3023-2_0_6_load_67 | 61 | 0.0012387 | 0.00031045 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3023-2_0_6_load_35 | 62 | 0.0028 | 0.00070174 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3023-2_0_6_load_36 | 63 | 0.0025455 | 0.00063797 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3023-2_0_6_load_39 | 66 | 0.0026885 | 0.00067379 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3023-2_0_6_load_96 | 68 | 0.0012384 | 0.00031038 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3023-2_0_6_load_195 | 70 | 0.018663 | 0.0046773 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3023-2_0_6_load_70 | 73 | 0.002409 | 0.00060375 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3023-2_0_6_load_40 | 75 | 0.0026774 | 0.00067103 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3023-2_0_6_load_194 | 78 | 0.0020923 | 0.00052437 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3023-2_0_6_load_171 | 79 | 0.0095719 | 0.0023989 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3023-2_0_6_load_49 | 80 | 0.0051515 | 0.0012911 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3023-2_0_6_load_50 | 81 | 0.0014284 | 0.00035799 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3023-2_0_6_load_53 | 83 | 0.0023044 | 0.00057753 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3023-2_0_6_load_54 | 84 | 0.0038671 | 0.00096919 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3023-2_0_6_load_73 | 85 | 0.0034686 | 0.00086931 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3023-2_0_6_load_72 | 87 | 0.0012681 | 0.00031782 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3023-2_0_6_load_122 | 88 | 0.0011939 | 0.00029922 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3023-2_0_6_load_57 | 89 | 0.0099312 | 0.002489 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3023-2_0_6_load_58 | 90 | 0.0038192 | 0.00095717 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3023-2_0_6_load_59 | 91 | 0.0024708 | 0.00061924 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3023-2_0_6_load_141 | 96 | 0.0024633 | 0.00061737 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3023-2_0_6_load_185 | 99 | 0.005931 | 0.0014864 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3023-2_0_6_load_145 | 100 | 0.031819 | 0.0079746 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3023-2_0_6_load_157 | 102 | 0.01449 | 0.0036314 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3023-2_0_6_load_113 | 103 | 0.022815 | 0.0057181 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3023-2_0_6_load_104 | 104 | 0.0071135 | 0.0017828 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3023-2_0_6_load_100 | 105 | 0.0036228 | 0.00090796 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3023-2_0_6_load_99 | 106 | 0.002621 | 0.00065689 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3023-2_0_6_load_138 | 107 | 0.0051575 | 0.0012926 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3023-2_0_6_load_190 | 109 | 0.002262 | 0.00056691 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3023-2_0_6_load_191 | 110 | 0.002153 | 0.00053959 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3023-2_0_6_load_192 | 111 | 0.0038913 | 0.00097524 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3023-2_0_6_load_75 | 113 | 0.003775 | 0.00094609 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3023-2_0_6_load_139 | 118 | 0.0059462 | 0.0014903 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3023-2_0_6_load_142 | 119 | 0.0027375 | 0.00068607 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3023-2_0_6_load_147 | 122 | 0.0035109 | 0.00087991 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3023-2_0_6_load_163 | 124 | 0.0014525 | 0.00036402 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3023-2_0_6_load_162 | 125 | 0.0014639 | 0.0003669 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3023-2_0_6_load_134 | 126 | 0.0044057 | 0.0011042 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3023-2_0_6_load_125 | 127 | 0.0010206 | 0.0002558 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3023-2_0_6_load_146 | 131 | 0.011375 | 0.0028509 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3023-2_0_6_load_161 | 132 | 0.0023939 | 0.00059998 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3023-2_0_6_load_158 | 133 | 0.0035366 | 0.00088636 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3023-2_0_6_load_131 | 134 | 0.0023878 | 0.00059845 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3023-2_0_6_load_188 | 135 | 0.0043895 | 0.0011001 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3023-2_0_6_load_126 | 139 | 0.0011939 | 0.00029922 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3023-2_0_6_load_83 | 140 | 0.0037521 | 0.00094037 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3023-2_0_6_load_84 | 141 | 0.0038075 | 0.00095426 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3023-2_0_6_load_86 | 143 | 0.0060923 | 0.0015269 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3023-2_0_6_load_87 | 144 | 0.0037172 | 0.00093162 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3023-2_0_6_load_88 | 145 | 0.0042966 | 0.0010768 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3023-2_0_6_load_89 | 146 | 0.0022777 | 0.00057084 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3023-2_0_6_load_120 | 148 | 0.0017812 | 0.00044642 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3023-2_0_6_load_166 | 150 | 0.014487 | 0.0036307 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3023-2_0_6_load_167 | 151 | 0.0022216 | 0.00055678 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3023-2_0_6_load_102 | 153 | 0.00097552 | 0.00024449 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3023-2_0_6_load_111 | 154 | 0.00092023 | 0.00023063 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3023-2_0_6_load_177 | 155 | 0.0027797 | 0.00069667 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3023-2_0_6_load_186 | 156 | 0.015723 | 0.0039406 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3023-2_0_6_load_115 | 157 | 0.0055239 | 0.0013844 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3023-2_0_6_load_196 | 160 | 0.0043257 | 0.0010841 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3023-2_0_6_load_119 | 161 | 0.003108 | 0.00077895 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3023-2_0_6_load_127 | 163 | 0.0017054 | 0.00042741 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3023-2_0_6_load_174 | 164 | 0.0014578 | 0.00036537 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3023-2_0_6_load_128 | 165 | 0.0019899 | 0.00049871 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3023-2_0_6_load_129 | 166 | 0.0015063 | 0.00037753 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3023-2_0_6_load_132 | 168 | 0.0075378 | 0.0018892 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3023-2_0_6_load_133 | 169 | 0.0046066 | 0.0011545 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3023-2_0_6_load_143 | 170 | 0.0098531 | 0.0024694 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3023-2_0_6_load_187 | 172 | 0.0065358 | 0.001638 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3023-2_0_6_load_159 | 173 | 0.0036657 | 0.0009187 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3023-2_0_6_load_168 | 176 | 0.00052836 | 0.00013242 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3023-2_0_6_load_150 | 177 | 0.0010024 | 0.00025123 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3023-2_0_6_load_151 | 178 | 0.0046806 | 0.0011731 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3023-2_0_6_load_152 | 179 | 0.0030142 | 0.00075543 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3023-2_0_6_load_153 | 180 | 0.0017428 | 0.00043678 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3023-2_0_6_load_178 | 181 | 0.00057982 | 0.00014532 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3023-2_0_6_load_160 | 182 | 0.0069448 | 0.0017405 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3023-2_0_6_load_184 | 183 | 0.015704 | 0.0039357 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3023-2_0_6_load_180 | 185 | 0.0020139 | 0.00050473 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3023-2_0_6_load_181 | 188 | 0.0033765 | 0.00084624 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3023-2_0_6_line_0 |  | 0 | 1 | 0.0022935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3023-2_0_6_line_1 |  | 0 | 2 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3023-2_0_6_line_2 |  | 1 | 3 | 0.024638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3023-2_0_6_line_3 |  | 2 | 4 | 0.0060299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3023-2_0_6_line_4 |  | 2 | 5 | 0.0020104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3023-2_0_6_line_5 |  | 3 | 6 | 0.020575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3023-2_0_6_line_6 |  | 4 | 7 | 0.0023827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3023-2_0_6_line_7 |  | 5 | 8 | 0.026646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3023-2_0_6_line_8 |  | 6 | 9 | 0.030265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3023-2_0_6_line_9 |  | 7 | 10 | 0.018482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3023-2_0_6_line_10 |  | 8 | 11 | 0.0132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3023-2_0_6_line_11 |  | 9 | 152 | 0.0047323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3023-2_0_6_line_12 |  | 10 | 104 | 0.0038538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3023-2_0_6_line_13 |  | 11 | 33 | 0.0042637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3023-2_0_6_line_14 |  | 12 | 13 | 0.0040573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3023-2_0_6_line_15 |  | 12 | 14 | 0.023379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3023-2_0_6_line_16 |  | 13 | 15 | 0.046513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3023-2_0_6_line_17 |  | 14 | 16 | 0.010187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3023-2_0_6_line_18 |  | 15 | 17 | 0.0094312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3023-2_0_6_line_19 |  | 16 | 18 | 0.00068109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3023-2_0_6_line_20 |  | 17 | 21 | 0.01348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3023-2_0_6_line_21 |  | 18 | 19 | 0.02383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3023-2_0_6_line_22 |  | 19 | 20 | 0.017033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3023-2_0_6_line_23 |  | 20 | 22 | 0.018097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3023-2_0_6_line_24 |  | 21 | 89 | 0.016726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3023-2_0_6_line_25 |  | 21 | 90 | 0.046685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3023-2_0_6_line_26 |  | 22 | 36 | 0.0061347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3023-2_0_6_line_27 |  | 22 | 91 | 0.034594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3023-2_0_6_line_28 |  | 23 | 24 | 0.01229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3023-2_0_6_line_29 |  | 23 | 25 | 0.009562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3023-2_0_6_line_30 |  | 24 | 71 | 0.0078569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3023-2_0_6_line_31 |  | 25 | 26 | 0.03647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3023-2_0_6_line_32 |  | 27 | 28 | 0.015041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3023-2_0_6_line_33 |  | 28 | 37 | 0.027148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3023-2_0_6_line_34 |  | 29 | 30 | 0.01695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3023-2_0_6_line_35 |  | 29 | 31 | 0.021068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3023-2_0_6_line_36 |  | 30 | 43 | 0.059505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3023-2_0_6_line_37 |  | 31 | 78 | 0.027979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3023-2_0_6_line_38 |  | 31 | 76 | 0.019269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3023-2_0_6_line_39 |  | 32 | 33 | 0.01527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3023-2_0_6_line_40 |  | 32 | 34 | 0.0070467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3023-2_0_6_line_41 |  | 34 | 35 | 0.0065166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3023-2_0_6_line_42 |  | 35 | 36 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3023-2_0_6_line_43 |  | 37 | 38 | 0.0070425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3023-2_0_6_line_44 |  | 38 | 39 | 0.010517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3023-2_0_6_line_45 |  | 38 | 40 | 0.0082595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3023-2_0_6_line_46 |  | 39 | 41 | 0.021072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3023-2_0_6_line_47 |  | 40 | 42 | 0.020011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3023-2_0_6_line_48 |  | 41 | 43 | 0.0024276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3023-2_0_6_line_49 |  | 43 | 44 | 0.020436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3023-2_0_6_line_50 |  | 45 | 46 | 0.018763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_3023-2_0_6_line_51 |  | 45 | 47 | 0.014623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_3023-2_0_6_line_52 |  | 46 | 48 | 0.013825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3023-2_0_6_line_53 |  | 46 | 49 | 0.021615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_3023-2_0_6_line_54 |  | 47 | 50 | 0.022412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_3023-2_0_6_line_55 |  | 47 | 51 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3023-2_0_6_line_56 |  | 49 | 52 | 0.007257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_3023-2_0_6_line_57 |  | 50 | 53 | 0.010981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_3023-2_0_6_line_58 |  | 50 | 54 | 0.034763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3023-2_0_6_line_59 |  | 52 | 55 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3023-2_0_6_line_60 |  | 52 | 56 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3023-2_0_6_line_61 |  | 53 | 59 | 0.015712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3023-2_0_6_line_62 |  | 53 | 60 | 0.011723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_3023-2_0_6_line_63 |  | 54 | 61 | 0.01544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3023-2_0_6_line_64 |  | 55 | 149 | 0.015999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3023-2_0_6_line_65 |  | 56 | 89 | 0.0060848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3023-2_0_6_line_66 |  | 57 | 58 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3023-2_0_6_line_67 |  | 58 | 129 | 0.030414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3023-2_0_6_line_68 |  | 60 | 81 | 0.0144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_3023-2_0_6_line_69 |  | 62 | 63 | 0.022284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3023-2_0_6_line_70 |  | 62 | 64 | 0.020096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3023-2_0_6_line_71 |  | 64 | 65 | 0.010737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3023-2_0_6_line_72 |  | 64 | 66 | 0.01636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3023-2_0_6_line_73 |  | 65 | 67 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3023-2_0_6_line_74 |  | 65 | 68 | 0.0088601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3023-2_0_6_line_75 |  | 66 | 69 | 0.015501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3023-2_0_6_line_76 |  | 67 | 70 | 0.049601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3023-2_0_6_line_77 |  | 67 | 71 | 0.084438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3023-2_0_6_line_78 |  | 68 | 72 | 0.039998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3023-2_0_6_line_79 |  | 69 | 73 | 0.016689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3023-2_0_6_line_80 |  | 69 | 74 | 0.030124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3023-2_0_6_line_81 |  | 71 | 79 | 0.00701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3023-2_0_6_line_82 |  | 72 | 115 | 0.0065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3023-2_0_6_line_83 |  | 72 | 112 | 0.018325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_3023-2_0_6_line_84 |  | 73 | 77 | 0.0026695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3023-2_0_6_line_85 |  | 74 | 108 | 0.005627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3023-2_0_6_line_86 |  | 74 | 109 | 0.056413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3023-2_0_6_line_87 |  | 75 | 76 | 0.013037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3023-2_0_6_line_88 |  | 76 | 77 | 0.025114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3023-2_0_6_line_89 |  | 80 | 81 | 0.021801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_3023-2_0_6_line_90 |  | 80 | 82 | 0.008727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_3023-2_0_6_line_91 |  | 82 | 83 | 0.017834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_3023-2_0_6_line_92 |  | 82 | 84 | 0.015428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_3023-2_0_6_line_93 |  | 83 | 85 | 0.0052565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_3023-2_0_6_line_94 |  | 84 | 86 | 0.0073991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_3023-2_0_6_line_95 |  | 85 | 87 | 0.013935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_3023-2_0_6_line_96 |  | 86 | 88 | 0.015582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_3023-2_0_6_line_97 |  | 87 | 112 | 0.0026194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_3023-2_0_6_line_98 |  | 88 | 162 | 0.0030549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_3023-2_0_6_line_99 |  | 92 | 93 | 0.057971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3023-2_0_6_line_100 |  | 92 | 94 | 0.012184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3023-2_0_6_line_101 |  | 93 | 95 | 0.046178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3023-2_0_6_line_102 |  | 93 | 96 | 0.049896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3023-2_0_6_line_103 |  | 94 | 100 | 0.0063096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3023-2_0_6_line_104 |  | 95 | 155 | 0.014831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3023-2_0_6_line_105 |  | 95 | 150 | 0.013392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3023-2_0_6_line_106 |  | 96 | 147 | 0.0055489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3023-2_0_6_line_107 |  | 97 | 98 | 0.057138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3023-2_0_6_line_108 |  | 97 | 99 | 0.052249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3023-2_0_6_line_109 |  | 98 | 101 | 0.006384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3023-2_0_6_line_110 |  | 98 | 102 | 0.023173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_3023-2_0_6_line_111 |  | 99 | 156 | 0.0013757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3023-2_0_6_line_112 |  | 101 | 103 | 0.011102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3023-2_0_6_line_113 |  | 103 | 138 | 0.027492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3023-2_0_6_line_114 |  | 104 | 107 | 0.021893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3023-2_0_6_line_115 |  | 105 | 106 | 0.021006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3023-2_0_6_line_116 |  | 106 | 152 | 0.0092735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3023-2_0_6_line_117 |  | 108 | 110 | 0.016702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3023-2_0_6_line_118 |  | 108 | 111 | 0.021698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3023-2_0_6_line_119 |  | 112 | 113 | 0.025269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_3023-2_0_6_line_120 |  | 113 | 114 | 0.0086766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_3023-2_0_6_line_121 |  | 114 | 126 | 0.029829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_3023-2_0_6_line_122 |  | 114 | 127 | 0.0070865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3023-2_0_6_line_123 |  | 115 | 119 | 0.0082647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_3023-2_0_6_line_124 |  | 116 | 117 | 0.003457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_3023-2_0_6_line_125 |  | 116 | 118 | 0.012892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3023-2_0_6_line_126 |  | 117 | 132 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3023-2_0_6_line_127 |  | 117 | 133 | 0.04011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3023-2_0_6_line_128 |  | 119 | 134 | 0.0053938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3023-2_0_6_line_129 |  | 120 | 121 | 0.023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_3023-2_0_6_line_130 |  | 120 | 122 | 0.034237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_3023-2_0_6_line_131 |  | 121 | 135 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_3023-2_0_6_line_132 |  | 121 | 136 | 0.004713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_3023-2_0_6_line_133 |  | 122 | 131 | 0.024338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_3023-2_0_6_line_134 |  | 123 | 124 | 0.015864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_3023-2_0_6_line_135 |  | 123 | 125 | 0.0041014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_3023-2_0_6_line_136 |  | 124 | 139 | 0.016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_3023-2_0_6_line_137 |  | 125 | 136 | 0.029692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_3023-2_0_6_line_138 |  | 128 | 129 | 0.033403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_3023-2_0_6_line_139 |  | 128 | 130 | 0.02077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_3023-2_0_6_line_140 |  | 128 | 131 | 0.017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_3023-2_0_6_line_141 |  | 129 | 137 | 0.007931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_3023-2_0_6_line_142 |  | 130 | 172 | 0.016942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_3023-2_0_6_line_143 |  | 132 | 169 | 0.0096299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_3023-2_0_6_line_144 |  | 133 | 173 | 0.015058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_3023-2_0_6_line_145 |  | 134 | 166 | 0.011454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_3023-2_0_6_line_146 |  | 136 | 179 | 0.0077196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_3023-2_0_6_line_147 |  | 137 | 138 | 0.018765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_3023-2_0_6_line_148 |  | 138 | 157 | 0.011916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_3023-2_0_6_line_149 |  | 139 | 162 | 0.011012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
150 | LV_3023-2_0_6_line_150 |  | 140 | 141 | 0.014054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_3023-2_0_6_line_151 |  | 140 | 142 | 0.0088864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_3023-2_0_6_line_152 |  | 141 | 143 | 0.012412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_3023-2_0_6_line_153 |  | 142 | 144 | 0.013214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_3023-2_0_6_line_154 |  | 142 | 145 | 0.028895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_3023-2_0_6_line_155 |  | 142 | 146 | 0.032068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_3023-2_0_6_line_156 |  | 146 | 147 | 0.0039008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_3023-2_0_6_line_157 |  | 147 | 148 | 0.0091068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_3023-2_0_6_line_158 |  | 148 | 161 | 0.011307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_3023-2_0_6_line_159 |  | 149 | 150 | 0.041408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_3023-2_0_6_line_160 |  | 149 | 151 | 0.015214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_3023-2_0_6_line_161 |  | 152 | 153 | 0.020602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_3023-2_0_6_line_162 |  | 153 | 154 | 0.0044161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_3023-2_0_6_line_163 |  | 157 | 158 | 0.02465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_3023-2_0_6_line_164 |  | 158 | 159 | 0.007312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_3023-2_0_6_line_165 |  | 159 | 160 | 0.009363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_3023-2_0_6_line_166 |  | 162 | 163 | 0.0081286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_3023-2_0_6_line_167 |  | 163 | 164 | 0.0029716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_3023-2_0_6_line_168 |  | 165 | 166 | 0.00092601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_3023-2_0_6_line_169 |  | 165 | 167 | 0.0059389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_3023-2_0_6_line_170 |  | 167 | 168 | 0.013122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_3023-2_0_6_line_171 |  | 167 | 169 | 0.014721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_3023-2_0_6_line_172 |  | 168 | 170 | 0.016082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_3023-2_0_6_line_173 |  | 170 | 171 | 0.029427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_3023-2_0_6_line_174 |  | 171 | 174 | 0.06408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_3023-2_0_6_line_175 |  | 173 | 182 | 0.012186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_3023-2_0_6_line_176 |  | 174 | 175 | 0.073225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_3023-2_0_6_line_177 |  | 174 | 176 | 0.021544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_3023-2_0_6_line_178 |  | 175 | 181 | 0.028412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_3023-2_0_6_line_179 |  | 177 | 178 | 0.01112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_3023-2_0_6_line_180 |  | 177 | 179 | 0.020983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_3023-2_0_6_line_181 |  | 178 | 180 | 0.003883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_3023-2_0_6_line_182 |  | 181 | 184 | 0.016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_3023-2_0_6_line_183 |  | 182 | 183 | 0.020134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_3023-2_0_6_line_184 |  | 184 | 185 | 0.019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_3023-2_0_6_line_185 |  | 185 | 186 | 0.0188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_3023-2_0_6_line_186 |  | 186 | 187 | 0.016338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_3023-2_0_6_line_187 |  | 187 | 188 | 0.018976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3023-2_0_6_trafo_28 | 0.63 MVA 20/0.4 kV | 189 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2751277.9315 | 1253245.5452 | 2751278.4438 | 1253247.7807
1 | 2751275.5692 | 1253230.5472 | 2751275.5701 | 1253235.2407 | 2751277.9315 | 1253245.5452
2 | 2751278.4438 | 1253247.7807 | 2751279.0748 | 1253250.534 | 2751282.1651 | 1253272.1272
3 | 2751275.5692 | 1253230.5472 | 2751270.1009 | 1253228.0061
4 | 2751275.5692 | 1253230.5472 | 2751277.482 | 1253231.1662
5 | 2751291.7109 | 1253289.5949 | 2751283.5264 | 1253279.8764 | 2751282.4441 | 1253274.0764 | 2751282.1651 | 1253272.1272
6 | 2751270.1009 | 1253228.0061 | 2751267.9402 | 1253227.002
7 | 2751277.482 | 1253231.1662 | 2751286.6885 | 1253234.1457 | 2751303.475 | 1253236.6321
8 | 2751291.7109 | 1253289.5949 | 2751261.4643 | 1253288.5285
9 | 2751251.1791 | 1253219.2133 | 2751267.9402 | 1253227.002
10 | 2751316.398 | 1253239.2996 | 2751305.8374 | 1253236.982 | 2751303.475 | 1253236.6321
11 | 2751256.7352 | 1253288.3561 | 2751260.7402 | 1253288.503 | 2751261.4643 | 1253288.5285
12 | 2751251.1791 | 1253219.2133 | 2751247.7951 | 1253217.3693
13 | 2751316.398 | 1253239.2996 | 2751320.5625 | 1253240.2135
14 | 2751395.3153 | 1253203.8529 | 2751392.9284 | 1253200.572
15 | 2751410.2107 | 1253221.6558 | 2751408.0775 | 1253220.3445 | 2751403.9673 | 1253215.746 | 2751395.3153 | 1253203.8529
16 | 2751369.296 | 1253160.5512 | 2751379.8655 | 1253178.6828 | 2751389.1766 | 1253195.4148 | 2751392.9284 | 1253200.572
17 | 2751410.2107 | 1253221.6558 | 2751406.5036 | 1253231.1443
18 | 2751364.5463 | 1253152.4034 | 2751369.296 | 1253160.5512
19 | 2751406.2558 | 1253231.7787 | 2751406.5036 | 1253231.1443
20 | 2751358.0776 | 1253140.5777 | 2751363.4117 | 1253150.457 | 2751364.5463 | 1253152.4034
21 | 2751401.654 | 1253254.8252 | 2751402.1482 | 1253242.2922 | 2751406.2558 | 1253231.7787
22 | 2751401.654 | 1253254.8252 | 2751384.6792 | 1253253.4173
23 | 2751366.5988 | 1253253.4391 | 2751380.9063 | 1253253.1044 | 2751384.6792 | 1253253.4173
24 | 2751358.0776 | 1253140.5777 | 2751352.2741 | 1253124.8906
25 | 2751358.0776 | 1253140.5777 | 2751387.2103 | 1253128.8439 | 2751395.8048 | 1253141.4748
26 | 2751366.5988 | 1253253.4391 | 2751362.0536 | 1253249.319
27 | 2751366.5988 | 1253253.4391 | 2751362.1875 | 1253255.5952 | 2751356.7332 | 1253258.0916 | 2751352.5458 | 1253262.1219 | 2751349.0088 | 1253267.8816 | 2751346.7251 | 1253277.1768 | 2751346.4671 | 1253278.6984
28 | 2751594.1849 | 1253082.6801 | 2751593.6552 | 1253074.1805 | 2751591.9108 | 1253070.8335
29 | 2751603.7578 | 1253082.1023 | 2751594.1849 | 1253082.6801
30 | 2751588.2796 | 1253063.8661 | 2751591.9108 | 1253070.8335
31 | 2751603.7578 | 1253082.1023 | 2751602.0031 | 1253045.6773
32 | 2751455.1438 | 1253190.1538 | 2751469.1201 | 1253195.7112
33 | 2751455.1438 | 1253190.1538 | 2751449.1583 | 1253187.7738 | 2751444.5414 | 1253184.6861 | 2751440.8067 | 1253178.985 | 2751439.1976 | 1253172.8267 | 2751439.1765 | 1253170.8552
34 | 2751536.73 | 1253163.2001 | 2751532.2948 | 1253163.6316 | 2751521.5063 | 1253157.3301
35 | 2751536.73 | 1253163.2001 | 2751535.1312 | 1253142.1942
36 | 2751468.1225 | 1253145.317 | 2751479.2126 | 1253138.8498 | 2751508.7231 | 1253152.1842 | 2751512.1215 | 1253151.8485 | 2751521.5063 | 1253157.3301
37 | 2751514.2155 | 1253132.5721 | 2751514.346 | 1253139.2709 | 2751517.7909 | 1253141.2498 | 2751535.1312 | 1253142.1942
38 | 2751533.6677 | 1253122.9825 | 2751535.1312 | 1253142.1942
39 | 2751335.4778 | 1253243.4868 | 2751320.5625 | 1253240.2135
40 | 2751335.4778 | 1253243.4868 | 2751342.3607 | 1253244.9973
41 | 2751348.7258 | 1253246.3941 | 2751342.3607 | 1253244.9973
42 | 2751362.0536 | 1253249.319 | 2751348.7258 | 1253246.3941
43 | 2751440.1555 | 1253164.0093 | 2751439.1308 | 1253166.5856 | 2751439.1765 | 1253170.8552
44 | 2751440.1555 | 1253164.0093 | 2751442.3662 | 1253160.8182 | 2751447.5531 | 1253156.6801
45 | 2751440.1555 | 1253164.0093 | 2751432.3006 | 1253161.456
46 | 2751447.5531 | 1253156.6801 | 2751447.5531 | 1253156.6801 | 2751465.9976 | 1253146.4909
47 | 2751412.7555 | 1253164.0868 | 2751429.0756 | 1253160.645 | 2751430.8336 | 1253160.9791 | 2751432.3006 | 1253161.456
48 | 2751468.1225 | 1253145.317 | 2751465.9976 | 1253146.4909
49 | 2751468.1225 | 1253145.317 | 2751471.4417 | 1253151.6192 | 2751483.2248 | 1253157.8933
50 | 2751370.715 | 1253081.8654 | 2751385.9066 | 1253070.853
51 | 2751397.7464 | 1253062.2703 | 2751385.9066 | 1253070.853
52 | 2751370.715 | 1253081.8654 | 2751365.8954 | 1253076.9597 | 2751358.9645 | 1253076.4707
53 | 2751370.715 | 1253081.8654 | 2751353.7537 | 1253095.323
54 | 2751416.5356 | 1253049.9718 | 2751397.7464 | 1253062.2703
55 | 2751397.7464 | 1253062.2703 | 2751394.628 | 1253056.674 | 2751385.5508 | 1253055.8843
56 | 2751350.0679 | 1253101.5794 | 2751353.7537 | 1253095.323
57 | 2751416.5356 | 1253049.9718 | 2751425.5165 | 1253043.6173
58 | 2751416.5356 | 1253049.9718 | 2751420.6456 | 1253055.1708 | 2751430.5599 | 1253075.7777 | 2751432.4482 | 1253080.6959
59 | 2751350.0679 | 1253101.5794 | 2751346.221 | 1253101.1473 | 2751336.3891 | 1253106.9053
60 | 2751350.0679 | 1253101.5794 | 2751351.3382 | 1253118.9287
61 | 2751425.5165 | 1253043.6173 | 2751420.5152 | 1253037.2499 | 2751412.9219 | 1253036.6712
62 | 2751425.5165 | 1253043.6173 | 2751435.0835 | 1253036.8427
63 | 2751431.1384 | 1253095.5979 | 2751432.9375 | 1253092.0321 | 2751433.3961 | 1253085.6153 | 2751432.5135 | 1253080.8659 | 2751432.4482 | 1253080.6959
64 | 2751322.5835 | 1253114.9904 | 2751336.3891 | 1253106.9053
65 | 2751351.3382 | 1253118.9287 | 2751351.6515 | 1253123.2076 | 2751352.2741 | 1253124.8906
66 | 2751315.0862 | 1253060.9092 | 2751323.4673 | 1253067.7223 | 2751326.6268 | 1253069.6998
67 | 2751291.4863 | 1253041.7246 | 2751315.0862 | 1253060.9092
68 | 2751435.0835 | 1253036.8427 | 2751437.1887 | 1253035.352 | 2751446.8952 | 1253030.4398 | 2751447.7844 | 1253030.1281
69 | 2751491.3387 | 1253039.1067 | 2751495.0185 | 1253041.9369 | 2751497.886 | 1253048.4833 | 2751500.6138 | 1253048.9869 | 2751508.3112 | 1253048.3906
70 | 2751528.3467 | 1253046.8385 | 2751508.3112 | 1253048.3906
71 | 2751528.3467 | 1253046.8385 | 2751527.5714 | 1253036.1304
72 | 2751528.3467 | 1253046.8385 | 2751529.5222 | 1253063.156
73 | 2751527.5714 | 1253036.1304 | 2751540.2381 | 1253035.6206
74 | 2751527.5714 | 1253036.1304 | 2751526.9349 | 1253027.2932
75 | 2751530.6361 | 1253078.6171 | 2751529.5222 | 1253063.156
76 | 2751540.2381 | 1253035.6206 | 2751544.8744 | 1253032.0579 | 2751555.702 | 1253031.7234 | 2751572.9483 | 1253030.4523 | 2751572.3616 | 1253014.7441
77 | 2751540.2381 | 1253035.6206 | 2751541.4973 | 1253059.2759 | 2751538.8601 | 1253059.3641 | 2751538.9455 | 1253061.3349 | 2751539.1029 | 1253064.3307 | 2751540.207 | 1253064.2589 | 2751546.7311 | 1253063.9255 | 2751549.5354 | 1253063.7971 | 2751552.6226 | 1253068.8365 | 2751583.3975 | 1253067.3001 | 2751588.2796 | 1253063.8661
78 | 2751524.0096 | 1252987.4028 | 2751524.8643 | 1252998.5466 | 2751526.9349 | 1253027.2932
79 | 2751530.6361 | 1253078.6171 | 2751531.6089 | 1253095.2776
80 | 2751500.8026 | 1253078.4762 | 2751505.7843 | 1253080.2942 | 2751530.6361 | 1253078.6171
81 | 2751588.2796 | 1253063.8661 | 2751587.8397 | 1253056.8703
82 | 2751524.0096 | 1252987.4028 | 2751523.7001 | 1252980.9107
83 | 2751507.0722 | 1252993.4088 | 2751516.6745 | 1252988.1492 | 2751519.8948 | 1252987.6978 | 2751524.0096 | 1252987.4028
84 | 2751531.7645 | 1253097.9426 | 2751531.6089 | 1253095.2776
85 | 2751500.8026 | 1253078.4762 | 2751495.8633 | 1253081.197
86 | 2751500.8026 | 1253078.4762 | 2751498.4507 | 1253072.1431 | 2751490.6783 | 1253060.1883 | 2751481.2555 | 1253051.3609 | 2751477.2579 | 1253049.1454 | 2751472.6109 | 1253050.4723 | 2751468.2469 | 1253052.8409 | 2751462.3628 | 1253058.5516
87 | 2751533.6677 | 1253122.9825 | 2751545.324 | 1253123.3031 | 2751546.4307 | 1253124.1219
88 | 2751533.6677 | 1253122.9825 | 2751532.3692 | 1253105.8769 | 2751531.7645 | 1253097.9426
89 | 2751467.4317 | 1253021.0025 | 2751464.1458 | 1253023.3961 | 2751458.4292 | 1253026.3973 | 2751447.7844 | 1253030.1281
90 | 2751474.4857 | 1253015.8642 | 2751467.4317 | 1253021.0025
91 | 2751474.4857 | 1253015.8642 | 2751484.013 | 1253010.5804 | 2751489.5787 | 1253006.4358
92 | 2751474.4857 | 1253015.8642 | 2751463.2547 | 1253005.286
93 | 2751489.5787 | 1253006.4358 | 2751493.7947 | 1253003.2963
94 | 2751457.8686 | 1253000.2129 | 2751463.2547 | 1253005.286
95 | 2751504.9713 | 1252994.9733 | 2751493.7947 | 1253003.2963
96 | 2751457.8686 | 1253000.2129 | 2751446.1245 | 1252989.9719
97 | 2751507.0722 | 1252993.4088 | 2751504.9713 | 1252994.9733
98 | 2751443.822 | 1252987.9641 | 2751446.1245 | 1252989.9719
99 | 2751239.6727 | 1253169.6044 | 2751232.4704 | 1253166.3507 | 2751223.2707 | 1253159.4202 | 2751224.4747 | 1253152.7778 | 2751224.5033 | 1253145.7494 | 2751234.0571 | 1253147.0946 | 2751241.1396 | 1253140.8582 | 2751246.6955 | 1253142.0679
100 | 2751249.1897 | 1253130.1421 | 2751246.6955 | 1253142.0679
101 | 2751280.2665 | 1253148.0865 | 2751275.4924 | 1253151.7348 | 2751243.6543 | 1253165.9469 | 2751239.6727 | 1253169.6044
102 | 2751239.6727 | 1253169.6044 | 2751265.5934 | 1253178.0745 | 2751287.0284 | 1253185.3211
103 | 2751249.1897 | 1253130.1421 | 2751255.4972 | 1253130.3033
104 | 2751294.502 | 1253146.1481 | 2751292.0981 | 1253145.0857 | 2751288.1584 | 1253145.6301 | 2751280.2665 | 1253148.0865
105 | 2751280.2665 | 1253148.0865 | 2751280.4416 | 1253145.6664 | 2751288.6362 | 1253138.3805
106 | 2751292.285 | 1253187.0982 | 2751287.0284 | 1253185.3211
107 | 2751245.4113 | 1253078.2839 | 2751242.083 | 1253074.9846 | 2751240.8856 | 1253074.2755 | 2751239.4528 | 1253073.9164 | 2751237.936 | 1253073.8888 | 2751236.5023 | 1253074.1524 | 2751235.2677 | 1253074.8994 | 2751234.1956 | 1253076.0843 | 2751213.3052 | 1253102.6771 | 2751209.3837 | 1253100.1412 | 2751208.2674 | 1253099.2118 | 2751205.4415 | 1253096.9374
108 | 2751205.4415 | 1253096.9374 | 2751204.4053 | 1253095.5318 | 2751203.5548 | 1253093.953 | 2751202.8644 | 1253092.3116 | 2751202.4991 | 1253090.3559 | 2751202.3573 | 1253087.9277 | 2751202.5963 | 1253085.6649 | 2751202.925 | 1253083.4378 | 2751203.5065 | 1253081.3617 | 2751204.251 | 1253079.1118 | 2751205.4104 | 1253076.5834 | 2751220.5705 | 1253049.9193
109 | 2751245.4113 | 1253078.2839 | 2751249.9546 | 1253082.782
110 | 2751245.4113 | 1253078.2839 | 2751260.4194 | 1253060.6278
111 | 2751220.5705 | 1253049.9193 | 2751221.2504 | 1253048.7234
112 | 2751249.9546 | 1253082.782 | 2751255.4791 | 1253077.5402 | 2751257.8827 | 1253075.0146
113 | 2751273.8391 | 1253052.7736 | 2751269.8504 | 1253059.9566 | 2751266.5903 | 1253064.9227 | 2751260.5219 | 1253072.2415 | 2751257.8827 | 1253075.0146
114 | 2751228.0717 | 1253207.9322 | 2751238.7148 | 1253212.4107 | 2751242.5492 | 1253214.5107 | 2751247.7951 | 1253217.3693
115 | 2751249.5105 | 1253282.5422 | 2751243.76 | 1253277.9147 | 2751238.9428 | 1253265.1699
116 | 2751256.7352 | 1253288.3561 | 2751249.5105 | 1253282.5422
117 | 2751495.8633 | 1253081.197 | 2751487.2979 | 1253082.2345 | 2751480.6847 | 1253086.9367
118 | 2751486.5657 | 1253100.8117 | 2751495.8633 | 1253081.197
119 | 2751507.0722 | 1252993.4088 | 2751493.3541 | 1252974.2281 | 2751491.9531 | 1252973.2866
120 | 2751484.7516 | 1252968.447 | 2751491.9531 | 1252973.2866
121 | 2751484.7516 | 1252968.447 | 2751484.8448 | 1252943.5695 | 2751488.7688 | 1252940.5506
122 | 2751484.7516 | 1252968.447 | 2751477.6881 | 1252968.9113 | 2751477.6822 | 1252968.9162
123 | 2751523.7001 | 1252980.9107 | 2751531.7915 | 1252979.2271 | 2751531.7915 | 1252979.2271
124 | 2751526.1723 | 1252933.0049 | 2751522.7151 | 1252933.2723
125 | 2751522.7151 | 1252933.2723 | 2751520.6247 | 1252920.5508
126 | 2751526.1723 | 1252933.0049 | 2751537.3424 | 1252947.6727
127 | 2751526.1723 | 1252933.0049 | 2751561.9739 | 1252928.9055 | 2751565.4502 | 1252926.7808
128 | 2751531.7915 | 1252979.2271 | 2751536.5564 | 1252976.6994
129 | 2751373.9317 | 1252966.4236 | 2751370.793 | 1252961.9168 | 2751363.6695 | 1252957.3414 | 2751354.8426 | 1252953.8347
130 | 2751354.8426 | 1252953.8347 | 2751353.6072 | 1252956.9729 | 2751349.4147 | 1252964.74 | 2751343.463 | 1252973.0961 | 2751335.9498 | 1252982.1682
131 | 2751373.9317 | 1252966.4236 | 2751371.0396 | 1252967.9178 | 2751362.6744 | 1252974.1101 | 2751357.7754 | 1252978.8007
132 | 2751376.6262 | 1252970.2962 | 2751373.9317 | 1252966.4236
133 | 2751322.6805 | 1253001.9474 | 2751332.186 | 1252989.8244 | 2751332.4317 | 1252986.4163 | 2751335.9498 | 1252982.1682
134 | 2751408.3145 | 1252964.9452 | 2751415.5723 | 1252966.332 | 2751422.9754 | 1252970.4569
135 | 2751408.3145 | 1252964.9452 | 2751404.2267 | 1252964.6106
136 | 2751435.5197 | 1252980.7295 | 2751425.0707 | 1252971.6244 | 2751422.9754 | 1252970.4569
137 | 2751376.6262 | 1252970.2962 | 2751387.7536 | 1252963.2626 | 2751404.2267 | 1252964.6106
138 | 2751291.4863 | 1253041.7246 | 2751312.1208 | 1253015.4147
139 | 2751327.9007 | 1253028.9755 | 2751312.1208 | 1253015.4147
140 | 2751312.1208 | 1253015.4147 | 2751322.6805 | 1253001.9474
141 | 2751284.7305 | 1253037.5369 | 2751291.4863 | 1253041.7246
142 | 2751327.9007 | 1253028.9755 | 2751338.6254 | 1253015.8366
143 | 2751537.3424 | 1252947.6727 | 2751543.1768 | 1252955.334
144 | 2751578.2986 | 1252918.9282 | 2751565.4502 | 1252926.7808
145 | 2751536.5564 | 1252976.6994 | 2751542.4917 | 1252973.5508 | 2751546.412 | 1252970.8955
146 | 2751376.6262 | 1252970.2962 | 2751380.3591 | 1252977.0533
147 | 2751284.7305 | 1253037.5369 | 2751276.452 | 1253048.0246 | 2751273.8391 | 1253052.7736
148 | 2751273.8391 | 1253052.7736 | 2751283.3746 | 1253059.9198
149 | 2751443.822 | 1252987.9641 | 2751435.5197 | 1252980.7295
150 | 2751335.555 | 1253198.0057 | 2751344.7762 | 1253198.3944 | 2751349.005 | 1253200.7158
151 | 2751326.6764 | 1253197.6313 | 2751335.555 | 1253198.0057
152 | 2751353.305 | 1253212.3593 | 2751349.005 | 1253200.7158
153 | 2751326.6764 | 1253197.6313 | 2751332.9317 | 1253209.2803
154 | 2751326.6764 | 1253197.6313 | 2751320.7371 | 1253187.503 | 2751319.0091 | 1253175.3581 | 2751314.7294 | 1253172.9576
155 | 2751326.6764 | 1253197.6313 | 2751315.7366 | 1253194.3932 | 2751296.0098 | 1253188.2569
156 | 2751292.285 | 1253187.0982 | 2751296.0098 | 1253188.2569
157 | 2751292.285 | 1253187.0982 | 2751298.6296 | 1253193.6312
158 | 2751306.5074 | 1253201.7429 | 2751298.6296 | 1253193.6312
159 | 2751322.5835 | 1253114.9904 | 2751317.7251 | 1253117.5021 | 2751299.5077 | 1253128.7145 | 2751288.6362 | 1253138.3805
160 | 2751314.211 | 1253127.6779 | 2751318.0254 | 1253121.1133 | 2751322.5835 | 1253114.9904
161 | 2751256.7352 | 1253288.3561 | 2751260.6885 | 1253292.5946 | 2751266.5591 | 1253298.617 | 2751269.5489 | 1253303.0421 | 2751269.7642 | 1253304.0749
162 | 2751270.6652 | 1253308.3981 | 2751269.7642 | 1253304.0749
163 | 2751292.2171 | 1253080.7703 | 2751290.8478 | 1253065.5204 | 2751283.3746 | 1253059.9198
164 | 2751292.2171 | 1253080.7703 | 2751295.5691 | 1253087.2734
165 | 2751295.5691 | 1253087.2734 | 2751303.3237 | 1253092.5543
166 | 2751443.822 | 1252987.9641 | 2751446.7043 | 1252980.3637
167 | 2751444.5289 | 1252978.3394 | 2751446.7043 | 1252980.3637
168 | 2751547.1787 | 1252970.3762 | 2751546.412 | 1252970.8955
169 | 2751552.0958 | 1252967.0457 | 2751547.1787 | 1252970.3762
170 | 2751552.0958 | 1252967.0457 | 2751565.0193 | 1252964.771
171 | 2751552.0958 | 1252967.0457 | 2751543.1768 | 1252955.334
172 | 2751565.0193 | 1252964.771 | 2751569.638 | 1252963.9581 | 2751580.4658 | 1252960.4178
173 | 2751606.4507 | 1252947.495 | 2751596.2938 | 1252955.2427 | 2751580.4658 | 1252960.4178
174 | 2751606.4507 | 1252947.495 | 2751610.2529 | 1252943.4884 | 2751626.2481 | 1252907.6627 | 2751631.0363 | 1252903.4811 | 2751643.0777 | 1252898.5067
175 | 2751578.2986 | 1252918.9282 | 2751588.6966 | 1252912.5732
176 | 2751643.0777 | 1252898.5067 | 2751650.7509 | 1252896.3565 | 2751658.6309 | 1252889.9631 | 2751691.031 | 1252872.7757 | 2751708.6616 | 1252866.8436
177 | 2751643.0777 | 1252898.5067 | 2751652.8286 | 1252909.8562 | 2751654.2376 | 1252916.2848
178 | 2751708.6616 | 1252866.8436 | 2751710.0547 | 1252880.5371 | 2751710.532 | 1252891.371 | 2751710.4387 | 1252895.1735
179 | 2751392.3297 | 1252993.6314 | 2751385.7052 | 1253002.5627
180 | 2751392.3297 | 1252993.6314 | 2751392.3297 | 1252993.6314 | 2751391.6432 | 1252990.3662 | 2751383.438 | 1252982.6268 | 2751380.3591 | 1252977.0533
181 | 2751383.3919 | 1253005.6815 | 2751385.7052 | 1253002.5627
182 | 2751709.2197 | 1252911.9353 | 2751710.1913 | 1252905.2537 | 2751710.4387 | 1252895.1735
183 | 2751600.7402 | 1252927.2624 | 2751598.8065 | 1252921.1069 | 2751593.6668 | 1252914.5468 | 2751588.6966 | 1252912.5732 | 2751588.6966 | 1252912.5732
184 | 2751709.2197 | 1252911.9353 | 2751710.6655 | 1252916.7993 | 2751717.9352 | 1252925.672 | 2751720.4842 | 1252927.2462
185 | 2751736.4791 | 1252937.1247 | 2751720.4842 | 1252927.2462
186 | 2751736.4791 | 1252937.1247 | 2751739.8815 | 1252941.9388 | 2751736.4182 | 1252948.3342 | 2751736.3367 | 1252951.513
187 | 2751736.3367 | 1252951.513 | 2751737.914 | 1252954.1893 | 2751752.1371 | 1252961.2286

## bus_geodata
| x | y | coords
0 | 2751277.9315 | 1253245.5452
1 | 2751278.4438 | 1253247.7807
2 | 2751275.5692 | 1253230.5472
3 | 2751282.1651 | 1253272.1272
4 | 2751270.1009 | 1253228.0061
5 | 2751277.482 | 1253231.1662
6 | 2751291.7109 | 1253289.5949
7 | 2751267.9402 | 1253227.002
8 | 2751303.475 | 1253236.6321
9 | 2751261.4643 | 1253288.5285
10 | 2751251.1791 | 1253219.2133
11 | 2751316.398 | 1253239.2996
12 | 2751395.3153 | 1253203.8529
13 | 2751392.9284 | 1253200.572
14 | 2751410.2107 | 1253221.6558
15 | 2751369.296 | 1253160.5512
16 | 2751406.5036 | 1253231.1443
17 | 2751364.5463 | 1253152.4034
18 | 2751406.2558 | 1253231.7787
19 | 2751401.654 | 1253254.8252
20 | 2751384.6792 | 1253253.4173
21 | 2751358.0776 | 1253140.5777
22 | 2751366.5988 | 1253253.4391
23 | 2751594.1849 | 1253082.6801
24 | 2751591.9108 | 1253070.8335
25 | 2751603.7578 | 1253082.1023
26 | 2751602.0031 | 1253045.6773
27 | 2751469.1201 | 1253195.7112
28 | 2751455.1438 | 1253190.1538
29 | 2751536.73 | 1253163.2001
30 | 2751521.5063 | 1253157.3301
31 | 2751535.1312 | 1253142.1942
32 | 2751335.4778 | 1253243.4868
33 | 2751320.5625 | 1253240.2135
34 | 2751342.3607 | 1253244.9973
35 | 2751348.7258 | 1253246.3941
36 | 2751362.0536 | 1253249.319
37 | 2751439.1765 | 1253170.8552
38 | 2751440.1555 | 1253164.0093
39 | 2751447.5531 | 1253156.6801
40 | 2751432.3006 | 1253161.456
41 | 2751465.9976 | 1253146.4909
42 | 2751412.7555 | 1253164.0868
43 | 2751468.1225 | 1253145.317
44 | 2751483.2248 | 1253157.8933
45 | 2751385.9066 | 1253070.853
46 | 2751370.715 | 1253081.8654
47 | 2751397.7464 | 1253062.2703
48 | 2751358.9645 | 1253076.4707
49 | 2751353.7537 | 1253095.323
50 | 2751416.5356 | 1253049.9718
51 | 2751385.5508 | 1253055.8843
52 | 2751350.0679 | 1253101.5794
53 | 2751425.5165 | 1253043.6173
54 | 2751432.4482 | 1253080.6959
55 | 2751336.3891 | 1253106.9053
56 | 2751351.3382 | 1253118.9287
57 | 2751326.6268 | 1253069.6998
58 | 2751315.0862 | 1253060.9092
59 | 2751412.9219 | 1253036.6712
60 | 2751435.0835 | 1253036.8427
61 | 2751431.1384 | 1253095.5979
62 | 2751508.3112 | 1253048.3906
63 | 2751491.3387 | 1253039.1067
64 | 2751528.3467 | 1253046.8385
65 | 2751527.5714 | 1253036.1304
66 | 2751529.5222 | 1253063.156
67 | 2751540.2381 | 1253035.6206
68 | 2751526.9349 | 1253027.2932
69 | 2751530.6361 | 1253078.617
70 | 2751572.3616 | 1253014.7441
71 | 2751588.2796 | 1253063.8661
72 | 2751524.0096 | 1252987.4028
73 | 2751531.6089 | 1253095.2776
74 | 2751500.8026 | 1253078.4762
75 | 2751546.4307 | 1253124.1219
76 | 2751533.6677 | 1253122.9825
77 | 2751531.7645 | 1253097.9426
78 | 2751514.2155 | 1253132.5721
79 | 2751587.8397 | 1253056.8703
80 | 2751467.4317 | 1253021.0025
81 | 2751447.7844 | 1253030.1281
82 | 2751474.4857 | 1253015.8642
83 | 2751489.5787 | 1253006.4358
84 | 2751463.2547 | 1253005.286
85 | 2751493.7947 | 1253003.2963
86 | 2751457.8686 | 1253000.2129
87 | 2751504.9713 | 1252994.9733
88 | 2751446.1245 | 1252989.9719
89 | 2751352.2741 | 1253124.8906
90 | 2751395.8048 | 1253141.4748
91 | 2751346.4671 | 1253278.6984
92 | 2751246.6955 | 1253142.0679
93 | 2751239.6727 | 1253169.6044
94 | 2751249.1897 | 1253130.1421
95 | 2751280.2665 | 1253148.0865
96 | 2751287.0284 | 1253185.3211
97 | 2751205.4415 | 1253096.9374
98 | 2751245.4113 | 1253078.2839
99 | 2751220.5705 | 1253049.9193
100 | 2751255.4972 | 1253130.3033
101 | 2751249.9546 | 1253082.782
102 | 2751260.4194 | 1253060.6278
103 | 2751257.8827 | 1253075.0146
104 | 2751247.7951 | 1253217.3693
105 | 2751238.9428 | 1253265.1699
106 | 2751249.5105 | 1253282.5422
107 | 2751228.0717 | 1253207.9322
108 | 2751495.8633 | 1253081.197
109 | 2751462.3628 | 1253058.5516
110 | 2751480.6847 | 1253086.9367
111 | 2751486.5657 | 1253100.8117
112 | 2751507.0722 | 1252993.4088
113 | 2751491.9531 | 1252973.2866
114 | 2751484.7516 | 1252968.447
115 | 2751523.7001 | 1252980.9107
116 | 2751522.7151 | 1252933.2723
117 | 2751526.1723 | 1252933.0049
118 | 2751520.6247 | 1252920.5508
119 | 2751531.7915 | 1252979.2271
120 | 2751354.8426 | 1252953.8347
121 | 2751373.9317 | 1252966.4236
122 | 2751335.9498 | 1252982.1682
123 | 2751408.3145 | 1252964.9452
124 | 2751422.9754 | 1252970.4569
125 | 2751404.2267 | 1252964.6106
126 | 2751488.7688 | 1252940.5506
127 | 2751477.6822 | 1252968.9162
128 | 2751312.1208 | 1253015.4147
129 | 2751291.4863 | 1253041.7246
130 | 2751327.9007 | 1253028.9755
131 | 2751322.6805 | 1253001.9474
132 | 2751537.3424 | 1252947.6727
133 | 2751565.4502 | 1252926.7808
134 | 2751536.5564 | 1252976.6994
135 | 2751357.7754 | 1252978.8007
136 | 2751376.6262 | 1252970.2962
137 | 2751284.7305 | 1253037.5369
138 | 2751273.8391 | 1253052.7736
139 | 2751435.5197 | 1252980.7295
140 | 2751335.555 | 1253198.0057
141 | 2751349.005 | 1253200.7158
142 | 2751326.6764 | 1253197.6313
143 | 2751353.305 | 1253212.3593
144 | 2751332.9317 | 1253209.2803
145 | 2751314.7294 | 1253172.9576
146 | 2751296.0098 | 1253188.2568
147 | 2751292.285 | 1253187.0982
148 | 2751298.6296 | 1253193.6312
149 | 2751322.5835 | 1253114.9904
150 | 2751288.6362 | 1253138.3805
151 | 2751314.211 | 1253127.6779
152 | 2751256.7352 | 1253288.3562
153 | 2751269.7642 | 1253304.0749
154 | 2751270.6652 | 1253308.3981
155 | 2751294.502 | 1253146.1481
156 | 2751221.2504 | 1253048.7234
157 | 2751283.3746 | 1253059.9198
158 | 2751292.2171 | 1253080.7703
159 | 2751295.5691 | 1253087.2734
160 | 2751303.3237 | 1253092.5543
161 | 2751306.5074 | 1253201.7429
162 | 2751443.822 | 1252987.9641
163 | 2751446.7043 | 1252980.3637
164 | 2751444.5289 | 1252978.3394
165 | 2751547.1787 | 1252970.3762
166 | 2751546.412 | 1252970.8955
167 | 2751552.0958 | 1252967.0457
168 | 2751565.0193 | 1252964.771
169 | 2751543.1768 | 1252955.334
170 | 2751580.4658 | 1252960.4178
171 | 2751606.4507 | 1252947.495
172 | 2751338.6254 | 1253015.8366
173 | 2751578.2986 | 1252918.9282
174 | 2751643.0777 | 1252898.5067
175 | 2751708.6616 | 1252866.8436
176 | 2751654.2376 | 1252916.2848
177 | 2751392.3297 | 1252993.6314
178 | 2751385.7052 | 1253002.5627
179 | 2751380.3591 | 1252977.0533
180 | 2751383.3919 | 1253005.6815
181 | 2751710.4387 | 1252895.1735
182 | 2751588.6966 | 1252912.5732
183 | 2751600.7402 | 1252927.2624
184 | 2751709.2197 | 1252911.9353
185 | 2751720.4842 | 1252927.2462
186 | 2751736.4791 | 1252937.1247
187 | 2751736.3367 | 1252951.513
188 | 2751752.1371 | 1252961.2286
189 | 2751397.7464 | 1253062.2703

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1