## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3023-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3023-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3023-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3023-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3023-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3023-9_0_4_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_3023-9_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_3023-9_0_4_node_100 | 0.4 | n |  | TRUE
8 | bus_LV_3023-9_0_4_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_3023-9_0_4_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_3023-9_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_3023-9_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_3023-9_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_3023-9_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_3023-9_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_3023-9_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3023-9_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_3023-9_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_3023-9_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_3023-9_0_4_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_3023-9_0_4_node_55 | 0.4 | n |  | TRUE
21 | bus_LV_3023-9_0_4_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_3023-9_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_3023-9_0_4_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_3023-9_0_4_node_60 | 0.4 | n |  | TRUE
25 | bus_LV_3023-9_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_3023-9_0_4_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_3023-9_0_4_node_57 | 0.4 | n |  | TRUE
28 | bus_LV_3023-9_0_4_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_3023-9_0_4_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_3023-9_0_4_node_66 | 0.4 | n |  | TRUE
31 | bus_LV_3023-9_0_4_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_3023-9_0_4_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_3023-9_0_4_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_3023-9_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_3023-9_0_4_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_3023-9_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_3023-9_0_4_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_3023-9_0_4_node_15 | 0.4 | n |  | TRUE
39 | bus_LV_3023-9_0_4_node_17 | 0.4 | n |  | TRUE
40 | bus_LV_3023-9_0_4_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_3023-9_0_4_node_161 | 0.4 | n |  | TRUE
42 | bus_LV_3023-9_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_3023-9_0_4_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_3023-9_0_4_node_122 | 0.4 | n |  | TRUE
45 | bus_LV_3023-9_0_4_node_123 | 0.4 | n |  | TRUE
46 | bus_LV_3023-9_0_4_node_121 | 0.4 | n |  | TRUE
47 | bus_LV_3023-9_0_4_node_22 | 0.4 | n |  | TRUE
48 | bus_LV_3023-9_0_4_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_3023-9_0_4_node_149 | 0.4 | n |  | TRUE
50 | bus_LV_3023-9_0_4_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_3023-9_0_4_node_125 | 0.4 | n |  | TRUE
52 | bus_LV_3023-9_0_4_node_148 | 0.4 | n |  | TRUE
53 | bus_LV_3023-9_0_4_node_24 | 0.4 | n |  | TRUE
54 | bus_LV_3023-9_0_4_node_81 | 0.4 | n |  | TRUE
55 | bus_LV_3023-9_0_4_node_99 | 0.4 | n |  | TRUE
56 | bus_LV_3023-9_0_4_node_126 | 0.4 | n |  | TRUE
57 | bus_LV_3023-9_0_4_node_26 | 0.4 | n |  | TRUE
58 | bus_LV_3023-9_0_4_node_29 | 0.4 | n |  | TRUE
59 | bus_LV_3023-9_0_4_node_27 | 0.4 | n |  | TRUE
60 | bus_LV_3023-9_0_4_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_3023-9_0_4_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_3023-9_0_4_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_3023-9_0_4_node_124 | 0.4 | n |  | TRUE
64 | bus_LV_3023-9_0_4_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_3023-9_0_4_node_140 | 0.4 | n |  | TRUE
66 | bus_LV_3023-9_0_4_node_130 | 0.4 | n |  | TRUE
67 | bus_LV_3023-9_0_4_node_82 | 0.4 | n |  | TRUE
68 | bus_LV_3023-9_0_4_node_84 | 0.4 | n |  | TRUE
69 | bus_LV_3023-9_0_4_node_30 | 0.4 | n |  | TRUE
70 | bus_LV_3023-9_0_4_node_31 | 0.4 | n |  | TRUE
71 | bus_LV_3023-9_0_4_node_32 | 0.4 | n |  | TRUE
72 | bus_LV_3023-9_0_4_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_3023-9_0_4_node_34 | 0.4 | n |  | TRUE
74 | bus_LV_3023-9_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_3023-9_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_3023-9_0_4_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_3023-9_0_4_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_3023-9_0_4_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_3023-9_0_4_node_41 | 0.4 | n |  | TRUE
80 | bus_LV_3023-9_0_4_node_42 | 0.4 | n |  | TRUE
81 | bus_LV_3023-9_0_4_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_3023-9_0_4_node_46 | 0.4 | n |  | TRUE
83 | bus_LV_3023-9_0_4_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_3023-9_0_4_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_3023-9_0_4_node_49 | 0.4 | n |  | TRUE
86 | bus_LV_3023-9_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_3023-9_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_3023-9_0_4_node_109 | 0.4 | n |  | TRUE
89 | bus_LV_3023-9_0_4_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_3023-9_0_4_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_3023-9_0_4_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_3023-9_0_4_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_3023-9_0_4_node_108 | 0.4 | n |  | TRUE
94 | bus_LV_3023-9_0_4_node_104 | 0.4 | n |  | TRUE
95 | bus_LV_3023-9_0_4_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_3023-9_0_4_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_3023-9_0_4_node_101 | 0.4 | n |  | TRUE
98 | bus_LV_3023-9_0_4_node_102 | 0.4 | n |  | TRUE
99 | bus_LV_3023-9_0_4_node_110 | 0.4 | n |  | TRUE
100 | bus_LV_3023-9_0_4_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_3023-9_0_4_node_105 | 0.4 | n |  | TRUE
102 | bus_LV_3023-9_0_4_node_120 | 0.4 | n |  | TRUE
103 | bus_LV_3023-9_0_4_node_106 | 0.4 | n |  | TRUE
104 | bus_LV_3023-9_0_4_node_115 | 0.4 | n |  | TRUE
105 | bus_LV_3023-9_0_4_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_3023-9_0_4_node_96 | 0.4 | n |  | TRUE
107 | bus_LV_3023-9_0_4_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_3023-9_0_4_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_3023-9_0_4_node_93 | 0.4 | n |  | TRUE
110 | bus_LV_3023-9_0_4_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_3023-9_0_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_3023-9_0_4_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_3023-9_0_4_node_87 | 0.4 | n |  | TRUE
114 | bus_LV_3023-9_0_4_node_88 | 0.4 | n |  | TRUE
115 | bus_LV_3023-9_0_4_node_89 | 0.4 | n |  | TRUE
116 | bus_LV_3023-9_0_4_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_3023-9_0_4_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_3023-9_0_4_node_156 | 0.4 | n |  | TRUE
119 | bus_LV_3023-9_0_4_node_91 | 0.4 | n |  | TRUE
120 | bus_LV_3023-9_0_4_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_3023-9_0_4_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_3023-9_0_4_node_160 | 0.4 | n |  | TRUE
123 | bus_LV_3023-9_0_4_node_154 | 0.4 | n |  | TRUE
124 | bus_LV_3023-9_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_3023-9_0_4_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_3023-9_0_4_node_103 | 0.4 | n |  | TRUE
127 | bus_LV_3023-9_0_4_node_158 | 0.4 | n |  | TRUE
128 | bus_LV_3023-9_0_4_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_3023-9_0_4_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_3023-9_0_4_node_118 | 0.4 | n |  | TRUE
131 | bus_LV_3023-9_0_4_node_129 | 0.4 | n |  | TRUE
132 | bus_LV_3023-9_0_4_node_136 | 0.4 | n |  | TRUE
133 | bus_LV_3023-9_0_4_node_159 | 0.4 | n |  | TRUE
134 | bus_LV_3023-9_0_4_node_134 | 0.4 | n |  | TRUE
135 | bus_LV_3023-9_0_4_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_3023-9_0_4_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_3023-9_0_4_node_133 | 0.4 | n |  | TRUE
138 | bus_LV_3023-9_0_4_node_137 | 0.4 | n |  | TRUE
139 | bus_LV_3023-9_0_4_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_3023-9_0_4_node_139 | 0.4 | n |  | TRUE
141 | bus_LV_3023-9_0_4_node_146 | 0.4 | n |  | TRUE
142 | bus_LV_3023-9_0_4_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_3023-9_0_4_node_144 | 0.4 | n |  | TRUE
144 | bus_LV_3023-9_0_4_node_142 | 0.4 | n |  | TRUE
145 | bus_LV_3023-9_0_4_node_143 | 0.4 | n |  | TRUE
146 | bus_LV_3023-9_0_4_node_155 | 0.4 | n |  | TRUE
147 | bus_LV_3023-9_0_4_node_153 | 0.4 | n |  | TRUE
148 | bus_LV_3023-9_0_4_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_3023-9_0_4_node_151 | 0.4 | n |  | TRUE
150 | bus_LV_3023-9_0_4_node_152 | 0.4 | n |  | TRUE
151 | bus_MV_41_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3023-9_0_4_load_0 | 0 | 0.016215 | 0.0040639 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3023-9_0_4_load_1 | 1 | 0.0060954 | 0.0015277 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3023-9_0_4_load_2 | 2 | 0.0048617 | 0.0012185 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3023-9_0_4_load_100 | 7 | 0.015912 | 0.003988 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3023-9_0_4_load_51 | 8 | 0.001553 | 0.00038923 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3023-9_0_4_load_38 | 9 | 0.0039055 | 0.00097882 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3023-9_0_4_load_5 | 11 | 0.0048072 | 0.0012048 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3023-9_0_4_load_8 | 14 | 0.0026621 | 0.00066718 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3023-9_0_4_load_14 | 16 | 0.011576 | 0.0029013 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3023-9_0_4_load_52 | 19 | 0.0072222 | 0.0018101 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3023-9_0_4_load_61 | 21 | 0.0038894 | 0.00097478 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3023-9_0_4_load_63 | 23 | 0.028155 | 0.0070562 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3023-9_0_4_load_60 | 24 | 0.0040703 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3023-9_0_4_load_57 | 27 | 0.0024997 | 0.00062649 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3023-9_0_4_load_71 | 28 | 0.01181 | 0.0029599 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3023-9_0_4_load_67 | 31 | 0.0070621 | 0.0017699 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3023-9_0_4_load_64 | 32 | 0.0070831 | 0.0017752 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3023-9_0_4_load_35 | 33 | 0.018288 | 0.0045833 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3023-9_0_4_load_80 | 35 | 0.0040948 | 0.0010263 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3023-9_0_4_load_58 | 37 | 0.0092886 | 0.002328 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3023-9_0_4_load_15 | 38 | 0.003031 | 0.00075964 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3023-9_0_4_load_19 | 40 | 0.0071533 | 0.0017928 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3023-9_0_4_load_161 | 41 | 0.0017759 | 0.00044509 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3023-9_0_4_load_122 | 44 | 0.0045358 | 0.0011368 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3023-9_0_4_load_123 | 45 | 0.0041481 | 0.0010396 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3023-9_0_4_load_121 | 46 | 0.0037669 | 0.00094407 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3023-9_0_4_load_149 | 49 | 0.0024235 | 0.00060739 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3023-9_0_4_load_148 | 52 | 0.011524 | 0.0028883 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3023-9_0_4_load_99 | 55 | 0.002176 | 0.00054535 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3023-9_0_4_load_126 | 56 | 0.0092386 | 0.0023154 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3023-9_0_4_load_127 | 60 | 0.0020586 | 0.00051594 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3023-9_0_4_load_59 | 61 | 0.00088463 | 0.00022171 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3023-9_0_4_load_45 | 62 | 0.00093916 | 0.00023538 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3023-9_0_4_load_124 | 63 | 0.00093951 | 0.00023546 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3023-9_0_4_load_44 | 64 | 0.00094617 | 0.00023713 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3023-9_0_4_load_130 | 66 | 0.00817 | 0.0020476 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3023-9_0_4_load_82 | 67 | 0.0017746 | 0.00044476 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3023-9_0_4_load_30 | 69 | 0.023875 | 0.0059837 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3023-9_0_4_load_31 | 70 | 0.014322 | 0.0035895 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3023-9_0_4_load_32 | 71 | 0.0030768 | 0.00077112 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3023-9_0_4_load_34 | 73 | 0.0030765 | 0.00077104 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3023-9_0_4_load_72 | 75 | 0.0045127 | 0.001131 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3023-9_0_4_load_76 | 76 | 0.01572 | 0.0039397 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3023-9_0_4_load_68 | 77 | 0.0073514 | 0.0018424 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3023-9_0_4_load_73 | 78 | 0.0029462 | 0.0007384 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3023-9_0_4_load_41 | 79 | 0.0026944 | 0.00067528 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3023-9_0_4_load_42 | 80 | 0.00093951 | 0.00023546 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3023-9_0_4_load_43 | 81 | 0.0011744 | 0.00029432 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3023-9_0_4_load_46 | 82 | 0.0034101 | 0.00085465 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3023-9_0_4_load_49 | 85 | 0.0057947 | 0.0014523 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3023-9_0_4_load_77 | 86 | 0.0057241 | 0.0014346 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3023-9_0_4_load_69 | 90 | 0.0052732 | 0.0013216 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3023-9_0_4_load_108 | 93 | 0.002437 | 0.00061076 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3023-9_0_4_load_104 | 94 | 0.0030134 | 0.00075524 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3023-9_0_4_load_101 | 97 | 0.0013624 | 0.00034144 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3023-9_0_4_load_110 | 99 | 0.0040012 | 0.0010028 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3023-9_0_4_load_105 | 101 | 0.0047157 | 0.0011819 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3023-9_0_4_load_120 | 102 | 0.0010501 | 0.00026317 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3023-9_0_4_load_106 | 103 | 0.0012796 | 0.00032071 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3023-9_0_4_load_115 | 104 | 0.009795 | 0.0024549 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3023-9_0_4_load_96 | 106 | 0.0011098 | 0.00027813 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3023-9_0_4_load_95 | 108 | 0.0018336 | 0.00045955 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3023-9_0_4_load_93 | 109 | 0.0026162 | 0.00065567 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3023-9_0_4_load_97 | 110 | 0.0037781 | 0.00094687 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3023-9_0_4_load_98 | 111 | 0.0019814 | 0.00049658 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3023-9_0_4_load_86 | 112 | 0.0015706 | 0.00039363 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3023-9_0_4_load_87 | 113 | 0.0031535 | 0.00079034 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3023-9_0_4_load_156 | 118 | 0.0014621 | 0.00036643 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3023-9_0_4_load_113 | 120 | 0.0021115 | 0.00052918 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3023-9_0_4_load_111 | 121 | 0.0047555 | 0.0011918 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3023-9_0_4_load_160 | 122 | 0.0023975 | 0.00060088 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3023-9_0_4_load_154 | 123 | 0.0013666 | 0.00034249 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3023-9_0_4_load_114 | 124 | 0.00093813 | 0.00023512 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3023-9_0_4_load_112 | 125 | 0.0017011 | 0.00042632 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3023-9_0_4_load_158 | 127 | 0.0016387 | 0.00041071 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3023-9_0_4_load_119 | 128 | 0.0014735 | 0.00036928 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3023-9_0_4_load_117 | 129 | 0.0027646 | 0.00069286 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3023-9_0_4_load_129 | 131 | 0.0021909 | 0.00054909 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3023-9_0_4_load_159 | 133 | 0.0020749 | 0.00052001 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3023-9_0_4_load_131 | 136 | 0.0075763 | 0.0018988 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3023-9_0_4_load_133 | 137 | 0.0041651 | 0.0010439 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3023-9_0_4_load_137 | 138 | 0.0028174 | 0.00070611 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3023-9_0_4_load_138 | 139 | 0.005016 | 0.0012571 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3023-9_0_4_load_139 | 140 | 0.0029736 | 0.00074526 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3023-9_0_4_load_141 | 142 | 0.0068729 | 0.0017225 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3023-9_0_4_load_142 | 144 | 0.0030988 | 0.00077664 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3023-9_0_4_load_143 | 145 | 0.0043075 | 0.0010796 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3023-9_0_4_load_155 | 146 | 0.0045009 | 0.001128 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3023-9_0_4_load_150 | 148 | 0.0072748 | 0.0018232 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3023-9_0_4_load_151 | 149 | 0.0025985 | 0.00065124 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3023-9_0_4_line_0 |  | 0 | 1 | 0.0009481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3023-9_0_4_line_1 |  | 0 | 2 | 0.014101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3023-9_0_4_line_2 |  | 1 | 3 | 0.020927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3023-9_0_4_line_3 |  | 2 | 4 | 0.0032163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3023-9_0_4_line_4 |  | 3 | 5 | 0.006919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3023-9_0_4_line_5 |  | 4 | 6 | 0.043379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3023-9_0_4_line_6 |  | 4 | 7 | 0.019362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3023-9_0_4_line_7 |  | 5 | 8 | 0.032997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3023-9_0_4_line_8 |  | 5 | 9 | 0.019188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3023-9_0_4_line_9 |  | 6 | 10 | 0.00498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3023-9_0_4_line_10 |  | 8 | 37 | 0.021781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3023-9_0_4_line_11 |  | 9 | 36 | 0.021083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3023-9_0_4_line_12 |  | 10 | 41 | 0.007809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3023-9_0_4_line_13 |  | 11 | 12 | 0.018246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_3023-9_0_4_line_14 |  | 11 | 13 | 0.02425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_3023-9_0_4_line_15 |  | 12 | 14 | 0.015742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3023-9_0_4_line_16 |  | 12 | 15 | 0.012877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_3023-9_0_4_line_17 |  | 13 | 16 | 0.015688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_3023-9_0_4_line_18 |  | 14 | 17 | 0.017293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3023-9_0_4_line_19 |  | 15 | 18 | 0.018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_3023-9_0_4_line_20 |  | 15 | 19 | 0.012297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3023-9_0_4_line_21 |  | 16 | 26 | 0.0029762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_3023-9_0_4_line_22 |  | 17 | 27 | 0.023071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3023-9_0_4_line_23 |  | 18 | 20 | 0.013071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_3023-9_0_4_line_24 |  | 18 | 21 | 0.016401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3023-9_0_4_line_25 |  | 20 | 28 | 0.022935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_3023-9_0_4_line_26 |  | 22 | 23 | 0.01648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3023-9_0_4_line_27 |  | 22 | 24 | 0.015937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3023-9_0_4_line_28 |  | 23 | 25 | 0.0083322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3023-9_0_4_line_29 |  | 25 | 26 | 0.005002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3023-9_0_4_line_30 |  | 26 | 33 | 0.034971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_3023-9_0_4_line_31 |  | 28 | 74 | 0.021952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_3023-9_0_4_line_32 |  | 29 | 30 | 0.014448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3023-9_0_4_line_33 |  | 29 | 31 | 0.060633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_3023-9_0_4_line_34 |  | 29 | 32 | 0.019559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_3023-9_0_4_line_35 |  | 30 | 86 | 0.015687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3023-9_0_4_line_36 |  | 32 | 89 | 0.00847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_3023-9_0_4_line_37 |  | 33 | 36 | 0.027608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_3023-9_0_4_line_38 |  | 34 | 35 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_3023-9_0_4_line_39 |  | 34 | 36 | 0.004608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3023-9_0_4_line_40 |  | 35 | 59 | 0.028254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_3023-9_0_4_line_41 |  | 38 | 39 | 0.010989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3023-9_0_4_line_42 |  | 39 | 40 | 0.019894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3023-9_0_4_line_43 |  | 40 | 42 | 0.011571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3023-9_0_4_line_44 |  | 42 | 57 | 0.010492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_3023-9_0_4_line_45 |  | 42 | 59 | 0.01407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_3023-9_0_4_line_46 |  | 43 | 44 | 0.0088104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3023-9_0_4_line_47 |  | 43 | 45 | 0.010639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3023-9_0_4_line_48 |  | 43 | 46 | 0.026902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3023-9_0_4_line_49 |  | 44 | 63 | 0.036735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3023-9_0_4_line_50 |  | 45 | 57 | 0.0040161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3023-9_0_4_line_51 |  | 46 | 64 | 0.022369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3023-9_0_4_line_52 |  | 47 | 48 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_3023-9_0_4_line_53 |  | 47 | 49 | 0.010223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_3023-9_0_4_line_54 |  | 48 | 50 | 0.031514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_3023-9_0_4_line_55 |  | 48 | 51 | 0.013202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_3023-9_0_4_line_56 |  | 48 | 52 | 0.048648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3023-9_0_4_line_57 |  | 49 | 65 | 0.032273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_3023-9_0_4_line_58 |  | 50 | 56 | 0.011959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_3023-9_0_4_line_59 |  | 51 | 66 | 0.048828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_3023-9_0_4_line_60 |  | 53 | 54 | 0.004549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3023-9_0_4_line_61 |  | 53 | 55 | 0.012093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3023-9_0_4_line_62 |  | 54 | 67 | 0.0028343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3023-9_0_4_line_63 |  | 54 | 59 | 0.025475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3023-9_0_4_line_64 |  | 55 | 68 | 0.013564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3023-9_0_4_line_65 |  | 56 | 60 | 0.0011408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_3023-9_0_4_line_66 |  | 57 | 58 | 0.024574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_3023-9_0_4_line_67 |  | 58 | 60 | 0.017442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_3023-9_0_4_line_68 |  | 61 | 62 | 0.013445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3023-9_0_4_line_69 |  | 62 | 81 | 0.0022846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3023-9_0_4_line_70 |  | 64 | 80 | 0.015159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3023-9_0_4_line_71 |  | 65 | 141 | 0.018265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_3023-9_0_4_line_72 |  | 65 | 139 | 0.018019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3023-9_0_4_line_73 |  | 66 | 131 | 0.0022141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_3023-9_0_4_line_74 |  | 68 | 106 | 0.00093167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3023-9_0_4_line_75 |  | 69 | 70 | 0.040968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3023-9_0_4_line_76 |  | 69 | 71 | 0.0067925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3023-9_0_4_line_77 |  | 70 | 72 | 0.010068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3023-9_0_4_line_78 |  | 71 | 73 | 0.014284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3023-9_0_4_line_79 |  | 72 | 74 | 0.019698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3023-9_0_4_line_80 |  | 72 | 75 | 0.0066742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3023-9_0_4_line_81 |  | 73 | 76 | 0.029021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3023-9_0_4_line_82 |  | 74 | 77 | 0.020272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3023-9_0_4_line_83 |  | 75 | 78 | 0.026228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3023-9_0_4_line_84 |  | 77 | 89 | 0.02227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_3023-9_0_4_line_85 |  | 78 | 95 | 0.19721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3023-9_0_4_line_86 |  | 79 | 80 | 0.0094478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3023-9_0_4_line_87 |  | 79 | 81 | 0.0046581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3023-9_0_4_line_88 |  | 82 | 83 | 0.012704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3023-9_0_4_line_89 |  | 83 | 84 | 0.013733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3023-9_0_4_line_90 |  | 83 | 85 | 0.011379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3023-9_0_4_line_91 |  | 84 | 86 | 0.027113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3023-9_0_4_line_92 |  | 85 | 87 | 0.024006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3023-9_0_4_line_93 |  | 87 | 88 | 0.017477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3023-9_0_4_line_94 |  | 88 | 102 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3023-9_0_4_line_95 |  | 88 | 103 | 0.0087425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3023-9_0_4_line_96 |  | 89 | 90 | 0.006644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3023-9_0_4_line_97 |  | 91 | 92 | 0.019842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3023-9_0_4_line_98 |  | 91 | 93 | 0.029195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3023-9_0_4_line_99 |  | 91 | 94 | 0.0088815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3023-9_0_4_line_100 |  | 92 | 99 | 0.047538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3023-9_0_4_line_101 |  | 92 | 100 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3023-9_0_4_line_102 |  | 94 | 101 | 0.031676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3023-9_0_4_line_103 |  | 95 | 96 | 0.01196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3023-9_0_4_line_104 |  | 96 | 97 | 0.10275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3023-9_0_4_line_105 |  | 97 | 98 | 0.054007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3023-9_0_4_line_106 |  | 98 | 126 | 0.021062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3023-9_0_4_line_107 |  | 100 | 121 | 0.018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3023-9_0_4_line_108 |  | 100 | 119 | 0.026727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3023-9_0_4_line_109 |  | 101 | 103 | 0.035933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3023-9_0_4_line_110 |  | 102 | 128 | 0.01896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_3023-9_0_4_line_111 |  | 104 | 105 | 0.024503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3023-9_0_4_line_112 |  | 105 | 129 | 0.038582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3023-9_0_4_line_113 |  | 105 | 130 | 0.004641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3023-9_0_4_line_114 |  | 106 | 110 | 0.013987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3023-9_0_4_line_115 |  | 107 | 108 | 0.024772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3023-9_0_4_line_116 |  | 107 | 109 | 0.015835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3023-9_0_4_line_117 |  | 108 | 111 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3023-9_0_4_line_118 |  | 110 | 111 | 0.024673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3023-9_0_4_line_119 |  | 112 | 113 | 0.015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_3023-9_0_4_line_120 |  | 112 | 114 | 0.030809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_3023-9_0_4_line_121 |  | 113 | 115 | 0.010235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_3023-9_0_4_line_122 |  | 114 | 116 | 0.030637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3023-9_0_4_line_123 |  | 115 | 117 | 0.023105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_3023-9_0_4_line_124 |  | 116 | 118 | 0.0052264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_3023-9_0_4_line_125 |  | 117 | 122 | 0.01046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3023-9_0_4_line_126 |  | 117 | 119 | 0.01218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3023-9_0_4_line_127 |  | 118 | 123 | 0.037612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3023-9_0_4_line_128 |  | 119 | 120 | 0.0022537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3023-9_0_4_line_129 |  | 120 | 124 | 0.014615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_3023-9_0_4_line_130 |  | 121 | 125 | 0.015485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_3023-9_0_4_line_131 |  | 123 | 150 | 0.042213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_3023-9_0_4_line_132 |  | 126 | 127 | 0.052631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_3023-9_0_4_line_133 |  | 128 | 130 | 0.0034026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_3023-9_0_4_line_134 |  | 131 | 136 | 0.041271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_3023-9_0_4_line_135 |  | 132 | 133 | 0.024969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_3023-9_0_4_line_136 |  | 132 | 134 | 0.090349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_3023-9_0_4_line_137 |  | 134 | 137 | 0.042775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
138 | LV_3023-9_0_4_line_138 |  | 134 | 135 | 0.04769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_3023-9_0_4_line_139 |  | 135 | 136 | 0.017474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_3023-9_0_4_line_140 |  | 138 | 139 | 0.011553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_3023-9_0_4_line_141 |  | 138 | 140 | 0.013628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_3023-9_0_4_line_142 |  | 141 | 143 | 0.005752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_3023-9_0_4_line_143 |  | 141 | 142 | 0.019904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_3023-9_0_4_line_144 |  | 143 | 144 | 0.02297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_3023-9_0_4_line_145 |  | 144 | 145 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_3023-9_0_4_line_146 |  | 146 | 147 | 0.018133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_3023-9_0_4_line_147 |  | 147 | 149 | 0.013715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_3023-9_0_4_line_148 |  | 148 | 149 | 0.0093852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_3023-9_0_4_line_149 |  | 148 | 150 | 0.017609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3023-9_0_4_trafo_67 | 0.63 MVA 20/0.4 kV | 151 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2751458.6583 | 1252887.726 | 2751458.1127 | 1252886.9506
1 | 2751458.6583 | 1252887.726 | 2751461.3659 | 1252891.5739 | 2751464.622 | 1252896.2172 | 2751465.6924 | 1252897.7572 | 2751466.7176 | 1252899.296
2 | 2751444.8836 | 1252871.8221 | 2751447.7062 | 1252872.1613 | 2751458.1127 | 1252886.9506
3 | 2751469.4489 | 1252897.5975 | 2751466.7176 | 1252899.296
4 | 2751439.6265 | 1252876.3366 | 2751444.8836 | 1252871.8221
5 | 2751469.4489 | 1252897.5975 | 2751470.6432 | 1252899.6078 | 2751474.5818 | 1252905.3141 | 2751475.9522 | 1252907.2288 | 2751477.8517 | 1252905.876 | 2751476.7566 | 1252904.4133 | 2751475.3804 | 1252902.4317 | 2751476.3829 | 1252901.6121 | 2751479.3287 | 1252899.4964 | 2751483.0064 | 1252896.8101 | 2751489.6773 | 1252892.2206 | 2751495.9921 | 1252887.9779
6 | 2751469.4489 | 1252897.5975 | 2751471.0473 | 1252896.504 | 2751470.1454 | 1252894.8682 | 2751469.2384 | 1252893.4325 | 2751467.785 | 1252885.3208 | 2751465.5136 | 1252880.1818
7 | 2751439.6265 | 1252876.3366 | 2751429.3063 | 1252883.0905 | 2751436.7032 | 1252893.8012 | 2751437.7542 | 1252901.4133
8 | 2751439.6265 | 1252876.3366 | 2751430.9854 | 1252864.3818 | 2751428.4973 | 1252860.7079
9 | 2751498.2109 | 1252892.439 | 2751495.9921 | 1252887.9779
10 | 2751437.7542 | 1252901.4133 | 2751419.8085 | 1252913.7572
11 | 2751416.6749 | 1252843.251 | 2751428.4973 | 1252860.7079
12 | 2751491.5812 | 1252896.5958 | 2751498.2109 | 1252892.439
13 | 2751358.3894 | 1252941.5021 | 2751359.8313 | 1252928.8155 | 2751359.8507 | 1252923.3378
14 | 2751360.7338 | 1252899.1317 | 2751359.9092 | 1252906.8738 | 2751359.8507 | 1252923.3378
15 | 2751358.3894 | 1252941.5021 | 2751360.6104 | 1252941.1585 | 2751372.6312 | 1252935.0261
16 | 2751358.3894 | 1252941.5021 | 2751356.8605 | 1252948.7368 | 2751354.8426 | 1252953.8347
17 | 2751360.7338 | 1252899.1317 | 2751363.5969 | 1252890.5076 | 2751366.676 | 1252884.6682
18 | 2751388.0351 | 1252927.1678 | 2751372.6312 | 1252935.0261
19 | 2751343.3629 | 1252944.5323 | 2751346.876 | 1252945.6231 | 2751348.6363 | 1252946.1686 | 2751352.1476 | 1252947.3261 | 2751350.4921 | 1252952.133 | 2751354.8426 | 1252953.8347
20 | 2751354.8426 | 1252953.8347 | 2751363.6695 | 1252957.3414 | 2751366.0247 | 1252958.8541
21 | 2751368.0642 | 1252882.0356 | 2751366.676 | 1252884.6682
22 | 2751388.0351 | 1252927.1678 | 2751398.9469 | 1252947.4949
23 | 2751343.3629 | 1252944.5323 | 2751340.2358 | 1252943.9964 | 2751336.4119 | 1252945.0219 | 2751330.6347 | 1252946.5536
24 | 2751343.3629 | 1252944.5323 | 2751344.9644 | 1252940.0689 | 2751345.7965 | 1252937.0539 | 2751346.2387 | 1252932.1604 | 2751346.2529 | 1252928.5425
25 | 2751330.6347 | 1252946.5536 | 2751330.5738 | 1252944.5056 | 2751330.2533 | 1252942.5733 | 2751325.4406 | 1252926.1677 | 2751324.604 | 1252924.5393
26 | 2751347.7467 | 1252887.6554 | 2751349.4481 | 1252882.238 | 2751353.6153 | 1252879.5974 | 2751356.8957 | 1252874.732
27 | 2751347.7467 | 1252887.6554 | 2751345.9044 | 1252893.2694 | 2751347.237 | 1252896.6623 | 2751346.7613 | 1252903.0282
28 | 2751363.8686 | 1252879.2924 | 2751360.4759 | 1252877.0369 | 2751359.6073 | 1252876.4586 | 2751356.8957 | 1252874.732
29 | 2751363.8686 | 1252879.2924 | 2751368.0642 | 1252882.0356
30 | 2751368.0642 | 1252882.0356 | 2751373.8583 | 1252874.5319 | 2751381.5416 | 1252867.5547 | 2751393.9699 | 1252858.9574
31 | 2751309.2903 | 1252911.4297 | 2751310.4734 | 1252910.9261 | 2751312.0306 | 1252910.8547 | 2751313.3839 | 1252911.0783 | 2751314.6202 | 1252911.7439 | 2751315.7208 | 1252912.6952 | 2751321.3128 | 1252918.9997 | 2751323.5994 | 1252922.5838 | 2751324.604 | 1252924.5393
32 | 2751325.3278 | 1252854.6839 | 2751320.0953 | 1252845.5413 | 2751318.0058 | 1252842.218
33 | 2751325.3278 | 1252854.6839 | 2751359.9992 | 1252831.9028 | 2751371.6355 | 1252847.1081
34 | 2751325.3278 | 1252854.6839 | 2751309.0295 | 1252865.4975
35 | 2751318.0058 | 1252842.218 | 2751310.9903 | 1252844.3409 | 2751302.6494 | 1252843.8221
36 | 2751301.9717 | 1252870.1803 | 2751309.0295 | 1252865.4975
37 | 2751416.6749 | 1252843.251 | 2751393.9699 | 1252858.9574
38 | 2751413.3905 | 1252840.0083 | 2751423.2161 | 1252831.9293 | 2751428.0339 | 1252827.4171
39 | 2751413.3905 | 1252840.0083 | 2751416.6749 | 1252843.251
40 | 2751447.2066 | 1252806.7068 | 2751434.3939 | 1252821.4603 | 2751428.0339 | 1252827.4171
41 | 2751475.1756 | 1252836.3841 | 2751480.1614 | 1252846.1774
42 | 2751475.1756 | 1252836.3841 | 2751466.1899 | 1252818.6356
43 | 2751459.1356 | 1252809.6701 | 2751464 | 1252814.3101 | 2751466.1899 | 1252818.6356
44 | 2751459.1356 | 1252809.6701 | 2751464.0211 | 1252805.8135 | 2751467.3657 | 1252803.1631
45 | 2751447.2066 | 1252806.7068 | 2751451.844 | 1252810.7737 | 2751454.3867 | 1252809.0704 | 2751457.4437 | 1252809.1041 | 2751459.1356 | 1252809.6701
46 | 2751475.351 | 1252815.368 | 2751483.0238 | 1252811.0377
47 | 2751475.351 | 1252815.368 | 2751473.5855 | 1252811.4858 | 2751469.7698 | 1252806.38
48 | 2751475.351 | 1252815.368 | 2751486.4843 | 1252839.8581
49 | 2751483.0238 | 1252811.0377 | 2751493.3923 | 1252805.186 | 2751500.4105 | 1252817.1216 | 2751509.0552 | 1252810.3472
50 | 2751467.3657 | 1252803.1631 | 2751469.7698 | 1252806.38
51 | 2751486.4843 | 1252839.8581 | 2751495.7416 | 1252860.2217
52 | 2751501.4893 | 1252742.821 | 2751505.385 | 1252740.4739 | 2751506.6978 | 1252743.7551 | 2751510.7806 | 1252747.6633 | 2751512.4978 | 1252746.6507
53 | 2751501.4893 | 1252742.821 | 2751501.1954 | 1252738.3758 | 2751502.7691 | 1252733.2333 | 2751502.9947 | 1252732.9144
54 | 2751491.9015 | 1252766.6769 | 2751490.567 | 1252762.472 | 2751505.7624 | 1252750.5045 | 2751510.7806 | 1252747.6633 | 2751512.4978 | 1252746.6507
55 | 2751518.4326 | 1252758.4362 | 2751514.6853 | 1252750.566 | 2751512.4978 | 1252746.6507
56 | 2751512.4978 | 1252746.6507 | 2751546.9506 | 1252726.2675 | 2751554.4106 | 1252721.9553
57 | 2751521.6329 | 1252706.5674 | 2751502.9947 | 1252732.9144
58 | 2751491.9015 | 1252766.6769 | 2751493.7603 | 1252772.5191 | 2751489.6317 | 1252776.6327
59 | 2751518.4326 | 1252758.4362 | 2751524.9181 | 1252759.6255 | 2751530.2325 | 1252758.4825 | 2751549.7938 | 1252745.8594 | 2751563.2585 | 1252747.0522
60 | 2751448.337 | 1252784.6585 | 2751445.1506 | 1252787.9136
61 | 2751448.337 | 1252784.6585 | 2751439.8091 | 1252776.0843
62 | 2751445.1506 | 1252787.9136 | 2751443.043 | 1252786.0185
63 | 2751447.2066 | 1252806.7068 | 2751444.5631 | 1252804.3814 | 2751443.5292 | 1252803.4763 | 2751441.4322 | 1252801.632 | 2751448.9764 | 1252792.7161 | 2751445.1506 | 1252787.9136
64 | 2751430.2439 | 1252766.4672 | 2751439.8091 | 1252776.0843
65 | 2751489.6317 | 1252776.6327 | 2751488.8236 | 1252777.4379
66 | 2751467.3657 | 1252803.1631 | 2751464.9969 | 1252798.954 | 2751465.5192 | 1252794.7743 | 2751470.3452 | 1252787.6352 | 2751475.043 | 1252782.5614
67 | 2751475.043 | 1252782.5614 | 2751481.1469 | 1252785.0866 | 2751488.8236 | 1252777.4379
68 | 2751514.1545 | 1252901.2756 | 2751508.6748 | 1252888.9984
69 | 2751508.6748 | 1252888.9984 | 2751507.7436 | 1252886.9121
70 | 2751495.7416 | 1252860.2217 | 2751500.2537 | 1252870.1472 | 2751500.6326 | 1252870.98 | 2751501.9944 | 1252874.031
71 | 2751521.6329 | 1252706.5674 | 2751532.1928 | 1252691.6451
72 | 2751521.6329 | 1252706.5674 | 2751513.6604 | 1252701.5252 | 2751506.8009 | 1252696.3613
73 | 2751565.4639 | 1252747.2476 | 2751563.2585 | 1252747.0522
74 | 2751429.5874 | 1252765.8062 | 2751430.2439 | 1252766.4672
75 | 2751265.2524 | 1252966.2176 | 2751270.2708 | 1252959.0242 | 2751286.4191 | 1252944.3 | 2751291.9164 | 1252937.7673 | 2751292.8731 | 1252936.2354
76 | 2751261.366 | 1252971.7884 | 2751265.2524 | 1252966.2176
77 | 2751298.2063 | 1252927.6959 | 2751292.8731 | 1252936.2354
78 | 2751261.366 | 1252971.7884 | 2751259.3772 | 1252974.6391 | 2751254.9756 | 1252984.5108
79 | 2751298.2063 | 1252927.6959 | 2751308.2447 | 1252912.4596 | 2751309.2903 | 1252911.4297
80 | 2751298.2063 | 1252927.6959 | 2751291.6201 | 1252926.6155
81 | 2751242.8437 | 1253010.8724 | 2751250.3111 | 1252994.972 | 2751254.9756 | 1252984.5108
82 | 2751309.2903 | 1252911.4297 | 2751309.4461 | 1252891.1583
83 | 2751291.6201 | 1252926.6155 | 2751284.4396 | 1252930.4692 | 2751278.5232 | 1252932.1309 | 2751268.89 | 1252939.1747
84 | 2751301.9717 | 1252870.1803 | 2751309.4461 | 1252891.1583
85 | 2751101.7808 | 1253041.7054 | 2751117.7403 | 1253037.3081 | 2751169.2008 | 1253010.0944 | 2751188.3447 | 1252997.4928 | 2751220.3458 | 1252973.6752 | 2751223.836 | 1252972.1183 | 2751268.89 | 1252939.1747
86 | 2751505.8451 | 1252882.6585 | 2751501.9944 | 1252874.031
87 | 2751505.8451 | 1252882.6585 | 2751507.7436 | 1252886.9121
88 | 2751263.2504 | 1252844.3552 | 2751263.8005 | 1252850.5976 | 2751265.6894 | 1252856.7518
89 | 2751276.0173 | 1252839.6432 | 2751270.4626 | 1252842.8045 | 2751263.2504 | 1252844.3552
90 | 2751263.2504 | 1252844.3552 | 2751254.4144 | 1252837.1858
91 | 2751276.0173 | 1252839.6432 | 2751287.3129 | 1252842.8681 | 2751302.6494 | 1252843.8221
92 | 2751245.0873 | 1252816.1862 | 2751245.8081 | 1252825.5026 | 2751251.6448 | 1252834.9386 | 2751254.4144 | 1252837.1858
93 | 2751245.0873 | 1252816.1862 | 2751232.9285 | 1252803.5969
94 | 2751232.9285 | 1252803.5969 | 2751218.6576 | 1252790.0416 | 2751218.6576 | 1252790.0416
95 | 2751232.9285 | 1252803.5969 | 2751239.2781 | 1252797.5875
96 | 2751296.4119 | 1252873.8419 | 2751301.9717 | 1252870.1803
97 | 2751294.2873 | 1252724.4973 | 2751293.3655 | 1252744.3153
98 | 2751293.3655 | 1252744.3153 | 2751310.1341 | 1252720.4169
99 | 2751293.3655 | 1252744.3153 | 2751286.7927 | 1252750.2885
100 | 2751294.2873 | 1252724.4973 | 2751261.7898 | 1252711.8329 | 2751250.5896 | 1252705.9314
101 | 2751295.2555 | 1252703.457 | 2751294.2873 | 1252724.4973
102 | 2751286.7927 | 1252750.2885 | 2751263.3506 | 1252771.5924
103 | 2751101.7808 | 1253041.7054 | 2751098.8911 | 1253030.0981
104 | 2751098.8911 | 1253030.0981 | 2751090.681 | 1253006.866 | 2751080.8468 | 1252967.0986 | 2751072.9899 | 1252941.2619 | 2751068.603 | 1252932.1203
105 | 2751040.0092 | 1252886.9124 | 2751054.9534 | 1252903.6765 | 2751068.603 | 1252932.1203
106 | 2751049.992 | 1252868.8048 | 2751043.6367 | 1252876.1277 | 2751040.0092 | 1252886.9124
107 | 2751295.2555 | 1252703.457 | 2751288.5666 | 1252701.9514 | 2751280.6213 | 1252693.5854
108 | 2751295.2555 | 1252703.457 | 2751295.7362 | 1252693.2149 | 2751312.0553 | 1252695.4671
109 | 2751263.3506 | 1252771.5924 | 2751259.7023 | 1252774.9079 | 2751257.8736 | 1252779.9884 | 2751239.2781 | 1252797.5875
110 | 2751202.2561 | 1252780.5883 | 2751209.2007 | 1252783.9943 | 2751218.6576 | 1252790.0416
111 | 2751196.485 | 1252782.8576 | 2751205.5748 | 1252785.8369 | 2751216.7527 | 1252795.7461
112 | 2751196.485 | 1252782.8576 | 2751192.7054 | 1252788.9449 | 2751184.0508 | 1252794.0512 | 2751180.4158 | 1252799.7974 | 2751182.0303 | 1252808.1245 | 2751186.452 | 1252812.3071
113 | 2751199.2012 | 1252779.0899 | 2751196.485 | 1252782.8576
114 | 2751429.5874 | 1252765.8062 | 2751419.7303 | 1252755.8821
115 | 2751374.1036 | 1252710.2443 | 2751381.6853 | 1252717.5785 | 2751391.7083 | 1252727.6697
116 | 2751374.1036 | 1252710.2443 | 2751363.2858 | 1252698.68
117 | 2751402.343 | 1252738.3766 | 2751391.7083 | 1252727.6697
118 | 2751402.343 | 1252738.3766 | 2751419.7303 | 1252755.8821
119 | 2751319.2144 | 1252651.5669 | 2751329.9968 | 1252663.0936
120 | 2751296.6648 | 1252630.5997 | 2751315.1388 | 1252647.2099 | 2751319.2144 | 1252651.5669
121 | 2751336.9889 | 1252670.5685 | 2751329.9968 | 1252663.0936
122 | 2751302.9876 | 1252600.643 | 2751301.2129 | 1252606.8593 | 2751299.054 | 1252618.3598 | 2751296.6648 | 1252630.5997
123 | 2751336.9889 | 1252670.5685 | 2751334.7663 | 1252673.9262 | 2751321.0765 | 1252687.2562
124 | 2751302.9876 | 1252600.643 | 2751306.5643 | 1252596.8321
125 | 2751321.0765 | 1252687.2562 | 2751328.3511 | 1252694.7938
126 | 2751321.0765 | 1252687.2562 | 2751312.0553 | 1252695.4671
127 | 2751306.5643 | 1252596.8321 | 2751311.3161 | 1252591.7692 | 2751318.1371 | 1252586.9276 | 2751333.2365 | 1252582.2642 | 2751339.7092 | 1252581.6591
128 | 2751312.0553 | 1252695.4671 | 2751314.2033 | 1252696.1493
129 | 2751326.7132 | 1252703.3381 | 2751319.2153 | 1252697.7411 | 2751314.2033 | 1252696.1493
130 | 2751269.9575 | 1252682.3571 | 2751280.6213 | 1252693.5854
131 | 2751380.8486 | 1252573.1605 | 2751365.5352 | 1252578.2187 | 2751355.5638 | 1252580.177 | 2751339.7092 | 1252581.6591
132 | 2751049.992 | 1252868.8048 | 2751055.5665 | 1252868.113 | 2751062.5421 | 1252869.3253 | 2751069.3305 | 1252874.0252 | 2751094.6457 | 1252893.2562
133 | 2751199.2012 | 1252779.0899 | 2751202.2561 | 1252780.5883
134 | 2751565.4639 | 1252747.2476 | 2751572.2201 | 1252747.8461 | 2751577.6273 | 1252747.5063 | 2751594.9763 | 1252753.1669 | 2751598.6966 | 1252752.3613 | 2751599.8873 | 1252755.9842 | 2751602.9558 | 1252755.0726
135 | 2751640.8669 | 1252802.6785 | 2751663.9754 | 1252793.0606
136 | 2751627.0518 | 1252712.1253 | 2751635.2156 | 1252720.0086 | 2751637.3412 | 1252723.978 | 2751649.1223 | 1252745.9788 | 2751652.6962 | 1252752.6546 | 2751655.1367 | 1252759.6573 | 2751663.9754 | 1252793.0606
137 | 2751627.0518 | 1252712.1253 | 2751622.9911 | 1252714.1344 | 2751609.4473 | 1252714.6662 | 2751591.4364 | 1252714.2049 | 2751585.1489 | 1252715.3117 | 2751584.9131 | 1252715.1447
138 | 2751627.0518 | 1252712.1253 | 2751635.2156 | 1252720.0086 | 2751637.3412 | 1252723.978 | 2751627.3355 | 1252742.6068 | 2751623.6608 | 1252746.3498 | 2751619.7066 | 1252750.0967
139 | 2751619.7066 | 1252750.0967 | 2751602.9558 | 1252755.0726
140 | 2751497.5711 | 1252689.4131 | 2751506.8009 | 1252696.3613
141 | 2751497.5711 | 1252689.4131 | 2751497.5711 | 1252689.4131 | 2751498.2471 | 1252678.9312 | 2751500.0773 | 1252676.3984
142 | 2751535.5367 | 1252686.9593 | 2751532.1928 | 1252691.6451
143 | 2751532.1928 | 1252691.6451 | 2751528.249 | 1252685.5494 | 2751517.4622 | 1252678.9523
144 | 2751535.5367 | 1252686.9593 | 2751541.6153 | 1252678.3842 | 2751549.7393 | 1252668.9384
145 | 2751549.7393 | 1252668.9384 | 2751565.5179 | 1252650.5926
146 | 2751418.0494 | 1252561.0771 | 2751435.6558 | 1252565.4149
147 | 2751418.0494 | 1252561.0771 | 2751413.5337 | 1252567.0008 | 2751407.376 | 1252568.1613
148 | 2751398.1532 | 1252569.8994 | 2751407.376 | 1252568.1613
149 | 2751380.8486 | 1252573.1605 | 2751398.1532 | 1252569.8994

## bus_geodata
| x | y | coords
0 | 2751458.6583 | 1252887.726
1 | 2751458.1127 | 1252886.9506
2 | 2751466.7176 | 1252899.296
3 | 2751444.8836 | 1252871.8221
4 | 2751469.4489 | 1252897.5975
5 | 2751439.6265 | 1252876.3366
6 | 2751495.9921 | 1252887.9779
7 | 2751465.5136 | 1252880.1818
8 | 2751437.7542 | 1252901.4133
9 | 2751428.4973 | 1252860.7079
10 | 2751498.2109 | 1252892.439
11 | 2751359.8507 | 1252923.3378
12 | 2751358.3894 | 1252941.5021
13 | 2751360.7338 | 1252899.1317
14 | 2751372.6312 | 1252935.0261
15 | 2751354.8426 | 1252953.8347
16 | 2751366.676 | 1252884.6682
17 | 2751388.0351 | 1252927.1678
18 | 2751343.3629 | 1252944.5323
19 | 2751366.0247 | 1252958.8541
20 | 2751330.6347 | 1252946.5536
21 | 2751346.2529 | 1252928.5425
22 | 2751347.7467 | 1252887.6554
23 | 2751356.8957 | 1252874.732
24 | 2751346.7613 | 1252903.0282
25 | 2751363.8686 | 1252879.2924
26 | 2751368.0642 | 1252882.0356
27 | 2751398.9469 | 1252947.4949
28 | 2751324.604 | 1252924.5393
29 | 2751325.3278 | 1252854.6839
30 | 2751318.0058 | 1252842.218
31 | 2751371.6355 | 1252847.1081
32 | 2751309.0295 | 1252865.4975
33 | 2751393.9699 | 1252858.9574
34 | 2751413.3905 | 1252840.0083
35 | 2751428.0339 | 1252827.4171
36 | 2751416.6749 | 1252843.251
37 | 2751419.8085 | 1252913.7572
38 | 2751480.1614 | 1252846.1774
39 | 2751475.1756 | 1252836.3841
40 | 2751466.1899 | 1252818.6356
41 | 2751491.5812 | 1252896.5958
42 | 2751459.1356 | 1252809.6701
43 | 2751475.351 | 1252815.368
44 | 2751483.0238 | 1252811.0377
45 | 2751469.7698 | 1252806.38
46 | 2751486.4843 | 1252839.8581
47 | 2751501.4893 | 1252742.821
48 | 2751512.4978 | 1252746.6507
49 | 2751502.9947 | 1252732.9144
50 | 2751491.9015 | 1252766.6769
51 | 2751518.4326 | 1252758.4362
52 | 2751554.4106 | 1252721.9553
53 | 2751448.337 | 1252784.6585
54 | 2751445.1506 | 1252787.9136
55 | 2751439.8091 | 1252776.0843
56 | 2751489.6317 | 1252776.6327
57 | 2751467.3657 | 1252803.1631
58 | 2751475.043 | 1252782.5614
59 | 2751447.2066 | 1252806.7068
60 | 2751488.8236 | 1252777.4379
61 | 2751514.1545 | 1252901.2756
62 | 2751508.6748 | 1252888.9984
63 | 2751509.0552 | 1252810.3472
64 | 2751495.7416 | 1252860.2217
65 | 2751521.6329 | 1252706.5674
66 | 2751563.2585 | 1252747.0522
67 | 2751443.043 | 1252786.0185
68 | 2751430.2439 | 1252766.4672
69 | 2751265.2524 | 1252966.2176
70 | 2751292.8731 | 1252936.2354
71 | 2751261.366 | 1252971.7884
72 | 2751298.2063 | 1252927.6959
73 | 2751254.9756 | 1252984.5108
74 | 2751309.2903 | 1252911.4297
75 | 2751291.6201 | 1252926.6155
76 | 2751242.8437 | 1253010.8724
77 | 2751309.4461 | 1252891.1583
78 | 2751268.89 | 1252939.1747
79 | 2751505.8451 | 1252882.6585
80 | 2751501.9944 | 1252874.031
81 | 2751507.7436 | 1252886.9121
82 | 2751265.6894 | 1252856.7518
83 | 2751263.2504 | 1252844.3552
84 | 2751276.0173 | 1252839.6432
85 | 2751254.4144 | 1252837.1858
86 | 2751302.6494 | 1252843.8221
87 | 2751245.0873 | 1252816.1862
88 | 2751232.9285 | 1252803.5969
89 | 2751301.9717 | 1252870.1803
90 | 2751296.4119 | 1252873.8419
91 | 2751293.3655 | 1252744.3153
92 | 2751294.2873 | 1252724.4973
93 | 2751310.1341 | 1252720.4169
94 | 2751286.7927 | 1252750.2885
95 | 2751101.7808 | 1253041.7054
96 | 2751098.8911 | 1253030.0981
97 | 2751068.603 | 1252932.1203
98 | 2751040.0092 | 1252886.9124
99 | 2751250.5896 | 1252705.9314
100 | 2751295.2555 | 1252703.457
101 | 2751263.3506 | 1252771.5924
102 | 2751218.6576 | 1252790.0416
103 | 2751239.2781 | 1252797.5875
104 | 2751216.7527 | 1252795.7461
105 | 2751196.485 | 1252782.8576
106 | 2751429.5874 | 1252765.8062
107 | 2751374.1036 | 1252710.2443
108 | 2751391.7083 | 1252727.6697
109 | 2751363.2858 | 1252698.68
110 | 2751419.7303 | 1252755.8821
111 | 2751402.343 | 1252738.3766
112 | 2751319.2144 | 1252651.5669
113 | 2751329.9968 | 1252663.0936
114 | 2751296.6648 | 1252630.5997
115 | 2751336.9889 | 1252670.5685
116 | 2751302.9876 | 1252600.643
117 | 2751321.0765 | 1252687.2562
118 | 2751306.5643 | 1252596.8321
119 | 2751312.0553 | 1252695.4671
120 | 2751314.2033 | 1252696.1493
121 | 2751280.6213 | 1252693.5854
122 | 2751328.3511 | 1252694.7938
123 | 2751339.7092 | 1252581.6591
124 | 2751326.7132 | 1252703.3381
125 | 2751269.9575 | 1252682.3571
126 | 2751049.992 | 1252868.8048
127 | 2751094.6457 | 1252893.2562
128 | 2751202.2561 | 1252780.5883
129 | 2751186.452 | 1252812.3071
130 | 2751199.2012 | 1252779.0899
131 | 2751565.4639 | 1252747.2476
132 | 2751663.9754 | 1252793.0606
133 | 2751640.8669 | 1252802.6785
134 | 2751627.0518 | 1252712.1253
135 | 2751619.7066 | 1252750.0967
136 | 2751602.9558 | 1252755.0726
137 | 2751584.9131 | 1252715.1447
138 | 2751497.5711 | 1252689.4131
139 | 2751506.8009 | 1252696.3613
140 | 2751500.0773 | 1252676.3984
141 | 2751532.1928 | 1252691.6451
142 | 2751517.4622 | 1252678.9523
143 | 2751535.5367 | 1252686.9593
144 | 2751549.7393 | 1252668.9384
145 | 2751565.5179 | 1252650.5926
146 | 2751435.6558 | 1252565.4149
147 | 2751418.0494 | 1252561.0771
148 | 2751398.1532 | 1252569.8994
149 | 2751407.376 | 1252568.1613
150 | 2751380.8486 | 1252573.1605
151 | 2751371.8057 | 1252847.3306

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1