## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3252-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3252-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3252-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3252-2_0_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_3252-2_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_3252-2_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_3252-2_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_3252-2_0_4_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_3252-2_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_3252-2_0_4_node_43 | 0.4 | n |  | TRUE
10 | bus_LV_3252-2_0_4_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_3252-2_0_4_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_3252-2_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_3252-2_0_4_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_3252-2_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_3252-2_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3252-2_0_4_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_3252-2_0_4_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_3252-2_0_4_node_128 | 0.4 | n |  | TRUE
19 | bus_LV_3252-2_0_4_node_129 | 0.4 | n |  | TRUE
20 | bus_LV_3252-2_0_4_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_3252-2_0_4_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_3252-2_0_4_node_131 | 0.4 | n |  | TRUE
23 | bus_LV_3252-2_0_4_node_389 | 0.4 | n |  | TRUE
24 | bus_LV_3252-2_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_3252-2_0_4_node_201 | 0.4 | n |  | TRUE
26 | bus_LV_3252-2_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_3252-2_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_3252-2_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_3252-2_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_3252-2_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_3252-2_0_4_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_3252-2_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_3252-2_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_3252-2_0_4_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_3252-2_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_3252-2_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_3252-2_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_3252-2_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_3252-2_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_3252-2_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_3252-2_0_4_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_3252-2_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_3252-2_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_3252-2_0_4_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_3252-2_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_3252-2_0_4_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_3252-2_0_4_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_3252-2_0_4_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_3252-2_0_4_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_3252-2_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_3252-2_0_4_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_3252-2_0_4_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_3252-2_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_3252-2_0_4_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_3252-2_0_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_3252-2_0_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_3252-2_0_4_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_3252-2_0_4_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_3252-2_0_4_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_3252-2_0_4_node_390 | 0.4 | n |  | TRUE
61 | bus_LV_3252-2_0_4_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_3252-2_0_4_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_3252-2_0_4_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_3252-2_0_4_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_3252-2_0_4_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_3252-2_0_4_node_66 | 0.4 | n |  | TRUE
67 | bus_LV_3252-2_0_4_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_3252-2_0_4_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_3252-2_0_4_node_72 | 0.4 | n |  | TRUE
70 | bus_LV_3252-2_0_4_node_73 | 0.4 | n |  | TRUE
71 | bus_MV_49_0_node_213 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3252-2_0_4_load_0 | 0 | 0.019277 | 0.0048314 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3252-2_0_4_load_1 | 1 | 0.0019555 | 0.00049008 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3252-2_0_4_load_7 | 5 | 0.0016145 | 0.00040462 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3252-2_0_4_load_3 | 6 | 0.0024983 | 0.00062612 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3252-2_0_4_load_4 | 8 | 0.0082817 | 0.0020756 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3252-2_0_4_load_43 | 9 | 0.0041674 | 0.0010444 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3252-2_0_4_load_42 | 10 | 0.0021495 | 0.00053873 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3252-2_0_4_load_39 | 12 | 0.0020913 | 0.00052413 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3252-2_0_4_load_40 | 13 | 0.0023786 | 0.00059614 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3252-2_0_4_load_8 | 14 | 0.002326 | 0.00058295 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3252-2_0_4_load_9 | 15 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3252-2_0_4_load_26 | 16 | 0.0024472 | 0.00061332 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3252-2_0_4_load_128 | 18 | 0.00081788 | 0.00020498 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3252-2_0_4_load_129 | 19 | 0.0010707 | 0.00026833 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3252-2_0_4_load_36 | 20 | 0.00072222 | 0.00018101 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3252-2_0_4_load_132 | 21 | 0.0010865 | 0.0002723 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3252-2_0_4_load_389 | 23 | 0.00221 | 0.00055389 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3252-2_0_4_load_24 | 24 | 0.0026059 | 0.00065309 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3252-2_0_4_load_201 | 25 | 0.001182 | 0.00029622 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3252-2_0_4_load_17 | 26 | 0.0013534 | 0.00033918 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3252-2_0_4_load_19 | 28 | 0.0020208 | 0.00050646 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3252-2_0_4_load_21 | 29 | 0.0011131 | 0.00027898 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3252-2_0_4_load_25 | 30 | 0.0057395 | 0.0014385 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3252-2_0_4_load_32 | 31 | 0.0010175 | 0.00025501 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3252-2_0_4_load_22 | 32 | 0.0027787 | 0.00069641 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3252-2_0_4_load_23 | 33 | 0.0032106 | 0.00080466 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3252-2_0_4_load_51 | 34 | 0.00074834 | 0.00018755 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3252-2_0_4_load_27 | 35 | 0.0031221 | 0.00078247 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3252-2_0_4_load_29 | 37 | 0.0012863 | 0.00032238 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3252-2_0_4_load_30 | 38 | 0.0012143 | 0.00030434 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3252-2_0_4_load_34 | 39 | 0.0013154 | 0.00032967 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3252-2_0_4_load_37 | 40 | 0.0024045 | 0.00060263 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3252-2_0_4_load_46 | 41 | 0.0026962 | 0.00067573 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3252-2_0_4_load_33 | 42 | 0.0012967 | 0.00032499 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3252-2_0_4_load_38 | 44 | 0.0014118 | 0.00035383 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3252-2_0_4_load_41 | 45 | 0.0024219 | 0.00060699 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3252-2_0_4_load_44 | 46 | 0.0022192 | 0.00055617 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3252-2_0_4_load_45 | 47 | 0.0022718 | 0.00056937 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3252-2_0_4_load_50 | 48 | 0.0022936 | 0.00057482 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3252-2_0_4_load_49 | 51 | 0.0009256 | 0.00023198 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3252-2_0_4_load_59 | 53 | 0.0029469 | 0.00073857 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3252-2_0_4_load_52 | 55 | 0.00085635 | 0.00021462 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3252-2_0_4_load_53 | 56 | 0.00015034 | 3.7679e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3252-2_0_4_load_55 | 57 | 0.0006612 | 0.00016571 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3252-2_0_4_load_57 | 58 | 0.0023827 | 0.00059716 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3252-2_0_4_load_390 | 60 | 0.006277 | 0.0015732 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3252-2_0_4_load_60 | 61 | 0.011241 | 0.0028174 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3252-2_0_4_load_61 | 62 | 0.00096134 | 0.00024093 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3252-2_0_4_load_67 | 63 | 0.00039598 | 9.9242e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3252-2_0_4_load_64 | 65 | 0.0010729 | 0.00026889 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3252-2_0_4_load_66 | 66 | 0.00029603 | 7.4193e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3252-2_0_4_load_72 | 69 | 0.00033963 | 8.512e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3252-2_0_4_load_73 | 70 | 0.00059138 | 0.00014821 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3252-2_0_4_line_0 |  | 0 | 1 | 0.010402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3252-2_0_4_line_1 |  | 1 | 2 | 0.015844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3252-2_0_4_line_2 |  | 2 | 3 | 0.024003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3252-2_0_4_line_3 |  | 2 | 4 | 0.029872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3252-2_0_4_line_4 |  | 2 | 5 | 0.019244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3252-2_0_4_line_5 |  | 3 | 9 | 0.036547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3252-2_0_4_line_6 |  | 3 | 10 | 0.019233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3252-2_0_4_line_7 |  | 4 | 11 | 0.024314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3252-2_0_4_line_8 |  | 4 | 12 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3252-2_0_4_line_9 |  | 5 | 13 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3252-2_0_4_line_10 |  | 6 | 7 | 0.011381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3252-2_0_4_line_11 |  | 7 | 16 | 0.022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3252-2_0_4_line_12 |  | 7 | 17 | 0.064162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3252-2_0_4_line_13 |  | 7 | 8 | 0.027914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3252-2_0_4_line_14 |  | 7 | 15 | 0.028245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3252-2_0_4_line_15 |  | 11 | 41 | 0.041429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3252-2_0_4_line_16 |  | 11 | 17 | 0.082039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3252-2_0_4_line_17 |  | 12 | 44 | 0.0094424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3252-2_0_4_line_18 |  | 13 | 45 | 0.00066315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3252-2_0_4_line_19 |  | 14 | 15 | 0.081388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3252-2_0_4_line_20 |  | 16 | 35 | 0.017902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3252-2_0_4_line_21 |  | 17 | 30 | 0.082818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3252-2_0_4_line_22 |  | 17 | 27 | 0.02542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3252-2_0_4_line_23 |  | 18 | 19 | 0.080398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3252-2_0_4_line_24 |  | 19 | 20 | 0.021463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3252-2_0_4_line_25 |  | 20 | 43 | 0.029065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3252-2_0_4_line_26 |  | 21 | 22 | 0.051649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3252-2_0_4_line_27 |  | 22 | 34 | 0.1808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3252-2_0_4_line_28 |  | 23 | 24 | 0.15266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3252-2_0_4_line_29 |  | 23 | 25 | 0.11145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3252-2_0_4_line_30 |  | 24 | 34 | 0.11528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3252-2_0_4_line_31 |  | 24 | 32 | 0.095831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3252-2_0_4_line_32 |  | 26 | 27 | 0.0097365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3252-2_0_4_line_33 |  | 26 | 28 | 0.023676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3252-2_0_4_line_34 |  | 27 | 29 | 0.0066339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3252-2_0_4_line_35 |  | 29 | 31 | 0.0092424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3252-2_0_4_line_36 |  | 30 | 33 | 0.0099041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3252-2_0_4_line_37 |  | 31 | 42 | 0.0063412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3252-2_0_4_line_38 |  | 32 | 33 | 0.062894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3252-2_0_4_line_39 |  | 35 | 36 | 0.0089911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3252-2_0_4_line_40 |  | 36 | 37 | 0.028008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3252-2_0_4_line_41 |  | 36 | 38 | 0.049651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3252-2_0_4_line_42 |  | 37 | 39 | 0.017773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3252-2_0_4_line_43 |  | 38 | 40 | 0.01665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3252-2_0_4_line_44 |  | 39 | 43 | 0.038628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3252-2_0_4_line_45 |  | 45 | 46 | 0.023417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3252-2_0_4_line_46 |  | 46 | 47 | 0.013529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3252-2_0_4_line_47 |  | 47 | 48 | 0.036667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3252-2_0_4_line_48 |  | 48 | 54 | 0.011749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3252-2_0_4_line_49 |  | 49 | 50 | 0.004171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3252-2_0_4_line_50 |  | 49 | 51 | 0.036679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3252-2_0_4_line_51 |  | 50 | 52 | 0.003776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3252-2_0_4_line_52 |  | 51 | 53 | 0.082141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3252-2_0_4_line_53 |  | 52 | 55 | 0.021967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3252-2_0_4_line_54 |  | 53 | 54 | 0.059261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3252-2_0_4_line_55 |  | 54 | 58 | 0.012065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3252-2_0_4_line_56 |  | 55 | 56 | 0.01839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3252-2_0_4_line_57 |  | 56 | 57 | 0.037401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3252-2_0_4_line_58 |  | 58 | 59 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3252-2_0_4_line_59 |  | 59 | 60 | 0.10302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3252-2_0_4_line_60 |  | 60 | 68 | 0.15061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3252-2_0_4_line_61 |  | 61 | 62 | 0.019352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3252-2_0_4_line_62 |  | 61 | 63 | 0.14983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3252-2_0_4_line_63 |  | 62 | 64 | 0.065304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3252-2_0_4_line_64 |  | 63 | 66 | 0.0028425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3252-2_0_4_line_65 |  | 64 | 65 | 0.049635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3252-2_0_4_line_66 |  | 66 | 67 | 0.048429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3252-2_0_4_line_67 |  | 67 | 68 | 0.003133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3252-2_0_4_line_68 |  | 68 | 69 | 0.1057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3252-2_0_4_line_69 |  | 69 | 70 | 0.0045176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3252-2_0_4_trafo_2 | 0.63 MVA 20/0.4 kV | 71 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2757500.0814 | 1245865.7465 | 2757500.0814 | 1245865.7465 | 2757493.7943 | 1245857.46
1 | 2757484.2179 | 1245844.8381 | 2757493.7943 | 1245857.46
2 | 2757484.2179 | 1245844.8381 | 2757493.9125 | 1245836.465 | 2757496.3428 | 1245825.5188
3 | 2757458.2412 | 1245858.5842 | 2757467.01 | 1245856.882 | 2757484.2179 | 1245844.8381
4 | 2757484.2179 | 1245844.8381 | 2757472.6804 | 1245829.4367
5 | 2757496.3428 | 1245825.5188 | 2757512.3306 | 1245813.8763 | 2757513.9112 | 1245807.879 | 2757509.9143 | 1245798.0964
6 | 2757496.3428 | 1245825.5188 | 2757487.9523 | 1245808.2123
7 | 2757458.2412 | 1245858.5842 | 2757444.7366 | 1245866.1109 | 2757439.533 | 1245873.3243
8 | 2757458.2412 | 1245858.5842 | 2757455.9979 | 1245849.1265 | 2757454.9266 | 1245847.7178
9 | 2757472.6804 | 1245829.4367 | 2757458.1727 | 1245810.0706
10 | 2757555.4355 | 1245949.4767 | 2757549.5793 | 1245939.7178
11 | 2757555.4355 | 1245949.4767 | 2757565.5267 | 1245958.309 | 2757565.1373 | 1245967.0379
12 | 2757501.2853 | 1245919.1421 | 2757504.4057 | 1245917.2119 | 2757542.6855 | 1245939.4282 | 2757555.4355 | 1245949.4767
13 | 2757555.4355 | 1245949.4767 | 2757582.3787 | 1245942.1794
14 | 2757555.4355 | 1245949.4767 | 2757546.2086 | 1245968.1278 | 2757543.466 | 1245975.0404
15 | 2757439.533 | 1245873.3243 | 2757405.6894 | 1245849.4289
16 | 2757501.2853 | 1245919.1421 | 2757504.4057 | 1245917.2119 | 2757486.5353 | 1245906.4046 | 2757479.7548 | 1245901.8423 | 2757470.5431 | 1245895.7473 | 2757439.533 | 1245873.3243
17 | 2757447.8142 | 1245841.6441 | 2757453.2442 | 1245845.5054 | 2757454.9266 | 1245847.7178
18 | 2757457.7751 | 1245809.5398 | 2757458.1727 | 1245810.0706
19 | 2757523.197 | 1246053.6556 | 2757530.8916 | 1246015.1116 | 2757533.0991 | 1246005.4385 | 2757536.4075 | 1245993.5925 | 2757537.126 | 1245991.0202 | 2757543.466 | 1245975.0404
20 | 2757571.0015 | 1245983.5722 | 2757564.9653 | 1245970.8954 | 2757565.1373 | 1245967.0379
21 | 2757501.2853 | 1245919.1421 | 2757526.289 | 1245933.4646 | 2757543.3074 | 1245944.1827 | 2757546.1011 | 1245949.7068 | 2757546.8883 | 1245953.3646 | 2757546.6104 | 1245956.9941 | 2757540.7876 | 1245970.1524 | 2757538.8458 | 1245975.7546
22 | 2757501.2853 | 1245919.1421 | 2757479.6122 | 1245932.5243
23 | 2757634.4774 | 1246163.9125 | 2757635.2521 | 1246141.6644 | 2757636.7981 | 1246083.5482
24 | 2757636.7981 | 1246083.5482 | 2757636.8519 | 1246081.5254 | 2757630.5169 | 1246069.3228 | 2757630.0202 | 1246063.6546
25 | 2757639.1119 | 1246037.2085 | 2757629.2412 | 1246054.7635 | 2757630.0202 | 1246063.6546
26 | 2757536.3044 | 1246445.5571 | 2757538.8918 | 1246445.4702 | 2757544.0685 | 1246454.6056 | 2757547.3485 | 1246455.1933 | 2757559.5937 | 1246454.0508 | 2757560.2382 | 1246452.5553 | 2757556.2305 | 1246433.8526 | 2757558.3928 | 1246433.265
27 | 2757527.9222 | 1246255.0468 | 2757558.3928 | 1246433.265
28 | 2757511.6898 | 1246140.9129 | 2757361.8577 | 1246111.6642
29 | 2757251.2399 | 1246125.2439 | 2757361.8577 | 1246111.6642
30 | 2757511.6898 | 1246140.9129 | 2757527.9222 | 1246255.0468
31 | 2757511.6898 | 1246140.9129 | 2757510.9741 | 1246135.6458 | 2757509.8996 | 1246122.8936 | 2757509.8218 | 1246112.7371 | 2757511.1125 | 1246095.1763 | 2757513.6174 | 1246078.2928 | 2757520.6761 | 1246046.1747
32 | 2757479.6122 | 1245932.5243 | 2757483.5789 | 1245941.4161
33 | 2757478.3691 | 1245964.5116 | 2757483.5789 | 1245941.4161
34 | 2757479.6122 | 1245932.5243 | 2757474.0304 | 1245928.9392
35 | 2757474.0304 | 1245928.9392 | 2757474.0304 | 1245928.9392 | 2757465.5302 | 1245932.5681
36 | 2757538.8458 | 1245975.7546 | 2757535.6021 | 1245985.1125
37 | 2757465.5302 | 1245932.5681 | 2757459.6982 | 1245935.0578
38 | 2757535.6021 | 1245985.1125 | 2757535.1876 | 1245986.3085 | 2757531.3186 | 1245999.0516 | 2757526.7401 | 1246018.5826 | 2757520.6761 | 1246046.1747
39 | 2757574.8668 | 1245991.69 | 2757571.0015 | 1245983.5722
40 | 2757574.8668 | 1245991.69 | 2757584.1159 | 1245990.4011 | 2757594.9089 | 1245992.1674 | 2757601.5357 | 1245996.153
41 | 2757574.8668 | 1245991.69 | 2757582.638 | 1246007.601 | 2757583.7062 | 1246023.1447 | 2757582.781 | 1246039.4818
42 | 2757615.5668 | 1246006.9902 | 2757605.6081 | 1245998.6024 | 2757601.5357 | 1245996.153
43 | 2757581.8395 | 1246056.1053 | 2757582.781 | 1246039.4818
44 | 2757639.1119 | 1246037.2085 | 2757623.7299 | 1246013.8656 | 2757615.5668 | 1246006.9902
45 | 2757457.7751 | 1245809.5398 | 2757446.6858 | 1245794.7369 | 2757444.7448 | 1245790.2143
46 | 2757444.7448 | 1245790.2143 | 2757439.4092 | 1245777.7821
47 | 2757439.4092 | 1245777.7821 | 2757427.7923 | 1245750.7144 | 2757426.7975 | 1245743.5715
48 | 2757426.4338 | 1245731.8487 | 2757426.421 | 1245740.8683 | 2757426.7975 | 1245743.5715
49 | 2757269.5347 | 1245750.6274 | 2757266.76 | 1245747.5063
50 | 2757269.5347 | 1245750.6274 | 2757274.3772 | 1245747.3303 | 2757284.7598 | 1245745.7819 | 2757295.4319 | 1245741.0158 | 2757299.6249 | 1245733.4664
51 | 2757264.584 | 1245750.5961 | 2757266.76 | 1245747.5063
52 | 2757373.9639 | 1245722.9102 | 2757368.2576 | 1245724.3532 | 2757355.0851 | 1245724.2036 | 2757343.5936 | 1245721.6741 | 2757326.9064 | 1245716.3818 | 2757321.0185 | 1245716.6259 | 2757314.4633 | 1245718.9432 | 2757307.8321 | 1245723.8388 | 2757300.9654 | 1245731.0527 | 2757299.6249 | 1245733.4664
53 | 2757264.584 | 1245750.5961 | 2757252.7528 | 1245767.4212 | 2757252.169 | 1245768.6924
54 | 2757426.4338 | 1245731.8487 | 2757416.0066 | 1245720.5609 | 2757410.0188 | 1245717.1653 | 2757401.5317 | 1245715.9389 | 2757373.9639 | 1245722.9102
55 | 2757426.4338 | 1245731.8487 | 2757428.1953 | 1245726.1565 | 2757430.6031 | 1245720.5452
56 | 2757252.169 | 1245768.6924 | 2757247.8025 | 1245778.2006 | 2757243.3035 | 1245784.7278
57 | 2757243.3035 | 1245784.7278 | 2757222.0775 | 1245815.522 | 2757222.0775 | 1245815.522
58 | 2757437.4062 | 1245704.691 | 2757430.6031 | 1245720.5452
59 | 2757437.4062 | 1245704.691 | 2757512.5696 | 1245634.2393
60 | 2757512.5696 | 1245634.2393 | 2757472.9241 | 1245488.944
61 | 2757374.6655 | 1245360.903 | 2757379.6354 | 1245347.4293 | 2757382.9138 | 1245343.6667
62 | 2757499.8623 | 1245443.2065 | 2757374.6655 | 1245360.903
63 | 2757430.7626 | 1245301.1071 | 2757426.3405 | 1245306.2058 | 2757418.2509 | 1245314.7551 | 2757398.1783 | 1245333.8412 | 2757389.8271 | 1245335.7326 | 2757382.9138 | 1245343.6667
64 | 2757498.7349 | 1245445.7555 | 2757498.8304 | 1245444.9107 | 2757499.8623 | 1245443.2065
65 | 2757430.7626 | 1245301.1071 | 2757473.3184 | 1245290.5929 | 2757478.9619 | 1245289.2586
66 | 2757475.005 | 1245486.5969 | 2757486.9367 | 1245473.1449 | 2757497.6246 | 1245455.578 | 2757498.7349 | 1245445.7555
67 | 2757475.005 | 1245486.5969 | 2757472.9241 | 1245488.944
68 | 2757472.9241 | 1245488.944 | 2757453.4636 | 1245498.3811 | 2757445.0612 | 1245501.3499 | 2757436.1552 | 1245506.7744 | 2757421.7931 | 1245513.2552 | 2757415.2131 | 1245514.504 | 2757407.8666 | 1245514.1532 | 2757393.9991 | 1245513.6847 | 2757374.1167 | 1245520.592
69 | 2757369.8493 | 1245522.0745 | 2757374.1167 | 1245520.592

## bus_geodata
| x | y | coords
0 | 2757500.0814 | 1245865.7465
1 | 2757493.7943 | 1245857.46
2 | 2757484.2179 | 1245844.8381
3 | 2757496.3428 | 1245825.5188
4 | 2757458.2412 | 1245858.5842
5 | 2757472.6804 | 1245829.4367
6 | 2757549.5793 | 1245939.7178
7 | 2757555.4355 | 1245949.4767
8 | 2757582.3787 | 1245942.1794
9 | 2757509.9143 | 1245798.0964
10 | 2757487.9523 | 1245808.2123
11 | 2757439.533 | 1245873.3243
12 | 2757454.9266 | 1245847.7178
13 | 2757458.1727 | 1245810.0706
14 | 2757523.197 | 1246053.6556
15 | 2757543.466 | 1245975.0404
16 | 2757565.1373 | 1245967.0379
17 | 2757501.2853 | 1245919.1421
18 | 2757634.4774 | 1246163.9125
19 | 2757636.7981 | 1246083.5482
20 | 2757630.0202 | 1246063.6546
21 | 2757536.3044 | 1246445.5571
22 | 2757558.3928 | 1246433.265
23 | 2757361.8577 | 1246111.6642
24 | 2757511.6898 | 1246140.9129
25 | 2757251.2399 | 1246125.2439
26 | 2757483.5789 | 1245941.4161
27 | 2757479.6122 | 1245932.5243
28 | 2757478.3691 | 1245964.5116
29 | 2757474.0304 | 1245928.9392
30 | 2757538.8458 | 1245975.7546
31 | 2757465.5302 | 1245932.5681
32 | 2757520.6761 | 1246046.1747
33 | 2757535.6021 | 1245985.1125
34 | 2757527.9222 | 1246255.0468
35 | 2757571.0015 | 1245983.5722
36 | 2757574.8668 | 1245991.69
37 | 2757601.5357 | 1245996.153
38 | 2757582.781 | 1246039.4818
39 | 2757615.5668 | 1246006.9902
40 | 2757581.8395 | 1246056.1053
41 | 2757405.6894 | 1245849.4289
42 | 2757459.6982 | 1245935.0578
43 | 2757639.1119 | 1246037.2085
44 | 2757447.8142 | 1245841.6441
45 | 2757457.7751 | 1245809.5398
46 | 2757444.7448 | 1245790.2143
47 | 2757439.4092 | 1245777.7821
48 | 2757426.7975 | 1245743.5715
49 | 2757269.5347 | 1245750.6274
50 | 2757266.76 | 1245747.5063
51 | 2757299.6249 | 1245733.4664
52 | 2757264.584 | 1245750.5961
53 | 2757373.9639 | 1245722.9102
54 | 2757426.4338 | 1245731.8487
55 | 2757252.169 | 1245768.6924
56 | 2757243.3035 | 1245784.7278
57 | 2757222.0775 | 1245815.522
58 | 2757430.6031 | 1245720.5452
59 | 2757437.4062 | 1245704.691
60 | 2757512.5696 | 1245634.2393
61 | 2757374.6655 | 1245360.903
62 | 2757382.9138 | 1245343.6667
63 | 2757499.8623 | 1245443.2065
64 | 2757430.7626 | 1245301.1071
65 | 2757478.9619 | 1245289.2586
66 | 2757498.7349 | 1245445.7555
67 | 2757475.005 | 1245486.5969
68 | 2757472.9241 | 1245488.944
69 | 2757374.1167 | 1245520.592
70 | 2757369.8493 | 1245522.0745
71 | 2757496.3428 | 1245825.5188

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1