## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3275-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3275-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3275-7_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_3275-7_0_3_node_40 | 0.4 | n |  | TRUE
4 | bus_LV_3275-7_0_3_node_56 | 0.4 | n |  | TRUE
5 | bus_LV_3275-7_0_3_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_3275-7_0_3_node_69 | 0.4 | n |  | TRUE
7 | bus_LV_3275-7_0_3_node_52 | 0.4 | n |  | TRUE
8 | bus_LV_3275-7_0_3_node_53 | 0.4 | n |  | TRUE
9 | bus_LV_3275-7_0_3_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_3275-7_0_3_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_3275-7_0_3_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_3275-7_0_3_node_58 | 0.4 | n |  | TRUE
13 | bus_LV_3275-7_0_3_node_68 | 0.4 | n |  | TRUE
14 | bus_LV_3275-7_0_3_node_59 | 0.4 | n |  | TRUE
15 | bus_LV_3275-7_0_3_node_60 | 0.4 | n |  | TRUE
16 | bus_LV_3275-7_0_3_node_61 | 0.4 | n |  | TRUE
17 | bus_LV_3275-7_0_3_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_3275-7_0_3_node_63 | 0.4 | n |  | TRUE
19 | bus_LV_3275-7_0_3_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_3275-7_0_3_node_269 | 0.4 | n |  | TRUE
21 | bus_LV_3275-7_0_3_node_64 | 0.4 | n |  | TRUE
22 | bus_LV_3275-7_0_3_node_65 | 0.4 | n |  | TRUE
23 | bus_LV_3275-7_0_3_node_66 | 0.4 | n |  | TRUE
24 | bus_LV_3275-7_0_3_node_202 | 0.4 | n |  | TRUE
25 | bus_LV_3275-7_0_3_node_70 | 0.4 | n |  | TRUE
26 | bus_LV_3275-7_0_3_node_71 | 0.4 | n |  | TRUE
27 | bus_LV_3275-7_0_3_node_72 | 0.4 | n |  | TRUE
28 | bus_LV_3275-7_0_3_node_216 | 0.4 | n |  | TRUE
29 | bus_LV_3275-7_0_3_node_231 | 0.4 | n |  | TRUE
30 | bus_LV_3275-7_0_3_node_183 | 0.4 | n |  | TRUE
31 | bus_LV_3275-7_0_3_node_184 | 0.4 | n |  | TRUE
32 | bus_LV_3275-7_0_3_node_185 | 0.4 | n |  | TRUE
33 | bus_LV_3275-7_0_3_node_196 | 0.4 | n |  | TRUE
34 | bus_LV_3275-7_0_3_node_186 | 0.4 | n |  | TRUE
35 | bus_LV_3275-7_0_3_node_187 | 0.4 | n |  | TRUE
36 | bus_LV_3275-7_0_3_node_188 | 0.4 | n |  | TRUE
37 | bus_LV_3275-7_0_3_node_189 | 0.4 | n |  | TRUE
38 | bus_LV_3275-7_0_3_node_191 | 0.4 | n |  | TRUE
39 | bus_LV_3275-7_0_3_node_193 | 0.4 | n |  | TRUE
40 | bus_LV_3275-7_0_3_node_190 | 0.4 | n |  | TRUE
41 | bus_LV_3275-7_0_3_node_192 | 0.4 | n |  | TRUE
42 | bus_LV_3275-7_0_3_node_194 | 0.4 | n |  | TRUE
43 | bus_LV_3275-7_0_3_node_195 | 0.4 | n |  | TRUE
44 | bus_LV_3275-7_0_3_node_198 | 0.4 | n |  | TRUE
45 | bus_LV_3275-7_0_3_node_211 | 0.4 | n |  | TRUE
46 | bus_LV_3275-7_0_3_node_197 | 0.4 | n |  | TRUE
47 | bus_LV_3275-7_0_3_node_199 | 0.4 | n |  | TRUE
48 | bus_LV_3275-7_0_3_node_200 | 0.4 | n |  | TRUE
49 | bus_LV_3275-7_0_3_node_201 | 0.4 | n |  | TRUE
50 | bus_LV_3275-7_0_3_node_203 | 0.4 | n |  | TRUE
51 | bus_LV_3275-7_0_3_node_204 | 0.4 | n |  | TRUE
52 | bus_LV_3275-7_0_3_node_205 | 0.4 | n |  | TRUE
53 | bus_LV_3275-7_0_3_node_206 | 0.4 | n |  | TRUE
54 | bus_LV_3275-7_0_3_node_207 | 0.4 | n |  | TRUE
55 | bus_LV_3275-7_0_3_node_208 | 0.4 | n |  | TRUE
56 | bus_LV_3275-7_0_3_node_209 | 0.4 | n |  | TRUE
57 | bus_LV_3275-7_0_3_node_210 | 0.4 | n |  | TRUE
58 | bus_LV_3275-7_0_3_node_212 | 0.4 | n |  | TRUE
59 | bus_LV_3275-7_0_3_node_214 | 0.4 | n |  | TRUE
60 | bus_LV_3275-7_0_3_node_213 | 0.4 | n |  | TRUE
61 | bus_LV_3275-7_0_3_node_215 | 0.4 | n |  | TRUE
62 | bus_LV_3275-7_0_3_node_222 | 0.4 | n |  | TRUE
63 | bus_LV_3275-7_0_3_node_217 | 0.4 | n |  | TRUE
64 | bus_LV_3275-7_0_3_node_218 | 0.4 | n |  | TRUE
65 | bus_LV_3275-7_0_3_node_219 | 0.4 | n |  | TRUE
66 | bus_LV_3275-7_0_3_node_220 | 0.4 | n |  | TRUE
67 | bus_LV_3275-7_0_3_node_221 | 0.4 | n |  | TRUE
68 | bus_LV_3275-7_0_3_node_236 | 0.4 | n |  | TRUE
69 | bus_LV_3275-7_0_3_node_223 | 0.4 | n |  | TRUE
70 | bus_LV_3275-7_0_3_node_229 | 0.4 | n |  | TRUE
71 | bus_LV_3275-7_0_3_node_224 | 0.4 | n |  | TRUE
72 | bus_LV_3275-7_0_3_node_225 | 0.4 | n |  | TRUE
73 | bus_LV_3275-7_0_3_node_226 | 0.4 | n |  | TRUE
74 | bus_LV_3275-7_0_3_node_227 | 0.4 | n |  | TRUE
75 | bus_LV_3275-7_0_3_node_228 | 0.4 | n |  | TRUE
76 | bus_LV_3275-7_0_3_node_252 | 0.4 | n |  | TRUE
77 | bus_LV_3275-7_0_3_node_230 | 0.4 | n |  | TRUE
78 | bus_LV_3275-7_0_3_node_253 | 0.4 | n |  | TRUE
79 | bus_LV_3275-7_0_3_node_232 | 0.4 | n |  | TRUE
80 | bus_LV_3275-7_0_3_node_233 | 0.4 | n |  | TRUE
81 | bus_LV_3275-7_0_3_node_234 | 0.4 | n |  | TRUE
82 | bus_LV_3275-7_0_3_node_235 | 0.4 | n |  | TRUE
83 | bus_LV_3275-7_0_3_node_237 | 0.4 | n |  | TRUE
84 | bus_LV_3275-7_0_3_node_238 | 0.4 | n |  | TRUE
85 | bus_LV_3275-7_0_3_node_239 | 0.4 | n |  | TRUE
86 | bus_LV_3275-7_0_3_node_240 | 0.4 | n |  | TRUE
87 | bus_LV_3275-7_0_3_node_262 | 0.4 | n |  | TRUE
88 | bus_LV_3275-7_0_3_node_241 | 0.4 | n |  | TRUE
89 | bus_LV_3275-7_0_3_node_242 | 0.4 | n |  | TRUE
90 | bus_LV_3275-7_0_3_node_243 | 0.4 | n |  | TRUE
91 | bus_LV_3275-7_0_3_node_244 | 0.4 | n |  | TRUE
92 | bus_LV_3275-7_0_3_node_245 | 0.4 | n |  | TRUE
93 | bus_LV_3275-7_0_3_node_246 | 0.4 | n |  | TRUE
94 | bus_LV_3275-7_0_3_node_264 | 0.4 | n |  | TRUE
95 | bus_LV_3275-7_0_3_node_247 | 0.4 | n |  | TRUE
96 | bus_LV_3275-7_0_3_node_248 | 0.4 | n |  | TRUE
97 | bus_LV_3275-7_0_3_node_249 | 0.4 | n |  | TRUE
98 | bus_LV_3275-7_0_3_node_265 | 0.4 | n |  | TRUE
99 | bus_LV_3275-7_0_3_node_250 | 0.4 | n |  | TRUE
100 | bus_LV_3275-7_0_3_node_251 | 0.4 | n |  | TRUE
101 | bus_LV_3275-7_0_3_node_254 | 0.4 | n |  | TRUE
102 | bus_LV_3275-7_0_3_node_255 | 0.4 | n |  | TRUE
103 | bus_LV_3275-7_0_3_node_256 | 0.4 | n |  | TRUE
104 | bus_LV_3275-7_0_3_node_257 | 0.4 | n |  | TRUE
105 | bus_LV_3275-7_0_3_node_258 | 0.4 | n |  | TRUE
106 | bus_LV_3275-7_0_3_node_259 | 0.4 | n |  | TRUE
107 | bus_LV_3275-7_0_3_node_260 | 0.4 | n |  | TRUE
108 | bus_LV_3275-7_0_3_node_261 | 0.4 | n |  | TRUE
109 | bus_LV_3275-7_0_3_node_263 | 0.4 | n |  | TRUE
110 | bus_LV_3275-7_0_3_node_266 | 0.4 | n |  | TRUE
111 | bus_LV_3275-7_0_3_node_267 | 0.4 | n |  | TRUE
112 | bus_LV_3275-7_0_3_node_268 | 0.4 | n |  | TRUE
113 | bus_LV_3275-7_0_3_node_270 | 0.4 | n |  | TRUE
114 | bus_LV_3275-7_0_3_node_271 | 0.4 | n |  | TRUE
115 | bus_MV_53_0_node_202 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3275-7_0_3_load_0 | 0 | 0.0011541 | 0.00028925 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3275-7_0_3_load_1 | 1 | 0.00069534 | 0.00017427 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3275-7_0_3_load_3 | 2 | 0.0012122 | 0.00030382 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3275-7_0_3_load_40 | 3 | 0.00045894 | 0.00011502 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3275-7_0_3_load_56 | 4 | 0.0041225 | 0.0010332 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3275-7_0_3_load_15 | 5 | 0.0011164 | 0.00027979 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3275-7_0_3_load_69 | 6 | 0.0012575 | 0.00031516 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3275-7_0_3_load_52 | 7 | 0.010299 | 0.0025812 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3275-7_0_3_load_53 | 8 | 0.00038435 | 9.6328e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3275-7_0_3_load_54 | 9 | 0.0024766 | 0.00062069 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3275-7_0_3_load_55 | 10 | 0.010232 | 0.0025643 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3275-7_0_3_load_57 | 11 | 0.0025023 | 0.00062712 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3275-7_0_3_load_58 | 12 | 0.0077185 | 0.0019344 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3275-7_0_3_load_68 | 13 | 0.0068252 | 0.0017105 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3275-7_0_3_load_59 | 14 | 0.0023067 | 0.00057812 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3275-7_0_3_load_60 | 15 | 0.0022465 | 0.00056303 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3275-7_0_3_load_61 | 16 | 0.0014976 | 0.00037533 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3275-7_0_3_load_62 | 17 | 0.0010066 | 0.00025228 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3275-7_0_3_load_63 | 18 | 0.0018897 | 0.00047361 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3275-7_0_3_load_269 | 20 | 0.0031051 | 0.00077822 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3275-7_0_3_load_64 | 21 | 0.0077448 | 0.001941 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3275-7_0_3_load_65 | 22 | 0.0073851 | 0.0018509 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3275-7_0_3_load_202 | 24 | 0.0016926 | 0.00042421 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3275-7_0_3_load_71 | 26 | 0.0033496 | 0.0008395 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3275-7_0_3_load_72 | 27 | 0.0022535 | 0.00056478 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3275-7_0_3_load_216 | 28 | 0.0037497 | 0.00093975 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3275-7_0_3_load_231 | 29 | 0.0094575 | 0.0023703 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3275-7_0_3_load_183 | 30 | 0.00056991 | 0.00014283 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3275-7_0_3_load_184 | 31 | 0.00054003 | 0.00013534 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3275-7_0_3_load_185 | 32 | 0.00072083 | 0.00018066 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3275-7_0_3_load_196 | 33 | 0.00181 | 0.00045363 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3275-7_0_3_load_186 | 34 | 0.0027935 | 0.00070012 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3275-7_0_3_load_187 | 35 | 0.0014179 | 0.00035537 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3275-7_0_3_load_188 | 36 | 0.002137 | 0.00053559 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3275-7_0_3_load_189 | 37 | 0.0022602 | 0.00056645 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3275-7_0_3_load_191 | 38 | 0.00056858 | 0.0001425 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3275-7_0_3_load_193 | 39 | 0.0015519 | 0.00038894 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3275-7_0_3_load_190 | 40 | 0.00049096 | 0.00012305 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3275-7_0_3_load_194 | 42 | 0.001298 | 0.00032531 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3275-7_0_3_load_195 | 43 | 0.0017112 | 0.00042887 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3275-7_0_3_load_198 | 44 | 0.0021057 | 0.00052774 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3275-7_0_3_load_211 | 45 | 0.0012081 | 0.00030279 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3275-7_0_3_load_197 | 46 | 0.0012761 | 0.00031981 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3275-7_0_3_load_199 | 47 | 0.0017772 | 0.0004454 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3275-7_0_3_load_200 | 48 | 0.00079247 | 0.00019861 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3275-7_0_3_load_201 | 49 | 0.0014955 | 0.00037481 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3275-7_0_3_load_203 | 50 | 0.0012293 | 0.0003081 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3275-7_0_3_load_204 | 51 | 0.0010981 | 0.00027521 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3275-7_0_3_load_205 | 52 | 0.0015157 | 0.00037988 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3275-7_0_3_load_206 | 53 | 0.0014738 | 0.00036936 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3275-7_0_3_load_207 | 54 | 0.0021089 | 0.00052855 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3275-7_0_3_load_209 | 56 | 0.0012761 | 0.00031981 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3275-7_0_3_load_210 | 57 | 0.0022695 | 0.00056878 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3275-7_0_3_load_212 | 58 | 0.001105 | 0.00027694 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3275-7_0_3_load_214 | 59 | 0.0011199 | 0.00028067 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3275-7_0_3_load_213 | 60 | 0.0017681 | 0.00044314 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3275-7_0_3_load_215 | 61 | 0.0015487 | 0.00038815 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3275-7_0_3_load_217 | 63 | 0.0078038 | 0.0019558 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3275-7_0_3_load_219 | 65 | 0.0023237 | 0.00058238 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3275-7_0_3_load_220 | 66 | 0.00097052 | 0.00024324 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3275-7_0_3_load_221 | 67 | 0.003596 | 0.00090123 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3275-7_0_3_load_236 | 68 | 0.0013489 | 0.00033806 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3275-7_0_3_load_223 | 69 | 0.00049436 | 0.0001239 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3275-7_0_3_load_224 | 71 | 0.0017476 | 0.00043799 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3275-7_0_3_load_225 | 72 | 0.0013639 | 0.00034184 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3275-7_0_3_load_226 | 73 | 0.0028918 | 0.00072476 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3275-7_0_3_load_227 | 74 | 0.0008438 | 0.00021148 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3275-7_0_3_load_228 | 75 | 0.0015122 | 0.000379 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3275-7_0_3_load_252 | 76 | 0.0032623 | 0.00081762 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3275-7_0_3_load_230 | 77 | 0.0020182 | 0.00050581 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3275-7_0_3_load_253 | 78 | 0.0018877 | 0.00047309 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3275-7_0_3_load_232 | 79 | 0.013466 | 0.0033748 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3275-7_0_3_load_233 | 80 | 0.0028047 | 0.00070294 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3275-7_0_3_load_234 | 81 | 0.0010745 | 0.0002693 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3275-7_0_3_load_235 | 82 | 0.0022574 | 0.00056576 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3275-7_0_3_load_238 | 84 | 0.006682 | 0.0016747 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3275-7_0_3_load_239 | 85 | 0.0035215 | 0.00088258 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3275-7_0_3_load_240 | 86 | 0.010293 | 0.0025796 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3275-7_0_3_load_262 | 87 | 0.0036496 | 0.00091466 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3275-7_0_3_load_241 | 88 | 0.0089627 | 0.0022463 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3275-7_0_3_load_242 | 89 | 0.015607 | 0.0039115 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3275-7_0_3_load_244 | 91 | 0.0018186 | 0.00045578 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3275-7_0_3_load_245 | 92 | 0.013954 | 0.0034971 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3275-7_0_3_load_246 | 93 | 0.0016894 | 0.00042341 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3275-7_0_3_load_264 | 94 | 0.0067694 | 0.0016966 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3275-7_0_3_load_247 | 95 | 0.0016959 | 0.00042502 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3275-7_0_3_load_248 | 96 | 0.0016546 | 0.00041469 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3275-7_0_3_load_249 | 97 | 0.0032386 | 0.00081167 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3275-7_0_3_load_265 | 98 | 0.0021089 | 0.00052855 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3275-7_0_3_load_250 | 99 | 0.002996 | 0.00075087 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3275-7_0_3_load_251 | 100 | 0.0016972 | 0.00042537 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3275-7_0_3_load_254 | 101 | 0.0018175 | 0.0004555 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3275-7_0_3_load_255 | 102 | 0.0022309 | 0.00055911 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3275-7_0_3_load_256 | 103 | 0.0023354 | 0.00058529 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3275-7_0_3_load_257 | 104 | 0.0021588 | 0.00054104 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3275-7_0_3_load_258 | 105 | 0.0022612 | 0.00056671 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3275-7_0_3_load_259 | 106 | 0.003788 | 0.00094936 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3275-7_0_3_load_260 | 107 | 0.0037551 | 0.00094112 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3275-7_0_3_load_261 | 108 | 0.0010377 | 0.00026007 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3275-7_0_3_load_263 | 109 | 0.0048347 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3275-7_0_3_load_266 | 110 | 0.0027896 | 0.00069913 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3275-7_0_3_load_270 | 113 | 0.0014637 | 0.00036683 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3275-7_0_3_load_271 | 114 | 0.001488 | 0.00037293 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3275-7_0_3_line_0 |  | 0 | 1 | 0.066112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3275-7_0_3_line_1 |  | 1 | 2 | 0.024137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3275-7_0_3_line_2 |  | 1 | 3 | 0.22015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3275-7_0_3_line_3 |  | 2 | 4 | 0.033656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3275-7_0_3_line_4 |  | 4 | 9 | 0.031831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3275-7_0_3_line_5 |  | 5 | 6 | 0.021316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3275-7_0_3_line_6 |  | 6 | 24 | 0.11161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3275-7_0_3_line_7 |  | 7 | 8 | 0.018431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3275-7_0_3_line_8 |  | 7 | 9 | 0.0068779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3275-7_0_3_line_9 |  | 8 | 10 | 0.01912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3275-7_0_3_line_10 |  | 10 | 11 | 0.042088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3275-7_0_3_line_11 |  | 11 | 12 | 0.035602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3275-7_0_3_line_12 |  | 12 | 13 | 0.037505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3275-7_0_3_line_13 |  | 13 | 19 | 0.010827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_3275-7_0_3_line_14 |  | 14 | 15 | 0.0013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_3275-7_0_3_line_15 |  | 14 | 16 | 0.04192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_3275-7_0_3_line_16 |  | 15 | 17 | 0.0095577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_3275-7_0_3_line_17 |  | 16 | 18 | 0.024584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_3275-7_0_3_line_18 |  | 17 | 19 | 0.0081642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_3275-7_0_3_line_19 |  | 18 | 20 | 0.0061246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_3275-7_0_3_line_20 |  | 19 | 23 | 0.036297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3275-7_0_3_line_21 |  | 20 | 111 | 0.033345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_3275-7_0_3_line_22 |  | 21 | 22 | 0.035984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3275-7_0_3_line_23 |  | 21 | 23 | 0.018765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3275-7_0_3_line_24 |  | 24 | 50 | 0.018254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3275-7_0_3_line_25 |  | 24 | 49 | 0.017421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3275-7_0_3_line_26 |  | 25 | 26 | 0.018808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_3275-7_0_3_line_27 |  | 25 | 27 | 0.017973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_3275-7_0_3_line_28 |  | 26 | 28 | 0.0038196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_3275-7_0_3_line_29 |  | 27 | 29 | 0.027738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_3275-7_0_3_line_30 |  | 28 | 63 | 0.024419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_3275-7_0_3_line_31 |  | 29 | 79 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_3275-7_0_3_line_32 |  | 30 | 31 | 0.059121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3275-7_0_3_line_33 |  | 31 | 32 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3275-7_0_3_line_34 |  | 32 | 33 | 0.1402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3275-7_0_3_line_35 |  | 33 | 46 | 0.012383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3275-7_0_3_line_36 |  | 33 | 40 | 0.03246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3275-7_0_3_line_37 |  | 34 | 35 | 0.023475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3275-7_0_3_line_38 |  | 34 | 36 | 0.00035408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3275-7_0_3_line_39 |  | 35 | 37 | 0.021484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3275-7_0_3_line_40 |  | 35 | 38 | 0.0070698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3275-7_0_3_line_41 |  | 37 | 39 | 0.036317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3275-7_0_3_line_42 |  | 39 | 41 | 0.035731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3275-7_0_3_line_43 |  | 41 | 42 | 0.020908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3275-7_0_3_line_44 |  | 41 | 43 | 0.0099978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3275-7_0_3_line_45 |  | 42 | 44 | 0.015908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3275-7_0_3_line_46 |  | 43 | 45 | 0.015462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3275-7_0_3_line_47 |  | 44 | 47 | 0.032711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3275-7_0_3_line_48 |  | 45 | 46 | 0.01559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3275-7_0_3_line_49 |  | 47 | 48 | 0.024402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3275-7_0_3_line_50 |  | 48 | 49 | 0.0041918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3275-7_0_3_line_51 |  | 50 | 51 | 0.02439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3275-7_0_3_line_52 |  | 51 | 52 | 0.0080213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3275-7_0_3_line_53 |  | 52 | 53 | 0.016058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3275-7_0_3_line_54 |  | 53 | 54 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3275-7_0_3_line_55 |  | 54 | 55 | 0.020847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3275-7_0_3_line_56 |  | 55 | 56 | 0.047975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3275-7_0_3_line_57 |  | 55 | 57 | 0.024629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3275-7_0_3_line_58 |  | 56 | 58 | 0.0091369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3275-7_0_3_line_59 |  | 57 | 59 | 0.042149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3275-7_0_3_line_60 |  | 58 | 60 | 0.0032037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3275-7_0_3_line_61 |  | 59 | 61 | 0.022863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3275-7_0_3_line_62 |  | 61 | 62 | 0.015613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3275-7_0_3_line_63 |  | 62 | 69 | 0.019644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3275-7_0_3_line_64 |  | 62 | 67 | 0.015663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3275-7_0_3_line_65 |  | 63 | 64 | 0.026078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_3275-7_0_3_line_66 |  | 64 | 65 | 0.038908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3275-7_0_3_line_67 |  | 64 | 66 | 0.008657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_3275-7_0_3_line_68 |  | 65 | 67 | 0.00054831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3275-7_0_3_line_69 |  | 66 | 68 | 0.0022618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_3275-7_0_3_line_70 |  | 68 | 81 | 0.0041057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_3275-7_0_3_line_71 |  | 69 | 70 | 0.0093685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3275-7_0_3_line_72 |  | 70 | 77 | 0.016779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3275-7_0_3_line_73 |  | 70 | 74 | 0.0069788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3275-7_0_3_line_74 |  | 71 | 72 | 0.003637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3275-7_0_3_line_75 |  | 71 | 73 | 0.01429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3275-7_0_3_line_76 |  | 72 | 74 | 0.01982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3275-7_0_3_line_77 |  | 73 | 75 | 0.019976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3275-7_0_3_line_78 |  | 75 | 76 | 0.015324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3275-7_0_3_line_79 |  | 76 | 100 | 0.01283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3275-7_0_3_line_80 |  | 77 | 78 | 0.0034253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3275-7_0_3_line_81 |  | 78 | 101 | 0.018485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3275-7_0_3_line_82 |  | 79 | 80 | 0.0035042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_3275-7_0_3_line_83 |  | 81 | 82 | 0.026648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_3275-7_0_3_line_84 |  | 82 | 83 | 0.0051563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_3275-7_0_3_line_85 |  | 83 | 84 | 0.019627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_3275-7_0_3_line_86 |  | 83 | 85 | 0.02934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3275-7_0_3_line_87 |  | 84 | 86 | 0.0041839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_3275-7_0_3_line_88 |  | 85 | 87 | 0.019108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3275-7_0_3_line_89 |  | 86 | 88 | 0.017825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_3275-7_0_3_line_90 |  | 87 | 108 | 0.0037853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3275-7_0_3_line_91 |  | 88 | 89 | 0.023328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_3275-7_0_3_line_92 |  | 89 | 90 | 0.024649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_3275-7_0_3_line_93 |  | 90 | 91 | 0.013896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_3275-7_0_3_line_94 |  | 90 | 92 | 0.017123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3275-7_0_3_line_95 |  | 91 | 93 | 0.0095016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_3275-7_0_3_line_96 |  | 92 | 94 | 0.016977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3275-7_0_3_line_97 |  | 93 | 95 | 0.020443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_3275-7_0_3_line_98 |  | 94 | 109 | 0.04149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3275-7_0_3_line_99 |  | 95 | 96 | 0.0117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_3275-7_0_3_line_100 |  | 96 | 97 | 0.002201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_3275-7_0_3_line_101 |  | 97 | 98 | 0.026856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_3275-7_0_3_line_102 |  | 98 | 110 | 0.015878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_3275-7_0_3_line_103 |  | 99 | 100 | 0.039984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3275-7_0_3_line_104 |  | 101 | 102 | 0.0019839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3275-7_0_3_line_105 |  | 102 | 103 | 0.021743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3275-7_0_3_line_106 |  | 103 | 104 | 0.00028583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3275-7_0_3_line_107 |  | 105 | 106 | 0.0029603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3275-7_0_3_line_108 |  | 105 | 107 | 0.03971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3275-7_0_3_line_109 |  | 107 | 108 | 0.0039353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3275-7_0_3_line_110 |  | 110 | 111 | 0.030878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_3275-7_0_3_line_111 |  | 111 | 112 | 0.016705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3275-7_0_3_line_112 |  | 112 | 113 | 0.022139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3275-7_0_3_line_113 |  | 113 | 114 | 0.037569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3275-7_0_3_trafo_233 | 0.63 MVA 20/0.4 kV | 115 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2755259.2901 | 1223178.5305 | 2755266.7916 | 1223202.2722 | 2755272.418 | 1223238.7634 | 2755272.4364 | 1223243.0548
1 | 2755272.5395 | 1223267.1915 | 2755272.4364 | 1223243.0548
2 | 2755272.4364 | 1223243.0548 | 2755480.2125 | 1223170.2911
3 | 2755272.5395 | 1223267.1915 | 2755272.5685 | 1223273.9885 | 2755271.9987 | 1223300.841
4 | 2755270.7465 | 1223332.646 | 2755271.8433 | 1223308.1676 | 2755271.9987 | 1223300.841
5 | 2754977.7987 | 1223262.4718 | 2754979.5455 | 1223283.7162
6 | 2754904.664 | 1223366.4807 | 2754979.5455 | 1223283.7162
7 | 2755270.4387 | 1223339.517 | 2755269.6137 | 1223357.9294
8 | 2755270.4387 | 1223339.517 | 2755270.7465 | 1223332.646
9 | 2755269.6137 | 1223357.9294 | 2755268.7579 | 1223377.0299
10 | 2755268.7579 | 1223377.0299 | 2755268.6803 | 1223378.761 | 2755265.8245 | 1223419.0145
11 | 2755259.1849 | 1223453.9184 | 2755262.6042 | 1223441.1931 | 2755265.5231 | 1223423.2639 | 2755265.8245 | 1223419.0145
12 | 2755259.1849 | 1223453.9184 | 2755258.0995 | 1223457.9576 | 2755252.2958 | 1223473.9098 | 2755245.6931 | 1223488.864
13 | 2755241.32 | 1223498.7686 | 2755245.6931 | 1223488.864
14 | 2755235.5803 | 1223516.9303 | 2755235.9796 | 1223515.6668
15 | 2755223.2467 | 1223556.9738 | 2755223.6289 | 1223554.7476 | 2755235.5803 | 1223516.9303
16 | 2755238.8598 | 1223506.5534 | 2755235.9796 | 1223515.6668
17 | 2755223.2467 | 1223556.9738 | 2755219.087 | 1223581.2033
18 | 2755241.32 | 1223498.7686 | 2755238.8598 | 1223506.5534
19 | 2755218.0507 | 1223587.2395 | 2755219.087 | 1223581.2033
20 | 2755276.4789 | 1223508.183 | 2755241.32 | 1223498.7686
21 | 2755212.4085 | 1223620.1039 | 2755218.0507 | 1223587.2395
22 | 2755283.359 | 1223490.725 | 2755296.5524 | 1223457.2472
23 | 2755276.4789 | 1223508.183 | 2755283.359 | 1223490.725
24 | 2754904.664 | 1223366.4807 | 2754911.03 | 1223374.6966 | 2754910.2241 | 1223382.5152
25 | 2754889.62 | 1223368.4561 | 2754902.3674 | 1223363.5165 | 2754904.664 | 1223366.4807
26 | 2754969.3972 | 1223489.7097 | 2754965.5941 | 1223508.1295
27 | 2754969.3972 | 1223489.7097 | 2754987.1188 | 1223492.7074
28 | 2754965.5941 | 1223508.1295 | 2754964.8218 | 1223511.8702
29 | 2754987.1188 | 1223492.7074 | 2755014.4687 | 1223497.3339
30 | 2754959.8843 | 1223535.7847 | 2754964.8218 | 1223511.8702
31 | 2755030.8351 | 1223500.1025 | 2755014.4687 | 1223497.3339
32 | 2754640.7236 | 1223532.4293 | 2754645.7889 | 1223524.0379 | 2754656.8796 | 1223475.982
33 | 2754656.8796 | 1223475.982 | 2754656.8796 | 1223475.982 | 2754657.7652 | 1223462.2819
34 | 2754795.5564 | 1223436.4143 | 2754657.7652 | 1223462.2819
35 | 2754799.7534 | 1223446.2335 | 2754794.4996 | 1223441.8606 | 2754795.5564 | 1223436.4143
36 | 2754800.5913 | 1223404.5201 | 2754801.0806 | 1223407.9451 | 2754795.5564 | 1223436.4143
37 | 2754800.12 | 1223363.2504 | 2754803.8315 | 1223349.1851 | 2754811.6746 | 1223344.9184
38 | 2754800.12 | 1223363.2504 | 2754800.0296 | 1223363.5928
39 | 2754811.6746 | 1223344.9184 | 2754811.6746 | 1223344.9184 | 2754821.7588 | 1223348.4283 | 2754828.3953 | 1223356.9571
40 | 2754811.6746 | 1223344.9184 | 2754805.4643 | 1223348.2968
41 | 2754828.3953 | 1223356.9571 | 2754828.8515 | 1223357.5433 | 2754823.343 | 1223392.6881
42 | 2754826.2171 | 1223427.2719 | 2754820.5533 | 1223410.4871 | 2754823.343 | 1223392.6881
43 | 2754826.2171 | 1223427.2719 | 2754847.1229 | 1223426.944
44 | 2754826.2171 | 1223427.2719 | 2754821.9276 | 1223436.3028
45 | 2754860.7996 | 1223421.4798 | 2754855.5409 | 1223426.8119 | 2754847.1229 | 1223426.944
46 | 2754821.9276 | 1223436.3028 | 2754816.3189 | 1223448.1114 | 2754813.9526 | 1223448.4404
47 | 2754860.7996 | 1223421.4798 | 2754873.1 | 1223409.0079 | 2754878.8321 | 1223394.9371
48 | 2754813.9526 | 1223448.4404 | 2754804.0581 | 1223449.8164 | 2754799.7534 | 1223446.2335
49 | 2754878.8321 | 1223394.9371 | 2754888.0385 | 1223372.3381
50 | 2754889.62 | 1223368.4561 | 2754889.62 | 1223368.4561 | 2754888.0385 | 1223372.3381
51 | 2754910.2241 | 1223382.5152 | 2754907.7235 | 1223406.7768
52 | 2754906.9012 | 1223414.7558 | 2754907.7235 | 1223406.7768
53 | 2754906.9012 | 1223414.7558 | 2754905.2548 | 1223430.7291
54 | 2754905.2548 | 1223430.7291 | 2754903.9075 | 1223443.8012
55 | 2754901.7702 | 1223464.5379 | 2754903.9075 | 1223443.8012
56 | 2754901.7702 | 1223464.5379 | 2754861.2791 | 1223490.269
57 | 2754901.7702 | 1223464.5379 | 2754903.217 | 1223489.1245
58 | 2754853.5676 | 1223495.1694 | 2754861.2791 | 1223490.269
59 | 2754903.217 | 1223489.1245 | 2754904.8789 | 1223517.3671 | 2754899.7814 | 1223530.2532
60 | 2754850.8637 | 1223496.8877 | 2754853.5676 | 1223495.1694
61 | 2754891.3713 | 1223551.5136 | 2754899.7814 | 1223530.2532
62 | 2754902.2565 | 1223562.7071 | 2754891.3713 | 1223551.5136 | 2754891.3713 | 1223551.5136
63 | 2754902.2565 | 1223562.7071 | 2754898.4912 | 1223565.6896 | 2754891.2145 | 1223578.6239
64 | 2754902.2565 | 1223562.7071 | 2754907.8079 | 1223559.0259 | 2754916.7825 | 1223558.3305
65 | 2754955.9655 | 1223561.4146 | 2754955.7735 | 1223559.4634 | 2754955.6254 | 1223556.4123 | 2754959.8843 | 1223535.7847
66 | 2754955.9655 | 1223561.4146 | 2754926.2833 | 1223557.5942 | 2754917.3292 | 1223558.2881
67 | 2754955.9655 | 1223561.4146 | 2754963.5195 | 1223565.6432
68 | 2754916.7825 | 1223558.3305 | 2754917.3292 | 1223558.2881
69 | 2754965.4931 | 1223566.748 | 2754963.5195 | 1223565.6432
70 | 2754969.1495 | 1223568.6065 | 2754967.4676 | 1223567.8532 | 2754965.4931 | 1223566.748
71 | 2754886.6209 | 1223586.789 | 2754891.2145 | 1223578.6239
72 | 2754886.6209 | 1223586.789 | 2754897.6084 | 1223599.4698
73 | 2754886.6209 | 1223586.789 | 2754883.1962 | 1223592.8697
74 | 2754867.5436 | 1223610.2552 | 2754870.0841 | 1223607.6526
75 | 2754867.5436 | 1223610.2552 | 2754861.3363 | 1223616.6141 | 2754857.7557 | 1223620.6614
76 | 2754883.1962 | 1223592.8697 | 2754882.1022 | 1223594.8121 | 2754875.8828 | 1223601.7122 | 2754870.0841 | 1223607.6526
77 | 2754857.7557 | 1223620.6614 | 2754855.8639 | 1223622.7997 | 2754851.4983 | 1223631.939 | 2754852.2171 | 1223638.4303 | 2754852.4379 | 1223638.8356
78 | 2754859.5251 | 1223652.3526 | 2754859.5311 | 1223651.855 | 2754852.4379 | 1223638.8356
79 | 2754859.5251 | 1223652.3526 | 2754859.3705 | 1223665.1817
80 | 2754899.8514 | 1223602.0586 | 2754897.6084 | 1223599.4698
81 | 2754899.8514 | 1223602.0586 | 2754911.9564 | 1223616.0292
82 | 2755034.2903 | 1223500.6869 | 2755030.8351 | 1223500.1025
83 | 2754969.1495 | 1223568.6065 | 2754985.528 | 1223575.9419 | 2754993.9519 | 1223578.1237
84 | 2754998.9436 | 1223579.4165 | 2754993.9519 | 1223578.1237
85 | 2754998.9436 | 1223579.4165 | 2755018.3369 | 1223582.4393
86 | 2754998.9436 | 1223579.4165 | 2754994.9425 | 1223588.2427 | 2754979.9646 | 1223600.9603
87 | 2755018.3369 | 1223582.4393 | 2755022.4709 | 1223583.0836
88 | 2754968.9054 | 1223615.6149 | 2754974.4084 | 1223611.029 | 2754976.6305 | 1223603.7913 | 2754979.9646 | 1223600.9603
89 | 2755040.1103 | 1223585.6497 | 2755026.6172 | 1223583.7299 | 2755022.4709 | 1223583.0836
90 | 2754968.9054 | 1223615.6149 | 2754965.9975 | 1223618.0382
91 | 2755040.1103 | 1223585.6497 | 2755062.2155 | 1223588.7949 | 2755063.2063 | 1223588.9322
92 | 2755087.6673 | 1223591.894 | 2755083.2507 | 1223591.6232 | 2755073.9795 | 1223590.425 | 2755063.2063 | 1223588.9322
93 | 2755087.6673 | 1223591.894 | 2755101.5603 | 1223592.1674
94 | 2755087.6673 | 1223591.894 | 2755078.0378 | 1223606.0525
95 | 2755111.0376 | 1223591.704 | 2755105.0569 | 1223592.2362 | 2755101.5603 | 1223592.1674
96 | 2755068.4904 | 1223620.0902 | 2755078.0378 | 1223606.0525
97 | 2755111.0376 | 1223591.704 | 2755131.4002 | 1223589.8922
98 | 2755037.7973 | 1223647.7296 | 2755043.8097 | 1223644.0328 | 2755067.3108 | 1223621.8245 | 2755068.4904 | 1223620.0902
99 | 2755131.4002 | 1223589.8922 | 2755135.3108 | 1223589.5442 | 2755142.8725 | 1223591.3481
100 | 2755145.0135 | 1223591.8588 | 2755142.8725 | 1223591.3481
101 | 2755145.0135 | 1223591.8588 | 2755154.0496 | 1223594.0144 | 2755169.2883 | 1223602.752
102 | 2755183.0628 | 1223610.6501 | 2755169.2883 | 1223602.752
103 | 2754879.6568 | 1223692.5158 | 2754859.1649 | 1223682.24 | 2754859.3705 | 1223665.1817
104 | 2754913.2556 | 1223617.5286 | 2754911.9564 | 1223616.0292
105 | 2754913.2556 | 1223617.5286 | 2754927.4935 | 1223633.9608
106 | 2754927.6807 | 1223634.1769 | 2754927.4935 | 1223633.9608
107 | 2754947.6018 | 1223652.4964 | 2754949.1451 | 1223655.0226
108 | 2754947.6018 | 1223652.4964 | 2754945.0444 | 1223648.31 | 2754945.7794 | 1223639.61 | 2754950.7914 | 1223630.7101 | 2754962.9743 | 1223620.5576
109 | 2754965.9975 | 1223618.0382 | 2754962.9743 | 1223620.5576
110 | 2755212.4085 | 1223620.1039 | 2755184.8351 | 1223611.6663 | 2755183.0628 | 1223610.6501
111 | 2755212.4085 | 1223620.1039 | 2755210.443 | 1223636.6901
112 | 2755210.443 | 1223636.6901 | 2755232.2522 | 1223632.8846
113 | 2755232.2522 | 1223632.8846 | 2755269.2621 | 1223626.4269

## bus_geodata
| x | y | coords
0 | 2755259.2901 | 1223178.5305
1 | 2755272.4364 | 1223243.0548
2 | 2755272.5395 | 1223267.1915
3 | 2755480.2125 | 1223170.2911
4 | 2755271.9987 | 1223300.841
5 | 2754977.7987 | 1223262.4718
6 | 2754979.5455 | 1223283.7162
7 | 2755270.4387 | 1223339.517
8 | 2755269.6137 | 1223357.9294
9 | 2755270.7465 | 1223332.646
10 | 2755268.7579 | 1223377.0299
11 | 2755265.8245 | 1223419.0145
12 | 2755259.1849 | 1223453.9184
13 | 2755245.6931 | 1223488.864
14 | 2755235.5803 | 1223516.9303
15 | 2755235.9796 | 1223515.6668
16 | 2755223.2467 | 1223556.9738
17 | 2755238.8598 | 1223506.5534
18 | 2755219.087 | 1223581.2033
19 | 2755241.32 | 1223498.7686
20 | 2755218.0507 | 1223587.2395
21 | 2755283.359 | 1223490.725
22 | 2755296.5524 | 1223457.2472
23 | 2755276.4789 | 1223508.183
24 | 2754904.664 | 1223366.4806
25 | 2754969.3972 | 1223489.7097
26 | 2754965.5941 | 1223508.1295
27 | 2754987.1188 | 1223492.7074
28 | 2754964.8218 | 1223511.8702
29 | 2755014.4687 | 1223497.3339
30 | 2754640.7236 | 1223532.4293
31 | 2754656.8796 | 1223475.982
32 | 2754657.7652 | 1223462.2819
33 | 2754795.5564 | 1223436.4143
34 | 2754800.12 | 1223363.2504
35 | 2754811.6746 | 1223344.9184
36 | 2754800.0296 | 1223363.5928
37 | 2754828.3953 | 1223356.9571
38 | 2754805.4643 | 1223348.2968
39 | 2754823.343 | 1223392.6881
40 | 2754800.5913 | 1223404.5201
41 | 2754826.2171 | 1223427.2719
42 | 2754847.1229 | 1223426.944
43 | 2754821.9276 | 1223436.3028
44 | 2754860.7996 | 1223421.4798
45 | 2754813.9526 | 1223448.4404
46 | 2754799.7534 | 1223446.2335
47 | 2754878.8321 | 1223394.9371
48 | 2754888.0385 | 1223372.3381
49 | 2754889.62 | 1223368.4561
50 | 2754910.2241 | 1223382.5152
51 | 2754907.7235 | 1223406.7768
52 | 2754906.9012 | 1223414.7558
53 | 2754905.2548 | 1223430.7291
54 | 2754903.9075 | 1223443.8012
55 | 2754901.7702 | 1223464.5379
56 | 2754861.2791 | 1223490.269
57 | 2754903.217 | 1223489.1245
58 | 2754853.5676 | 1223495.1694
59 | 2754899.7814 | 1223530.2532
60 | 2754850.8637 | 1223496.8877
61 | 2754891.3713 | 1223551.5136
62 | 2754902.2565 | 1223562.7071
63 | 2754959.8843 | 1223535.7847
64 | 2754955.9655 | 1223561.4146
65 | 2754917.3292 | 1223558.2881
66 | 2754963.5195 | 1223565.6432
67 | 2754916.7825 | 1223558.3305
68 | 2754965.4931 | 1223566.748
69 | 2754891.2145 | 1223578.6239
70 | 2754886.6209 | 1223586.789
71 | 2754867.5436 | 1223610.2552
72 | 2754870.0841 | 1223607.6526
73 | 2754857.7557 | 1223620.6614
74 | 2754883.1962 | 1223592.8697
75 | 2754852.4379 | 1223638.8356
76 | 2754859.5251 | 1223652.3526
77 | 2754897.6084 | 1223599.4698
78 | 2754899.8514 | 1223602.0586
79 | 2755030.8351 | 1223500.1025
80 | 2755034.2903 | 1223500.6869
81 | 2754969.1495 | 1223568.6065
82 | 2754993.9519 | 1223578.1237
83 | 2754998.9436 | 1223579.4165
84 | 2755018.3369 | 1223582.4393
85 | 2754979.9646 | 1223600.9603
86 | 2755022.4709 | 1223583.0836
87 | 2754968.9054 | 1223615.6149
88 | 2755040.1103 | 1223585.6497
89 | 2755063.2063 | 1223588.9322
90 | 2755087.6673 | 1223591.894
91 | 2755101.5603 | 1223592.1674
92 | 2755078.0378 | 1223606.0525
93 | 2755111.0376 | 1223591.704
94 | 2755068.4904 | 1223620.0902
95 | 2755131.4002 | 1223589.8922
96 | 2755142.8725 | 1223591.3481
97 | 2755145.0135 | 1223591.8588
98 | 2755169.2883 | 1223602.752
99 | 2754879.6568 | 1223692.5158
100 | 2754859.3705 | 1223665.1817
101 | 2754911.9564 | 1223616.0292
102 | 2754913.2556 | 1223617.5286
103 | 2754927.4935 | 1223633.9608
104 | 2754927.6807 | 1223634.1769
105 | 2754947.6018 | 1223652.4964
106 | 2754949.1451 | 1223655.0226
107 | 2754962.9743 | 1223620.5576
108 | 2754965.9975 | 1223618.0382
109 | 2755037.7973 | 1223647.7296
110 | 2755183.0628 | 1223610.6501
111 | 2755212.4085 | 1223620.1039
112 | 2755210.443 | 1223636.6901
113 | 2755232.2522 | 1223632.8846
114 | 2755269.2621 | 1223626.4269
115 | 2754969.3972 | 1223489.7097

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1