## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5207-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5207-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5207-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5207-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5207-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5207-4_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_5207-4_0_3_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_5207-4_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_5207-4_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_5207-4_0_3_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_5207-4_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_5207-4_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_5207-4_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_5207-4_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_5207-4_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_5207-4_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_5207-4_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_5207-4_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_5207-4_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_5207-4_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_5207-4_0_3_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_5207-4_0_3_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_5207-4_0_3_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_5207-4_0_3_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_5207-4_0_3_node_61 | 0.4 | n |  | TRUE
25 | bus_LV_5207-4_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_5207-4_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_5207-4_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_5207-4_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_5207-4_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_5207-4_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_5207-4_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_5207-4_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_5207-4_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_5207-4_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_5207-4_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_5207-4_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_5207-4_0_3_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_5207-4_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_5207-4_0_3_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_5207-4_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_5207-4_0_3_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_5207-4_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_5207-4_0_3_node_123 | 0.4 | n |  | TRUE
44 | bus_LV_5207-4_0_3_node_120 | 0.4 | n |  | TRUE
45 | bus_LV_5207-4_0_3_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_5207-4_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_5207-4_0_3_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_5207-4_0_3_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_5207-4_0_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_5207-4_0_3_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_5207-4_0_3_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_5207-4_0_3_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_5207-4_0_3_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_5207-4_0_3_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_5207-4_0_3_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_5207-4_0_3_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_5207-4_0_3_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_5207-4_0_3_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_5207-4_0_3_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_5207-4_0_3_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_5207-4_0_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_5207-4_0_3_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_5207-4_0_3_node_129 | 0.4 | n |  | TRUE
64 | bus_LV_5207-4_0_3_node_121 | 0.4 | n |  | TRUE
65 | bus_LV_5207-4_0_3_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_5207-4_0_3_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_5207-4_0_3_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_5207-4_0_3_node_89 | 0.4 | n |  | TRUE
69 | bus_LV_5207-4_0_3_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_5207-4_0_3_node_88 | 0.4 | n |  | TRUE
71 | bus_LV_5207-4_0_3_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_5207-4_0_3_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_5207-4_0_3_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_5207-4_0_3_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_5207-4_0_3_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_5207-4_0_3_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_5207-4_0_3_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_5207-4_0_3_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_5207-4_0_3_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_5207-4_0_3_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_5207-4_0_3_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_5207-4_0_3_node_104 | 0.4 | n |  | TRUE
83 | bus_LV_5207-4_0_3_node_105 | 0.4 | n |  | TRUE
84 | bus_LV_5207-4_0_3_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_5207-4_0_3_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_5207-4_0_3_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_5207-4_0_3_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_5207-4_0_3_node_81 | 0.4 | n |  | TRUE
89 | bus_LV_5207-4_0_3_node_108 | 0.4 | n |  | TRUE
90 | bus_LV_5207-4_0_3_node_107 | 0.4 | n |  | TRUE
91 | bus_LV_5207-4_0_3_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_5207-4_0_3_node_106 | 0.4 | n |  | TRUE
93 | bus_LV_5207-4_0_3_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_5207-4_0_3_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_5207-4_0_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_5207-4_0_3_node_92 | 0.4 | n |  | TRUE
97 | bus_LV_5207-4_0_3_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_5207-4_0_3_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_5207-4_0_3_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_5207-4_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_5207-4_0_3_node_109 | 0.4 | n |  | TRUE
102 | bus_LV_5207-4_0_3_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_5207-4_0_3_node_111 | 0.4 | n |  | TRUE
104 | bus_LV_5207-4_0_3_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_5207-4_0_3_node_110 | 0.4 | n |  | TRUE
106 | bus_LV_5207-4_0_3_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_5207-4_0_3_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_5207-4_0_3_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_5207-4_0_3_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_5207-4_0_3_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_5207-4_0_3_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_5207-4_0_3_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_5207-4_0_3_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_5207-4_0_3_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_5207-4_0_3_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_5207-4_0_3_node_134 | 0.4 | n |  | TRUE
117 | bus_LV_5207-4_0_3_node_132 | 0.4 | n |  | TRUE
118 | bus_LV_5207-4_0_3_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_5207-4_0_3_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_5207-4_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_5207-4_0_3_node_117 | 0.4 | n |  | TRUE
122 | bus_LV_5207-4_0_3_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_5207-4_0_3_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_5207-4_0_3_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_5207-4_0_3_node_122 | 0.4 | n |  | TRUE
126 | bus_LV_5207-4_0_3_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_5207-4_0_3_node_124 | 0.4 | n |  | TRUE
128 | bus_LV_5207-4_0_3_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_5207-4_0_3_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_5207-4_0_3_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_5207-4_0_3_node_140 | 0.4 | n |  | TRUE
132 | bus_LV_5207-4_0_3_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_5207-4_0_3_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_5207-4_0_3_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_5207-4_0_3_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_5207-4_0_3_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_5207-4_0_3_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_5207-4_0_3_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_5207-4_0_3_node_141 | 0.4 | n |  | TRUE
140 | bus_LV_5207-4_0_3_node_142 | 0.4 | n |  | TRUE
141 | bus_MV_69_0_node_169 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5207-4_0_3_load_0 | 0 | 0.0062173 | 0.0015582 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5207-4_0_3_load_2 | 2 | 0.0038495 | 0.00096479 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5207-4_0_3_load_3 | 3 | 0.0034502 | 0.0008647 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5207-4_0_3_load_7 | 5 | 0.0045774 | 0.0011472 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5207-4_0_3_load_18 | 7 | 0.0037999 | 0.00095235 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5207-4_0_3_load_5 | 8 | 0.0059716 | 0.0014966 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5207-4_0_3_load_47 | 9 | 0.0016589 | 0.00041576 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5207-4_0_3_load_16 | 10 | 0.0038704 | 0.00097003 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5207-4_0_3_load_6 | 11 | 0.0048476 | 0.0012149 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5207-4_0_3_load_13 | 13 | 0.0034578 | 0.00086661 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5207-4_0_3_load_9 | 15 | 0.0037371 | 0.00093661 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5207-4_0_3_load_14 | 18 | 0.0031955 | 0.00080087 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5207-4_0_3_load_15 | 19 | 0.012697 | 0.0031822 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5207-4_0_3_load_34 | 20 | 0.025031 | 0.0062734 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5207-4_0_3_load_32 | 21 | 0.0015644 | 0.00039207 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5207-4_0_3_load_60 | 22 | 0.008598 | 0.0021548 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5207-4_0_3_load_30 | 23 | 0.001624 | 0.00040702 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5207-4_0_3_load_17 | 25 | 0.0021402 | 0.00053638 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5207-4_0_3_load_19 | 26 | 0.0030048 | 0.00075308 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5207-4_0_3_load_20 | 27 | 0.0023294 | 0.00058381 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5207-4_0_3_load_21 | 28 | 0.0022451 | 0.00056269 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5207-4_0_3_load_22 | 29 | 0.0017633 | 0.00044193 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5207-4_0_3_load_23 | 30 | 0.0019944 | 0.00049984 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5207-4_0_3_load_24 | 31 | 0.0030464 | 0.00076349 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5207-4_0_3_load_25 | 32 | 0.0018493 | 0.00046348 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5207-4_0_3_load_26 | 33 | 0.0037814 | 0.00094772 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5207-4_0_3_load_27 | 34 | 0.0069729 | 0.0017476 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5207-4_0_3_load_28 | 35 | 0.0048788 | 0.0012227 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5207-4_0_3_load_35 | 36 | 0.0028341 | 0.00071029 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5207-4_0_3_load_36 | 37 | 0.00692 | 0.0017343 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5207-4_0_3_load_29 | 38 | 0.0014085 | 0.000353 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5207-4_0_3_load_31 | 39 | 0.004844 | 0.001214 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5207-4_0_3_load_33 | 40 | 0.0032723 | 0.00082011 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5207-4_0_3_load_45 | 42 | 0.0051763 | 0.0012973 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5207-4_0_3_load_123 | 43 | 0.0025752 | 0.0006454 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5207-4_0_3_load_120 | 44 | 0.0031996 | 0.0008019 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5207-4_0_3_load_37 | 46 | 0.0066358 | 0.0016631 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5207-4_0_3_load_38 | 47 | 0.0056821 | 0.0014241 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5207-4_0_3_load_40 | 49 | 0.0017776 | 0.00044551 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5207-4_0_3_load_41 | 50 | 0.0039202 | 0.0009825 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5207-4_0_3_load_42 | 51 | 0.0052611 | 0.0013185 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5207-4_0_3_load_53 | 52 | 0.0022421 | 0.00056191 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5207-4_0_3_load_58 | 53 | 0.0019008 | 0.00047639 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5207-4_0_3_load_44 | 54 | 0.0016371 | 0.00041031 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5207-4_0_3_load_57 | 56 | 0.0024877 | 0.00062347 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5207-4_0_3_load_48 | 57 | 0.0020914 | 0.00052416 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5207-4_0_3_load_49 | 58 | 0.0011759 | 0.00029471 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5207-4_0_3_load_50 | 59 | 0.005024 | 0.0012591 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5207-4_0_3_load_51 | 60 | 0.0050306 | 0.0012608 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5207-4_0_3_load_54 | 61 | 0.001233 | 0.00030901 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5207-4_0_3_load_55 | 62 | 0.0017913 | 0.00044895 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5207-4_0_3_load_129 | 63 | 0.0033024 | 0.00082767 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5207-4_0_3_load_121 | 64 | 0.0031394 | 0.00078682 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5207-4_0_3_load_62 | 65 | 0.0016898 | 0.00042351 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5207-4_0_3_load_63 | 66 | 0.0011727 | 0.00029391 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5207-4_0_3_load_64 | 67 | 0.0016047 | 0.00040217 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5207-4_0_3_load_89 | 68 | 0.00285 | 0.00071427 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5207-4_0_3_load_65 | 69 | 0.0030564 | 0.000766 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5207-4_0_3_load_66 | 71 | 0.0018527 | 0.00046433 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5207-4_0_3_load_68 | 73 | 0.00091064 | 0.00022823 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5207-4_0_3_load_70 | 75 | 0.002613 | 0.00065488 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5207-4_0_3_load_75 | 76 | 0.0010764 | 0.00026976 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5207-4_0_3_load_74 | 77 | 0.0015804 | 0.0003961 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5207-4_0_3_load_71 | 78 | 0.0017759 | 0.00044509 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5207-4_0_3_load_76 | 79 | 0.003149 | 0.00078921 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5207-4_0_3_load_72 | 80 | 0.0017655 | 0.00044249 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5207-4_0_3_load_73 | 81 | 0.0045897 | 0.0011503 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5207-4_0_3_load_104 | 82 | 0.0024377 | 0.00061095 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5207-4_0_3_load_105 | 83 | 0.0035604 | 0.00089231 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5207-4_0_3_load_77 | 84 | 0.0020704 | 0.00051888 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5207-4_0_3_load_79 | 86 | 0.0047776 | 0.0011974 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5207-4_0_3_load_81 | 88 | 0.0035655 | 0.00089359 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5207-4_0_3_load_108 | 89 | 0.0040648 | 0.0010187 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5207-4_0_3_load_107 | 90 | 0.0030686 | 0.00076906 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5207-4_0_3_load_106 | 92 | 0.0031597 | 0.00079188 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5207-4_0_3_load_83 | 93 | 0.0019577 | 0.00049064 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5207-4_0_3_load_84 | 94 | 0.0039617 | 0.00099289 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5207-4_0_3_load_91 | 95 | 0.0055405 | 0.0013886 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5207-4_0_3_load_92 | 96 | 0.0072875 | 0.0018264 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5207-4_0_3_load_85 | 97 | 0.0039166 | 0.0009816 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5207-4_0_3_load_86 | 98 | 0.0018472 | 0.00046295 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5207-4_0_3_load_87 | 99 | 0.0033764 | 0.0008462 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5207-4_0_3_load_109 | 101 | 0.0057395 | 0.0014385 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5207-4_0_3_load_111 | 103 | 0.0021468 | 0.00053805 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5207-4_0_3_load_98 | 104 | 0.0044557 | 0.0011167 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5207-4_0_3_load_110 | 105 | 0.0020518 | 0.00051423 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5207-4_0_3_load_93 | 106 | 0.0061766 | 0.001548 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5207-4_0_3_load_94 | 107 | 0.0031803 | 0.00079705 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5207-4_0_3_load_95 | 108 | 0.0015401 | 0.000386 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5207-4_0_3_load_96 | 109 | 0.00376 | 0.00094233 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5207-4_0_3_load_97 | 110 | 0.0041447 | 0.0010388 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5207-4_0_3_load_101 | 112 | 0.0032347 | 0.0008107 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5207-4_0_3_load_112 | 114 | 0.0022257 | 0.00055782 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5207-4_0_3_load_103 | 115 | 0.0043679 | 0.0010947 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5207-4_0_3_load_134 | 116 | 0.0064381 | 0.0016136 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5207-4_0_3_load_132 | 117 | 0.0019891 | 0.00049851 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5207-4_0_3_load_113 | 118 | 0.0027642 | 0.00069277 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5207-4_0_3_load_114 | 119 | 0.0039812 | 0.00099779 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5207-4_0_3_load_119 | 120 | 0.0045776 | 0.0011472 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5207-4_0_3_load_117 | 121 | 0.0030435 | 0.00076276 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5207-4_0_3_load_115 | 122 | 0.0023133 | 0.00057976 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5207-4_0_3_load_116 | 123 | 0.0012369 | 0.00030999 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5207-4_0_3_load_118 | 124 | 0.0013866 | 0.00034752 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5207-4_0_3_load_122 | 125 | 0.0022613 | 0.00056672 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5207-4_0_3_load_124 | 127 | 0.0035451 | 0.00088847 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5207-4_0_3_load_125 | 128 | 0.0023639 | 0.00059244 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5207-4_0_3_load_127 | 129 | 0.0055339 | 0.0013869 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5207-4_0_3_load_128 | 130 | 0.002999 | 0.00075163 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5207-4_0_3_load_140 | 131 | 0.0030513 | 0.00076474 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5207-4_0_3_load_130 | 133 | 0.0035434 | 0.00088805 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5207-4_0_3_load_131 | 134 | 0.0021222 | 0.00053186 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5207-4_0_3_load_133 | 135 | 0.002757 | 0.00069097 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5207-4_0_3_load_135 | 136 | 0.012107 | 0.0030344 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5207-4_0_3_load_136 | 137 | 0.014053 | 0.0035221 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5207-4_0_3_load_141 | 139 | 0.002924 | 0.00073283 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5207-4_0_3_load_142 | 140 | 0.003596 | 0.00090125 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5207-4_0_3_line_0 |  | 0 | 1 | 0.029172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5207-4_0_3_line_1 |  | 0 | 2 | 0.0019655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5207-4_0_3_line_2 |  | 1 | 3 | 0.010549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5207-4_0_3_line_3 |  | 1 | 4 | 0.007967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5207-4_0_3_line_4 |  | 3 | 5 | 0.015726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5207-4_0_3_line_5 |  | 4 | 6 | 0.057722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5207-4_0_3_line_6 |  | 4 | 7 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5207-4_0_3_line_7 |  | 5 | 8 | 0.0069908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5207-4_0_3_line_8 |  | 6 | 9 | 0.055042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5207-4_0_3_line_9 |  | 7 | 10 | 0.0068015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5207-4_0_3_line_10 |  | 8 | 11 | 0.0097974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5207-4_0_3_line_11 |  | 9 | 57 | 0.0068123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5207-4_0_3_line_12 |  | 10 | 25 | 0.010035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5207-4_0_3_line_13 |  | 11 | 12 | 0.01718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5207-4_0_3_line_14 |  | 12 | 13 | 0.0021317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5207-4_0_3_line_15 |  | 13 | 14 | 0.019715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5207-4_0_3_line_16 |  | 14 | 17 | 0.005718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_5207-4_0_3_line_17 |  | 14 | 15 | 0.052667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_5207-4_0_3_line_18 |  | 15 | 16 | 0.050422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_5207-4_0_3_line_19 |  | 16 | 18 | 0.047127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_5207-4_0_3_line_20 |  | 16 | 19 | 0.018395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5207-4_0_3_line_21 |  | 17 | 20 | 0.062566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_5207-4_0_3_line_22 |  | 17 | 21 | 0.030141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5207-4_0_3_line_23 |  | 18 | 22 | 0.0048637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5207-4_0_3_line_24 |  | 21 | 23 | 0.018664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5207-4_0_3_line_25 |  | 22 | 24 | 0.026049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5207-4_0_3_line_26 |  | 23 | 38 | 0.023313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_5207-4_0_3_line_27 |  | 24 | 65 | 0.010345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5207-4_0_3_line_28 |  | 24 | 66 | 0.057025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5207-4_0_3_line_29 |  | 25 | 26 | 0.0052955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5207-4_0_3_line_30 |  | 26 | 27 | 0.0038154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5207-4_0_3_line_31 |  | 27 | 28 | 0.0054648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5207-4_0_3_line_32 |  | 28 | 29 | 0.0087288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5207-4_0_3_line_33 |  | 29 | 30 | 0.0070053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5207-4_0_3_line_34 |  | 30 | 31 | 0.0079316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5207-4_0_3_line_35 |  | 31 | 32 | 0.0094995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5207-4_0_3_line_36 |  | 32 | 33 | 0.0043274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5207-4_0_3_line_37 |  | 33 | 34 | 0.0094942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5207-4_0_3_line_38 |  | 34 | 35 | 0.0087477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5207-4_0_3_line_39 |  | 35 | 36 | 0.010932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5207-4_0_3_line_40 |  | 36 | 37 | 0.0075817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5207-4_0_3_line_41 |  | 38 | 39 | 0.061839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_5207-4_0_3_line_42 |  | 39 | 40 | 0.024415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_5207-4_0_3_line_43 |  | 40 | 41 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_5207-4_0_3_line_44 |  | 40 | 42 | 0.046594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5207-4_0_3_line_45 |  | 41 | 43 | 0.029357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5207-4_0_3_line_46 |  | 41 | 44 | 0.040634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_5207-4_0_3_line_47 |  | 42 | 45 | 0.017806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5207-4_0_3_line_48 |  | 43 | 63 | 0.015338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5207-4_0_3_line_49 |  | 44 | 64 | 0.005222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_5207-4_0_3_line_50 |  | 45 | 54 | 0.041091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5207-4_0_3_line_51 |  | 45 | 49 | 0.022234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5207-4_0_3_line_52 |  | 46 | 47 | 0.0039982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5207-4_0_3_line_53 |  | 46 | 48 | 0.01327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5207-4_0_3_line_54 |  | 47 | 49 | 0.0092755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5207-4_0_3_line_55 |  | 48 | 50 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5207-4_0_3_line_56 |  | 48 | 51 | 0.01253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5207-4_0_3_line_57 |  | 50 | 52 | 0.066183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5207-4_0_3_line_58 |  | 51 | 53 | 0.015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5207-4_0_3_line_59 |  | 52 | 55 | 0.038629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5207-4_0_3_line_60 |  | 53 | 56 | 0.0015143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5207-4_0_3_line_61 |  | 55 | 60 | 0.048875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5207-4_0_3_line_62 |  | 56 | 62 | 0.022138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5207-4_0_3_line_63 |  | 57 | 58 | 0.0029457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5207-4_0_3_line_64 |  | 58 | 59 | 0.032156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5207-4_0_3_line_65 |  | 61 | 62 | 0.022027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5207-4_0_3_line_66 |  | 63 | 126 | 0.010656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5207-4_0_3_line_67 |  | 64 | 125 | 0.022131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_5207-4_0_3_line_68 |  | 65 | 67 | 0.009003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5207-4_0_3_line_69 |  | 66 | 68 | 0.014294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5207-4_0_3_line_70 |  | 67 | 69 | 0.0055305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5207-4_0_3_line_71 |  | 68 | 70 | 0.015454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5207-4_0_3_line_72 |  | 69 | 71 | 0.0076043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5207-4_0_3_line_73 |  | 70 | 100 | 0.011452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5207-4_0_3_line_74 |  | 70 | 98 | 0.028738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5207-4_0_3_line_75 |  | 71 | 72 | 0.029191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5207-4_0_3_line_76 |  | 72 | 73 | 0.044472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5207-4_0_3_line_77 |  | 72 | 74 | 0.040201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5207-4_0_3_line_78 |  | 73 | 75 | 0.070425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5207-4_0_3_line_79 |  | 74 | 76 | 0.0096551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5207-4_0_3_line_80 |  | 74 | 77 | 0.023443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5207-4_0_3_line_81 |  | 75 | 78 | 0.0094072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5207-4_0_3_line_82 |  | 76 | 79 | 0.021881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5207-4_0_3_line_83 |  | 78 | 80 | 0.10279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5207-4_0_3_line_84 |  | 79 | 84 | 0.02858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5207-4_0_3_line_85 |  | 80 | 81 | 0.021399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5207-4_0_3_line_86 |  | 81 | 82 | 0.14563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5207-4_0_3_line_87 |  | 82 | 83 | 0.037279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5207-4_0_3_line_88 |  | 84 | 85 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5207-4_0_3_line_89 |  | 85 | 86 | 0.017381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5207-4_0_3_line_90 |  | 85 | 87 | 0.025984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5207-4_0_3_line_91 |  | 86 | 88 | 0.032715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5207-4_0_3_line_92 |  | 87 | 89 | 0.013271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5207-4_0_3_line_93 |  | 87 | 90 | 0.0015554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5207-4_0_3_line_94 |  | 88 | 91 | 0.01303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5207-4_0_3_line_95 |  | 90 | 92 | 0.020472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5207-4_0_3_line_96 |  | 91 | 93 | 0.0094872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5207-4_0_3_line_97 |  | 91 | 94 | 0.048292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5207-4_0_3_line_98 |  | 93 | 95 | 0.019194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5207-4_0_3_line_99 |  | 95 | 96 | 0.0091388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5207-4_0_3_line_100 |  | 97 | 98 | 0.028249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5207-4_0_3_line_101 |  | 97 | 99 | 0.0061783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5207-4_0_3_line_102 |  | 100 | 101 | 0.024984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5207-4_0_3_line_103 |  | 101 | 105 | 0.0038529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5207-4_0_3_line_104 |  | 102 | 103 | 0.022925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5207-4_0_3_line_105 |  | 102 | 104 | 0.024353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5207-4_0_3_line_106 |  | 103 | 114 | 0.0041653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5207-4_0_3_line_107 |  | 104 | 109 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5207-4_0_3_line_108 |  | 106 | 107 | 0.013432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5207-4_0_3_line_109 |  | 106 | 108 | 0.00022833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5207-4_0_3_line_110 |  | 107 | 109 | 0.011009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_5207-4_0_3_line_111 |  | 108 | 110 | 0.02813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5207-4_0_3_line_112 |  | 110 | 111 | 0.0245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5207-4_0_3_line_113 |  | 111 | 112 | 0.034606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5207-4_0_3_line_114 |  | 111 | 113 | 0.015484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5207-4_0_3_line_115 |  | 112 | 115 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5207-4_0_3_line_116 |  | 113 | 116 | 0.028396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5207-4_0_3_line_117 |  | 114 | 118 | 0.010961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5207-4_0_3_line_118 |  | 116 | 117 | 0.018392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5207-4_0_3_line_119 |  | 117 | 133 | 0.010582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5207-4_0_3_line_120 |  | 118 | 119 | 0.0049402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5207-4_0_3_line_121 |  | 119 | 120 | 0.0043857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5207-4_0_3_line_122 |  | 120 | 121 | 0.0030703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_5207-4_0_3_line_123 |  | 121 | 122 | 0.020042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_5207-4_0_3_line_124 |  | 122 | 123 | 0.0015735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5207-4_0_3_line_125 |  | 123 | 124 | 0.012794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_5207-4_0_3_line_126 |  | 124 | 125 | 0.0073767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_5207-4_0_3_line_127 |  | 126 | 130 | 0.024145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5207-4_0_3_line_128 |  | 126 | 127 | 0.019769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_5207-4_0_3_line_129 |  | 127 | 128 | 0.03544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_5207-4_0_3_line_130 |  | 128 | 129 | 0.0066951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_5207-4_0_3_line_131 |  | 130 | 131 | 0.029427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_5207-4_0_3_line_132 |  | 131 | 132 | 0.028588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_5207-4_0_3_line_133 |  | 132 | 139 | 0.049841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_5207-4_0_3_line_134 |  | 132 | 138 | 0.036992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_5207-4_0_3_line_135 |  | 133 | 134 | 0.0067851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_5207-4_0_3_line_136 |  | 134 | 135 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_5207-4_0_3_line_137 |  | 136 | 137 | 0.017469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_5207-4_0_3_line_138 |  | 137 | 138 | 0.01311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_5207-4_0_3_line_139 |  | 139 | 140 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5207-4_0_3_trafo_34 | 0.63 MVA 20/0.4 kV | 141 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2709827.614 | 1096264.7027 | 2709847.7223 | 1096285.8371
1 | 2709849.0771 | 1096287.2611 | 2709847.7223 | 1096285.8371
2 | 2709827.614 | 1096264.7027 | 2709836.5389 | 1096259.0799
3 | 2709820.7986 | 1096268.8602 | 2709827.614 | 1096264.7027
4 | 2709849.8441 | 1096250.6975 | 2709836.5389 | 1096259.0799
5 | 2709773.152 | 1096301.4436 | 2709801.1877 | 1096282.2704 | 2709820.7986 | 1096268.8602
6 | 2709820.7986 | 1096268.8602 | 2709811.5447 | 1096254.5948
7 | 2709855.7589 | 1096246.9711 | 2709849.8441 | 1096250.6975
8 | 2709773.152 | 1096301.4436 | 2709771.0498 | 1096290.4428 | 2709743.8663 | 1096256.0453
9 | 2709811.5447 | 1096254.5948 | 2709807.8432 | 1096248.8887
10 | 2709855.7589 | 1096246.9711 | 2709864.0484 | 1096241.7487
11 | 2709743.8663 | 1096256.0453 | 2709739.6425 | 1096250.7005
12 | 2709802.3819 | 1096240.4698 | 2709807.8432 | 1096248.8887
13 | 2709878.584 | 1096232.5912 | 2709864.0484 | 1096241.7487
14 | 2709878.584 | 1096232.5912 | 2709880.3879 | 1096231.4553
15 | 2709897.0708 | 1096220.9509 | 2709880.3879 | 1096231.4553
16 | 2709897.0708 | 1096220.9509 | 2709893.8795 | 1096216.2011
17 | 2709897.0708 | 1096220.9509 | 2709925.0066 | 1096265.5983
18 | 2709951.7515 | 1096308.3423 | 2709925.0066 | 1096265.5983
19 | 2709951.7515 | 1096308.3423 | 2709991.4012 | 1096282.8693
20 | 2709951.7515 | 1096308.3423 | 2709936.263 | 1096318.267
21 | 2709893.8795 | 1096216.2011 | 2709935.9606 | 1096188.121 | 2709929.6077 | 1096177.8437
22 | 2709893.8795 | 1096216.2011 | 2709877.0659 | 1096191.1857
23 | 2709995.4931 | 1096280.2404 | 2709991.4012 | 1096282.8693
24 | 2709877.0659 | 1096191.1857 | 2709866.6543 | 1096175.6953
25 | 2710014.3308 | 1096262.3548 | 2710007.7492 | 1096269.8518 | 2709996.0706 | 1096279.8694 | 2709995.4931 | 1096280.2404
26 | 2709853.6495 | 1096156.3466 | 2709866.6543 | 1096175.6953
27 | 2710014.3308 | 1096262.3548 | 2710020.7952 | 1096263.895 | 2710024.4815 | 1096263.5764
28 | 2710014.3308 | 1096262.3548 | 2710022.7136 | 1096248.2304 | 2710027.074 | 1096234.1888 | 2710028.1321 | 1096221.1103 | 2710026.6828 | 1096208.4169
29 | 2709802.3819 | 1096240.4698 | 2709799.5001 | 1096236.0272
30 | 2709797.4237 | 1096232.8263 | 2709799.5001 | 1096236.0272
31 | 2709797.4237 | 1096232.8263 | 2709794.4496 | 1096228.2416
32 | 2709794.4496 | 1096228.2416 | 2709789.6993 | 1096220.9187
33 | 2709785.8869 | 1096215.0416 | 2709789.6993 | 1096220.9187
34 | 2709781.5703 | 1096208.3874 | 2709785.8869 | 1096215.0416
35 | 2709781.5703 | 1096208.3874 | 2709776.4005 | 1096200.4178
36 | 2709774.0455 | 1096196.7874 | 2709776.4005 | 1096200.4178
37 | 2709774.0455 | 1096196.7874 | 2709771.6316 | 1096193.0662 | 2709767.0126 | 1096191.0036 | 2709767.0126 | 1096191.0036
38 | 2709767.0126 | 1096191.0036 | 2709759.6725 | 1096195.7623
39 | 2709759.6725 | 1096195.7623 | 2709750.4992 | 1096201.7095
40 | 2709744.1374 | 1096205.8339 | 2709750.4992 | 1096201.7095
41 | 2709853.6495 | 1096156.3466 | 2709852.1356 | 1096154.0942 | 2709827.9828 | 1096117.4334 | 2709819.6103 | 1096104.7193
42 | 2709806.1828 | 1096084.3287 | 2709819.6103 | 1096104.7193
43 | 2709806.1828 | 1096084.3287 | 2709818.9909 | 1096074.8315
44 | 2709806.1828 | 1096084.3287 | 2709770.9892 | 1096114.8646
45 | 2709818.9909 | 1096074.8315 | 2709825.7718 | 1096067.449 | 2709840.1459 | 1096054.5204
46 | 2709818.9909 | 1096074.8315 | 2709825.2852 | 1096077.2245 | 2709858.9287 | 1096073.0642
47 | 2709757.5399 | 1096126.5341 | 2709770.9892 | 1096114.8646
48 | 2709840.1459 | 1096054.5204 | 2709851.5495 | 1096044.2636
49 | 2709858.9287 | 1096073.0642 | 2709864.1112 | 1096072.4233
50 | 2709757.5399 | 1096126.5341 | 2709798.2248 | 1096119.9754
51 | 2709757.5399 | 1096126.5341 | 2709750.7988 | 1096131.7158 | 2709739.3948 | 1096139.3643
52 | 2709728.3709 | 1096146.7579 | 2709731.6915 | 1096144.5309
53 | 2709717.3502 | 1096154.1493 | 2709728.3709 | 1096146.7579
54 | 2709739.3948 | 1096139.3643 | 2709731.6915 | 1096144.5309
55 | 2709717.3502 | 1096154.1493 | 2709702.2855 | 1096164.251
56 | 2709717.3502 | 1096154.1493 | 2709709.9787 | 1096145.7662 | 2709708.6662 | 1096145.3835
57 | 2709702.2855 | 1096164.251 | 2709647.3169 | 1096201.1104
58 | 2709693.9754 | 1096146.2685 | 2709702.7033 | 1096143.6447 | 2709708.6662 | 1096145.3835
59 | 2709633.9391 | 1096232.3411 | 2709632.1041 | 1096223.6912 | 2709632.2475 | 1096215.744 | 2709635.0236 | 1096209.1675 | 2709641.0745 | 1096205.2962 | 2709647.3169 | 1096201.1104
60 | 2709692.5252 | 1096146.7045 | 2709693.9754 | 1096146.2685
61 | 2709633.9391 | 1096232.3411 | 2709677.4547 | 1096210.0879
62 | 2709671.3248 | 1096153.0778 | 2709692.5252 | 1096146.7045
63 | 2709737.816 | 1096248.3894 | 2709739.6425 | 1096250.7005
64 | 2709717.8782 | 1096223.1604 | 2709737.816 | 1096248.3894
65 | 2709650.2303 | 1096159.4194 | 2709671.3248 | 1096153.0778
66 | 2709859.4722 | 1096037.1377 | 2709851.5495 | 1096044.2636
67 | 2709864.1112 | 1096072.4233 | 2709865.9972 | 1096072.1901 | 2709886.2267 | 1096071.986
68 | 2710024.4815 | 1096263.5764 | 2710033.4511 | 1096262.8011 | 2710033.4511 | 1096262.8011
69 | 2710026.6828 | 1096208.4169 | 2710026.5406 | 1096207.1722 | 2710021.8033 | 1096195.0214
70 | 2710033.4511 | 1096262.8011 | 2710038.6178 | 1096260.8284
71 | 2710015.0966 | 1096181.1255 | 2710019.87 | 1096190.0623 | 2710021.8033 | 1096195.0214
72 | 2710045.7219 | 1096258.1159 | 2710038.6178 | 1096260.8284
73 | 2710009.6936 | 1096171.021 | 2710015.0966 | 1096181.1255
74 | 2710015.0966 | 1096181.1255 | 2710016.2957 | 1096171.8077 | 2710013.7376 | 1096152.6339
75 | 2710072.9592 | 1096247.6172 | 2710064.9219 | 1096250.785 | 2710045.7219 | 1096258.1159
76 | 2710072.9592 | 1096247.6172 | 2710078.0999 | 1096257.6503 | 2710095.2601 | 1096286.0701
77 | 2710112.3477 | 1096239.047 | 2710080.3065 | 1096245.7601 | 2710072.9592 | 1096247.6172
78 | 2710131.662 | 1096346.357 | 2710095.2601 | 1096286.0701
79 | 2710112.3477 | 1096239.047 | 2710111.7388 | 1096229.4111
80 | 2710112.3477 | 1096239.047 | 2710124.9676 | 1096239.9428 | 2710135.743 | 1096240.5323
81 | 2710131.662 | 1096346.357 | 2710136.5246 | 1096354.4101
82 | 2710111.7388 | 1096229.4111 | 2710110.359 | 1096207.5734
83 | 2710136.5246 | 1096354.4101 | 2710189.6545 | 1096442.4011
84 | 2710110.359 | 1096207.5734 | 2710108.5568 | 1096179.0507
85 | 2710206.8462 | 1096454.3243 | 2710205.2551 | 1096453.8961 | 2710194.992 | 1096448.6621 | 2710189.7795 | 1096442.608 | 2710189.6545 | 1096442.4011
86 | 2710206.8462 | 1096454.3243 | 2710351.0637 | 1096434.1203
87 | 2710351.0637 | 1096434.1203 | 2710362.1961 | 1096431.8172 | 2710387.2959 | 1096425.3871
88 | 2710107.6937 | 1096165.3913 | 2710108.5568 | 1096179.0507
89 | 2710107.6937 | 1096165.3913 | 2710106.7667 | 1096148.0352
90 | 2710081.7232 | 1096167.5669 | 2710107.6937 | 1096165.3913
91 | 2710106.7667 | 1096148.0352 | 2710105.0219 | 1096115.3668
92 | 2710081.7232 | 1096167.5669 | 2710081.2972 | 1096154.3059
93 | 2710081.7232 | 1096167.5669 | 2710081.695 | 1096169.1221
94 | 2710104.3269 | 1096102.3549 | 2710105.0219 | 1096115.3668
95 | 2710081.3242 | 1096189.5904 | 2710081.695 | 1096169.1221
96 | 2710104.3269 | 1096102.3549 | 2710094.8462 | 1096102.7041
97 | 2710104.3269 | 1096102.3549 | 2710101.7527 | 1096054.1312
98 | 2710075.6657 | 1096103.4105 | 2710094.8462 | 1096102.7041
99 | 2710066.6201 | 1096102.3055 | 2710073.9747 | 1096103.4727 | 2710075.6657 | 1096103.4105
100 | 2710012.035 | 1096124.9291 | 2710010.2248 | 1096137.8307 | 2710013.5671 | 1096151.3558 | 2710013.7376 | 1096152.6339
101 | 2710012.8935 | 1096118.8108 | 2710012.035 | 1096124.9291
102 | 2710009.6936 | 1096171.021 | 2709999.6131 | 1096176.2088 | 2709988.1496 | 1096168.8042
103 | 2709988.1496 | 1096168.8042 | 2709984.9131 | 1096166.7136
104 | 2709974.8782 | 1096095.9967 | 2709953.1056 | 1096088.8201
105 | 2709974.8782 | 1096095.9967 | 2709975.0221 | 1096088.0495 | 2709977.1327 | 1096081.45 | 2709979.6927 | 1096072.3269
106 | 2709953.1056 | 1096088.8201 | 2709949.1497 | 1096087.5161
107 | 2709983.2643 | 1096059.599 | 2709979.6927 | 1096072.3269
108 | 2709989.8677 | 1096036.0668 | 2709986.2386 | 1096048.9996
109 | 2709989.9294 | 1096035.847 | 2709989.8677 | 1096036.0668
110 | 2709983.2643 | 1096059.599 | 2709986.2386 | 1096048.9996
111 | 2709997.5293 | 1096008.7635 | 2709989.9294 | 1096035.847
112 | 2710004.1486 | 1095985.1745 | 2709997.5293 | 1096008.7635
113 | 2710004.1486 | 1095985.1745 | 2710037.0328 | 1095995.9539
114 | 2710004.1486 | 1095985.1745 | 2710007.0814 | 1095969.9729
115 | 2710049.0979 | 1095999.9088 | 2710037.0328 | 1095995.9539
116 | 2710007.0814 | 1095969.9729 | 2709999.6857 | 1095974.4866 | 2709992.2422 | 1095981.6456 | 2709987.641 | 1095989.8468
117 | 2709938.7397 | 1096084.0848 | 2709949.1497 | 1096087.5161
118 | 2709978.6418 | 1096005.887 | 2709987.641 | 1095989.8468
119 | 2709978.6418 | 1096005.887 | 2709973.4642 | 1096015.1155
120 | 2709938.7397 | 1096084.0848 | 2709934.0478 | 1096082.5383
121 | 2709929.8825 | 1096081.1654 | 2709934.0478 | 1096082.5383
122 | 2709929.8825 | 1096081.1654 | 2709926.9665 | 1096080.2042
123 | 2709926.9665 | 1096080.2042 | 2709911.1696 | 1096074.9973 | 2709907.7929 | 1096074.5279
124 | 2709906.2343 | 1096074.3113 | 2709907.7929 | 1096074.5279
125 | 2709893.5621 | 1096072.5499 | 2709906.2343 | 1096074.3113
126 | 2709893.5621 | 1096072.5499 | 2709889.2832 | 1096071.9552 | 2709886.2267 | 1096071.986
127 | 2709859.4722 | 1096037.1377 | 2709867.6787 | 1096029.7588 | 2709874.5267 | 1096018.581
128 | 2709859.4722 | 1096037.1377 | 2709868.9963 | 1096038.7331 | 2709878.8219 | 1096036.3445
129 | 2709878.8219 | 1096036.3445 | 2709892.7934 | 1096032.9482 | 2709897.9792 | 1096033.6646 | 2709912.466 | 1096040.0366
130 | 2709918.5945 | 1096042.7322 | 2709912.466 | 1096040.0366
131 | 2709889.8995 | 1095993.4887 | 2709874.5267 | 1096018.581
132 | 2709904.8336 | 1095969.1121 | 2709889.8995 | 1095993.4887
133 | 2709904.8336 | 1095969.1121 | 2709856.6214 | 1095981.7503
134 | 2709926.4667 | 1095939.072 | 2709915.61 | 1095953.7411 | 2709904.8336 | 1095969.1121
135 | 2709973.4642 | 1096015.1155 | 2709970.1443 | 1096021.033
136 | 2709962.443 | 1096034.7598 | 2709970.1443 | 1096021.033
137 | 2709953.7009 | 1095934.5791 | 2709945.8228 | 1095940.245 | 2709942.3658 | 1095942.0393 | 2709938.6069 | 1095942.9608
138 | 2709926.4667 | 1095939.072 | 2709930.0886 | 1095941.4391 | 2709934.1833 | 1095942.9364 | 2709938.6069 | 1095942.9608
139 | 2709856.6214 | 1095981.7503 | 2709841.7854 | 1095985.6393 | 2709838.125 | 1095986.6186

## bus_geodata
| x | y | coords
0 | 2709847.7223 | 1096285.8371
1 | 2709827.614 | 1096264.7027
2 | 2709849.0771 | 1096287.2611
3 | 2709836.5389 | 1096259.0799
4 | 2709820.7986 | 1096268.8602
5 | 2709849.8441 | 1096250.6975
6 | 2709773.152 | 1096301.4436
7 | 2709811.5447 | 1096254.5948
8 | 2709855.7589 | 1096246.9711
9 | 2709743.8663 | 1096256.0453
10 | 2709807.8432 | 1096248.8887
11 | 2709864.0484 | 1096241.7487
12 | 2709878.584 | 1096232.5912
13 | 2709880.3879 | 1096231.4553
14 | 2709897.0708 | 1096220.9509
15 | 2709925.0066 | 1096265.5983
16 | 2709951.7515 | 1096308.3423
17 | 2709893.8795 | 1096216.2011
18 | 2709991.4012 | 1096282.8693
19 | 2709936.263 | 1096318.267
20 | 2709929.6077 | 1096177.8437
21 | 2709877.0659 | 1096191.1857
22 | 2709995.4931 | 1096280.2404
23 | 2709866.6543 | 1096175.6953
24 | 2710014.3308 | 1096262.3548
25 | 2709802.3819 | 1096240.4698
26 | 2709799.5001 | 1096236.0272
27 | 2709797.4237 | 1096232.8263
28 | 2709794.4496 | 1096228.2416
29 | 2709789.6993 | 1096220.9187
30 | 2709785.8869 | 1096215.0416
31 | 2709781.5703 | 1096208.3874
32 | 2709776.4005 | 1096200.4178
33 | 2709774.0455 | 1096196.7874
34 | 2709767.0126 | 1096191.0036
35 | 2709759.6725 | 1096195.7623
36 | 2709750.4992 | 1096201.7095
37 | 2709744.1374 | 1096205.8339
38 | 2709853.6495 | 1096156.3466
39 | 2709819.6103 | 1096104.7193
40 | 2709806.1828 | 1096084.3287
41 | 2709818.9909 | 1096074.8315
42 | 2709770.9892 | 1096114.8646
43 | 2709840.1459 | 1096054.5204
44 | 2709858.9287 | 1096073.0642
45 | 2709757.5399 | 1096126.5341
46 | 2709728.3709 | 1096146.7579
47 | 2709731.6915 | 1096144.5309
48 | 2709717.3502 | 1096154.1493
49 | 2709739.3948 | 1096139.3643
50 | 2709702.2855 | 1096164.251
51 | 2709708.6662 | 1096145.3835
52 | 2709647.3169 | 1096201.1104
53 | 2709693.9754 | 1096146.2685
54 | 2709798.2248 | 1096119.9754
55 | 2709633.9391 | 1096232.3411
56 | 2709692.5252 | 1096146.7044
57 | 2709739.6425 | 1096250.7005
58 | 2709737.816 | 1096248.3894
59 | 2709717.8782 | 1096223.1604
60 | 2709677.4547 | 1096210.0879
61 | 2709650.2303 | 1096159.4194
62 | 2709671.3248 | 1096153.0778
63 | 2709851.5495 | 1096044.2636
64 | 2709864.1112 | 1096072.4233
65 | 2710024.4815 | 1096263.5764
66 | 2710026.6828 | 1096208.4169
67 | 2710033.4511 | 1096262.8011
68 | 2710021.8033 | 1096195.0214
69 | 2710038.6178 | 1096260.8284
70 | 2710015.0966 | 1096181.1255
71 | 2710045.7219 | 1096258.1159
72 | 2710072.9592 | 1096247.6172
73 | 2710095.2601 | 1096286.0701
74 | 2710112.3477 | 1096239.047
75 | 2710131.662 | 1096346.357
76 | 2710111.7388 | 1096229.4111
77 | 2710135.743 | 1096240.5323
78 | 2710136.5246 | 1096354.4101
79 | 2710110.359 | 1096207.5734
80 | 2710189.6545 | 1096442.4011
81 | 2710206.8462 | 1096454.3243
82 | 2710351.0637 | 1096434.1203
83 | 2710387.2959 | 1096425.3871
84 | 2710108.5568 | 1096179.0507
85 | 2710107.6937 | 1096165.3913
86 | 2710106.7667 | 1096148.0352
87 | 2710081.7232 | 1096167.5669
88 | 2710105.0219 | 1096115.3668
89 | 2710081.2972 | 1096154.3059
90 | 2710081.695 | 1096169.1221
91 | 2710104.3269 | 1096102.3549
92 | 2710081.3242 | 1096189.5904
93 | 2710094.8462 | 1096102.7041
94 | 2710101.7527 | 1096054.1312
95 | 2710075.6657 | 1096103.4105
96 | 2710066.6201 | 1096102.3055
97 | 2710012.035 | 1096124.9291
98 | 2710013.7376 | 1096152.6339
99 | 2710012.8935 | 1096118.8108
100 | 2710009.6936 | 1096171.021
101 | 2709988.1496 | 1096168.8042
102 | 2709974.8782 | 1096095.9967
103 | 2709953.1056 | 1096088.8201
104 | 2709979.6927 | 1096072.3269
105 | 2709984.9131 | 1096166.7136
106 | 2709989.8677 | 1096036.0668
107 | 2709986.2386 | 1096048.9996
108 | 2709989.9294 | 1096035.847
109 | 2709983.2643 | 1096059.599
110 | 2709997.5293 | 1096008.7635
111 | 2710004.1486 | 1095985.1745
112 | 2710037.0328 | 1095995.9539
113 | 2710007.0814 | 1095969.9729
114 | 2709949.1497 | 1096087.5161
115 | 2710049.0979 | 1095999.9088
116 | 2709987.641 | 1095989.8468
117 | 2709978.6418 | 1096005.887
118 | 2709938.7397 | 1096084.0848
119 | 2709934.0478 | 1096082.5383
120 | 2709929.8825 | 1096081.1654
121 | 2709926.9665 | 1096080.2042
122 | 2709907.7929 | 1096074.5279
123 | 2709906.2343 | 1096074.3113
124 | 2709893.5621 | 1096072.5499
125 | 2709886.2267 | 1096071.986
126 | 2709859.4722 | 1096037.1377
127 | 2709878.8219 | 1096036.3445
128 | 2709912.466 | 1096040.0366
129 | 2709918.5945 | 1096042.7322
130 | 2709874.5267 | 1096018.581
131 | 2709889.8995 | 1095993.4887
132 | 2709904.8336 | 1095969.1121
133 | 2709973.4642 | 1096015.1155
134 | 2709970.1443 | 1096021.033
135 | 2709962.443 | 1096034.7598
136 | 2709953.7009 | 1095934.579
137 | 2709938.6069 | 1095942.9608
138 | 2709926.4667 | 1095939.072
139 | 2709856.6214 | 1095981.7503
140 | 2709838.125 | 1095986.6186
141 | 2709893.8795 | 1096216.2011

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98509 | -0.28525 | 0.0062173 | 0.0015582
1 | 0.98536 | -0.27998 | 0 | 0
2 | 0.98508 | -0.28539 | 0.0038495 | 0.00096479
3 | 0.98606 | -0.26645 | 0.0034502 | 0.0008647
4 | 0.98491 | -0.28876 | 0 | 0
5 | 0.98714 | -0.24536 | 0.0045774 | 0.0011472
6 | 0.98438 | -0.29909 | 0 | 0
7 | 0.9841 | -0.30449 | 0.0037999 | 0.00095235
8 | 0.98765 | -0.23543 | 0.0059716 | 0.0014966
9 | 0.98387 | -0.30895 | 0.0016589 | 0.00041576
10 | 0.9838 | -0.31032 | 0.0038704 | 0.00097003
11 | 0.98843 | -0.22048 | 0.0048476 | 0.0012149
12 | 0.98986 | -0.19284 | 0 | 0
13 | 0.99003 | -0.18942 | 0.0034578 | 0.00086661
14 | 0.99174 | -0.1566 | 0 | 0
15 | 0.98978 | -0.19412 | 0.0037371 | 0.00093661
16 | 0.98705 | -0.24656 | 0 | 0
17 | 0.99212 | -0.14937 | 0 | 0
18 | 0.98478 | -0.29046 | 0.0031955 | 0.00080087
19 | 0.98684 | -0.25074 | 0.012697 | 0.0031822
20 | 1 | 0 | -0.41717 | -0.10718
21 | 0.99031 | -0.18388 | 0.0015644 | 0.00039207
22 | 0.98432 | -0.29927 | 0.008598 | 0.0021548
23 | 0.9892 | -0.20513 | 0.001624 | 0.00040702
24 | 0.98209 | -0.34252 | 0 | 0
25 | 0.9834 | -0.31823 | 0.0021402 | 0.00053638
26 | 0.98319 | -0.32221 | 0.0030048 | 0.00075308
27 | 0.98306 | -0.32486 | 0.0023294 | 0.00058381
28 | 0.98287 | -0.32844 | 0.0022451 | 0.00056269
29 | 0.9826 | -0.3338 | 0.0017633 | 0.00044193
30 | 0.98239 | -0.33788 | 0.0019944 | 0.00049984
31 | 0.98217 | -0.34222 | 0.0030464 | 0.00076349
32 | 0.98193 | -0.3469 | 0.0018493 | 0.00046348
33 | 0.98183 | -0.34889 | 0.0037814 | 0.00094772
34 | 0.98164 | -0.3526 | 0.0069729 | 0.0017476
35 | 0.98152 | -0.35491 | 0.0048788 | 0.0012227
36 | 0.98142 | -0.35684 | 0.0028341 | 0.00071029
37 | 0.98137 | -0.35779 | 0.00692 | 0.0017343
38 | 0.98783 | -0.23152 | 0.0014085 | 0.000353
39 | 0.98421 | -0.30136 | 0.004844 | 0.001214
40 | 0.98282 | -0.32836 | 0.0032723 | 0.00082011
41 | 0.98215 | -0.34139 | 0 | 0
42 | 0.98089 | -0.36609 | 0.0051763 | 0.0012973
43 | 0.98062 | -0.37118 | 0.0025752 | 0.0006454
44 | 0.98114 | -0.36099 | 0.0031996 | 0.0008019
45 | 0.98023 | -0.37887 | 0 | 0
46 | 0.97903 | -0.40252 | 0.0066358 | 0.0016631
47 | 0.97914 | -0.4003 | 0.0056821 | 0.0014241
48 | 0.97873 | -0.40828 | 0 | 0
49 | 0.97945 | -0.3942 | 0.0017776 | 0.00044551
50 | 0.97854 | -0.41198 | 0.0039202 | 0.0009825
51 | 0.97859 | -0.41117 | 0.0052611 | 0.0013185
52 | 0.9781 | -0.42075 | 0.0022421 | 0.00056191
53 | 0.97848 | -0.41324 | 0.0019008 | 0.00047639
54 | 0.98017 | -0.38009 | 0.0016371 | 0.00041031
55 | 0.97792 | -0.42429 | 0 | 0
56 | 0.97847 | -0.41339 | 0.0024877 | 0.00062347
57 | 0.98382 | -0.30997 | 0.0020914 | 0.00052416
58 | 0.98381 | -0.31029 | 0.0011759 | 0.00029471
59 | 0.98366 | -0.3132 | 0.005024 | 0.0012591
60 | 0.97769 | -0.42877 | 0.0050306 | 0.0012608
61 | 0.97839 | -0.41511 | 0.001233 | 0.00030901
62 | 0.97841 | -0.41461 | 0.0017913 | 0.00044895
63 | 0.97986 | -0.38606 | 0.0033024 | 0.00082767
64 | 0.98101 | -0.36341 | 0.0031394 | 0.00078682
65 | 0.98141 | -0.35583 | 0.0016898 | 0.00042351
66 | 0.98099 | -0.36415 | 0.0011727 | 0.00029391
67 | 0.98083 | -0.36715 | 0.0016047 | 0.00040217
68 | 0.98073 | -0.36927 | 0.00285 | 0.00071427
69 | 0.98048 | -0.37396 | 0.0030564 | 0.000766
70 | 0.98048 | -0.37401 | 0 | 0
71 | 0.98002 | -0.38289 | 0.0018527 | 0.00046433
72 | 0.97831 | -0.41629 | 0 | 0
73 | 0.97758 | -0.43061 | 0.00091064 | 0.00022823
74 | 0.97661 | -0.44949 | 0 | 0
75 | 0.97648 | -0.45215 | 0.002613 | 0.00065488
76 | 0.97622 | -0.4572 | 0.0010764 | 0.00026976
77 | 0.97658 | -0.45017 | 0.0015804 | 0.0003961
78 | 0.97636 | -0.45458 | 0.0017759 | 0.00044509
79 | 0.97535 | -0.47427 | 0.003149 | 0.00078921
80 | 0.97518 | -0.47784 | 0.0017655 | 0.00044249
81 | 0.97497 | -0.482 | 0.0045897 | 0.0011503
82 | 0.97415 | -0.49804 | 0.0024377 | 0.00061095
83 | 0.97403 | -0.50048 | 0.0035604 | 0.00089231
84 | 0.9743 | -0.49496 | 0.0020704 | 0.00051888
85 | 0.97382 | -0.50436 | 0 | 0
86 | 0.97338 | -0.51302 | 0.0047776 | 0.0011974
87 | 0.97357 | -0.50927 | 0 | 0
88 | 0.9727 | -0.52645 | 0.0035655 | 0.00089359
89 | 0.97352 | -0.51027 | 0.0040648 | 0.0010187
90 | 0.97356 | -0.50945 | 0.0030686 | 0.00076906
91 | 0.97247 | -0.53096 | 0 | 0
92 | 0.9735 | -0.51064 | 0.0031597 | 0.00079188
93 | 0.97234 | -0.53354 | 0.0019577 | 0.00049064
94 | 0.9723 | -0.53448 | 0.0039617 | 0.00099289
95 | 0.97211 | -0.53808 | 0.0055405 | 0.0013886
96 | 0.97205 | -0.53931 | 0.0072875 | 0.0018264
97 | 0.98005 | -0.38252 | 0.0039166 | 0.0009816
98 | 0.98024 | -0.37878 | 0.0018472 | 0.00046295
99 | 0.98003 | -0.38289 | 0.0033764 | 0.0008462
100 | 0.9804 | -0.37563 | 0 | 0
101 | 0.98022 | -0.37916 | 0.0057395 | 0.0014385
102 | 0.97617 | -0.45812 | 0 | 0
103 | 0.97719 | -0.43813 | 0.0021468 | 0.00053805
104 | 0.97509 | -0.47939 | 0.0044557 | 0.0011167
105 | 0.98021 | -0.37931 | 0.0020518 | 0.00051423
106 | 0.97369 | -0.50683 | 0.0061766 | 0.001548
107 | 0.97415 | -0.49787 | 0.0031803 | 0.00079705
108 | 0.97369 | -0.50696 | 0.0015401 | 0.000386
109 | 0.97455 | -0.48988 | 0.00376 | 0.00094233
110 | 0.97294 | -0.52176 | 0.0041447 | 0.0010388
111 | 0.97238 | -0.5328 | 0 | 0
112 | 0.97213 | -0.53765 | 0.0032347 | 0.0008107
113 | 0.97213 | -0.53761 | 0 | 0
114 | 0.97738 | -0.43434 | 0.0022257 | 0.00055782
115 | 0.97208 | -0.53868 | 0.0043679 | 0.0010947
116 | 0.97169 | -0.54644 | 0.0064381 | 0.0016136
117 | 0.97151 | -0.54998 | 0.0019891 | 0.00049851
118 | 0.97791 | -0.42393 | 0.0027642 | 0.00069277
119 | 0.97817 | -0.41899 | 0.0039812 | 0.00099779
120 | 0.97841 | -0.41429 | 0.0045776 | 0.0011472
121 | 0.97859 | -0.41074 | 0.0030435 | 0.00076276
122 | 0.97983 | -0.38653 | 0.0023133 | 0.00057976
123 | 0.97993 | -0.38457 | 0.0012369 | 0.00030999
124 | 0.98035 | -0.37644 | 0.0013866 | 0.00034752
125 | 0.98051 | -0.37326 | 0.0022613 | 0.00056672
126 | 0.97936 | -0.39577 | 0 | 0
127 | 0.97915 | -0.39988 | 0.0035451 | 0.00088847
128 | 0.97889 | -0.40497 | 0.0023639 | 0.00059244
129 | 0.97886 | -0.40565 | 0.0055339 | 0.0013869
130 | 0.97849 | -0.41278 | 0.002999 | 0.00075163
131 | 0.97752 | -0.43195 | 0.0030513 | 0.00076474
132 | 0.97665 | -0.449 | 0 | 0
133 | 0.97143 | -0.55162 | 0.0035434 | 0.00088805
134 | 0.97139 | -0.55224 | 0.0021222 | 0.00053186
135 | 0.97135 | -0.55304 | 0.002757 | 0.00069097
136 | 0.97523 | -0.47686 | 0.012107 | 0.0030344
137 | 0.97543 | -0.47299 | 0.014053 | 0.0035221
138 | 0.97575 | -0.4667 | 0 | 0
139 | 0.97634 | -0.45495 | 0.002924 | 0.00073283
140 | 0.97628 | -0.4562 | 0.003596 | 0.00090125
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010067 | -0.002523 | 0.010069 | 0.0025242 | 2.5296e-06 | 1.2474e-06 | 0.015206 | 0.015206 | 0.015206 | 0.98509 | -0.28525 | 0.98536 | -0.27998 | 4.1776
1 | 0.0038496 | 0.00096478 | -0.0038495 | -0.00096479 | 2.4923e-08 | -9.0722e-09 | 0.0058149 | 0.0058149 | 0.0058149 | 0.98509 | -0.28525 | 0.98508 | -0.28539 | 1.5975
2 | -0.071611 | -0.018007 | 0.071657 | 0.018036 | 4.6278e-05 | 2.9483e-05 | 0.10816 | 0.10816 | 0.10816 | 0.98536 | -0.27998 | 0.98606 | -0.26645 | 29.7149
3 | 0.061541 | 0.015483 | -0.061515 | -0.015466 | 2.5815e-05 | 1.642e-05 | 0.092956 | 0.092956 | 0.092956 | 0.98536 | -0.27998 | 0.98491 | -0.28876 | 25.5374
4 | -0.075107 | -0.018901 | 0.075183 | 0.018949 | 7.5792e-05 | 4.8306e-05 | 0.11337 | 0.11337 | 0.11337 | 0.98606 | -0.26645 | 0.98714 | -0.24536 | 31.1452
5 | 0.009961 | 0.0024987 | -0.0099561 | -0.0024963 | 4.903e-06 | 2.4037e-06 | 0.01505 | 0.01505 | 0.01505 | 0.98491 | -0.28876 | 0.98438 | -0.29909 | 4.1347
6 | 0.051554 | 0.012967 | -0.051516 | -0.012943 | 3.8701e-05 | 2.4552e-05 | 0.077906 | 0.077906 | 0.077906 | 0.98491 | -0.28876 | 0.9841 | -0.30449 | 21.4027
7 | -0.07976 | -0.020096 | 0.079798 | 0.020121 | 3.7919e-05 | 2.4179e-05 | 0.12027 | 0.12027 | 0.12027 | 0.98714 | -0.24536 | 0.98765 | -0.23543 | 33.0408
8 | 0.0099561 | 0.0024963 | -0.0099515 | -0.002494 | 4.6755e-06 | 2.2929e-06 | 0.01505 | 0.015051 | 0.015051 | 0.98438 | -0.29909 | 0.98387 | -0.30895 | 4.1348
9 | 0.047716 | 0.011991 | -0.047703 | -0.011982 | 1.3281e-05 | 8.4134e-06 | 0.07216 | 0.07216 | 0.07216 | 0.9841 | -0.30449 | 0.9838 | -0.31032 | 19.8243
10 | -0.08577 | -0.021617 | 0.085831 | 0.021656 | 6.1391e-05 | 3.9165e-05 | 0.12927 | 0.12927 | 0.12927 | 0.98765 | -0.23543 | 0.98843 | -0.22048 | 35.5125
11 | 0.0082925 | 0.0020782 | -0.0082921 | -0.0020781 | 4.0182e-07 | 1.7066e-07 | 0.012542 | 0.012542 | 0.012542 | 0.98387 | -0.30895 | 0.98382 | -0.30997 | 3.4455
12 | 0.043832 | 0.011012 | -0.043816 | -0.011002 | 1.6545e-05 | 1.0461e-05 | 0.066306 | 0.066306 | 0.066306 | 0.9838 | -0.31032 | 0.9834 | -0.31823 | 18.216
13 | -0.090679 | -0.022871 | 0.090799 | 0.022948 | 0.00012015 | 7.6674e-05 | 0.13656 | 0.13656 | 0.13656 | 0.98843 | -0.22048 | 0.98986 | -0.19284 | 37.5174
14 | -0.090799 | -0.022948 | 0.090814 | 0.022958 | 1.4908e-05 | 9.514e-06 | 0.13656 | 0.13656 | 0.13656 | 0.98986 | -0.19284 | 0.99003 | -0.18942 | 37.5173
15 | -0.094272 | -0.023824 | 0.09442 | 0.023919 | 0.00014857 | 9.483e-05 | 0.14176 | 0.14176 | 0.14176 | 0.99003 | -0.18942 | 0.99174 | -0.1566 | 38.9451
16 | -0.21623 | -0.055021 | 0.21631 | 0.055069 | 7.5373e-05 | 4.8017e-05 | 0.32474 | 0.32474 | 0.32474 | 0.99174 | -0.1566 | 0.99212 | -0.14937 | 29.7377
17 | 0.12181 | 0.031102 | -0.12159 | -0.030963 | 0.00022041 | 0.00013903 | 0.18298 | 0.18298 | 0.18298 | 0.99174 | -0.1566 | 0.98978 | -0.19412 | 16.7561
18 | 0.11786 | 0.030026 | -0.11756 | -0.029837 | 0.00029739 | 0.00018904 | 0.17736 | 0.17736 | 0.17736 | 0.98978 | -0.19412 | 0.98705 | -0.24656 | 24.3625
19 | 0.10486 | 0.026654 | -0.10464 | -0.026513 | 0.00022119 | 0.00014036 | 0.15821 | 0.15821 | 0.15821 | 0.98705 | -0.24656 | 0.98478 | -0.29046 | 21.7327
20 | 0.0127 | 0.0031835 | -0.012697 | -0.0031822 | 2.5285e-06 | 1.3832e-06 | 0.019145 | 0.019145 | 0.019145 | 0.98705 | -0.24656 | 0.98684 | -0.25074 | 5.2597
21 | -0.41252 | -0.10526 | 0.41552 | 0.10718 | 0.0030003 | 0.0019177 | 0.61938 | 0.61938 | 0.61938 | 0.99212 | -0.14937 | 1 | 0 | 56.7197
22 | 0.19621 | 0.050195 | -0.19588 | -0.049986 | 0.00032708 | 0.00020817 | 0.29464 | 0.29464 | 0.29464 | 0.99212 | -0.14937 | 0.99031 | -0.18388 | 26.9821
23 | 0.10144 | 0.025713 | -0.1014 | -0.025685 | 4.2911e-05 | 2.7401e-05 | 0.15339 | 0.15339 | 0.15339 | 0.98478 | -0.29046 | 0.98432 | -0.29927 | 42.139
24 | 0.19432 | 0.049594 | -0.19412 | -0.049468 | 0.00019932 | 0.00012685 | 0.29229 | 0.29229 | 0.29229 | 0.99031 | -0.18388 | 0.9892 | -0.20513 | 26.7668
25 | 0.092802 | 0.02353 | -0.09261 | -0.023407 | 0.00019252 | 0.00012288 | 0.14039 | 0.14039 | 0.14039 | 0.98432 | -0.29927 | 0.98209 | -0.34252 | 38.5682
26 | 0.19249 | 0.049061 | -0.19225 | -0.048905 | 0.00024483 | 0.00015579 | 0.28985 | 0.28985 | 0.28985 | 0.9892 | -0.20513 | 0.98783 | -0.23152 | 26.5431
27 | 0.07162 | 0.018135 | -0.071574 | -0.018106 | 4.574e-05 | 2.9143e-05 | 0.10858 | 0.10858 | 0.10858 | 0.98209 | -0.34252 | 0.98141 | -0.35583 | 29.8301
28 | 0.02099 | 0.005272 | -0.020968 | -0.0052589 | 2.1634e-05 | 1.3125e-05 | 0.031807 | 0.031807 | 0.031807 | 0.98209 | -0.34252 | 0.98099 | -0.36415 | 8.7382
29 | 0.041675 | 0.010465 | -0.041667 | -0.01046 | 7.8986e-06 | 4.988e-06 | 0.063068 | 0.063068 | 0.063068 | 0.9834 | -0.31823 | 0.98319 | -0.32221 | 17.3263
30 | 0.038663 | 0.0097072 | -0.038658 | -0.0097041 | 4.8998e-06 | 3.0875e-06 | 0.05852 | 0.05852 | 0.05852 | 0.98319 | -0.32221 | 0.98306 | -0.32486 | 16.077
31 | 0.036328 | 0.0091203 | -0.036322 | -0.0091164 | 6.1979e-06 | 3.8974e-06 | 0.054994 | 0.054994 | 0.054994 | 0.98306 | -0.32486 | 0.98287 | -0.32844 | 15.1083
32 | 0.034077 | 0.0085537 | -0.034068 | -0.0085483 | 8.7137e-06 | 5.4662e-06 | 0.051595 | 0.051595 | 0.051595 | 0.98287 | -0.32844 | 0.9826 | -0.3338 | 14.1745
33 | 0.032305 | 0.0081063 | -0.032299 | -0.0081024 | 6.2881e-06 | 3.9357e-06 | 0.048925 | 0.048925 | 0.048925 | 0.9826 | -0.3338 | 0.98239 | -0.33788 | 13.4409
34 | 0.030304 | 0.0076025 | -0.030298 | -0.0075986 | 6.2676e-06 | 3.9108e-06 | 0.045904 | 0.045904 | 0.045904 | 0.98239 | -0.33788 | 0.98217 | -0.34222 | 12.611
35 | 0.027252 | 0.0068351 | -0.027245 | -0.0068314 | 6.0729e-06 | 3.7665e-06 | 0.041289 | 0.041289 | 0.041289 | 0.98217 | -0.34222 | 0.98193 | -0.3469 | 11.3431
36 | 0.025396 | 0.0063679 | -0.025394 | -0.0063664 | 2.4037e-06 | 1.4836e-06 | 0.038486 | 0.038486 | 0.038486 | 0.98193 | -0.3469 | 0.98183 | -0.34889 | 10.5732
37 | 0.021612 | 0.0054187 | -0.021609 | -0.0054164 | 3.8199e-06 | 2.3247e-06 | 0.032756 | 0.032756 | 0.032756 | 0.98183 | -0.34889 | 0.98164 | -0.3526 | 8.9988
38 | 0.014636 | 0.0036688 | -0.014634 | -0.0036679 | 1.6146e-06 | 9.2279e-07 | 0.022186 | 0.022186 | 0.022186 | 0.98164 | -0.3526 | 0.98152 | -0.35491 | 6.095
39 | 0.0097553 | 0.0024451 | -0.0097544 | -0.0024447 | 8.9671e-07 | 4.3573e-07 | 0.014789 | 0.014789 | 0.014789 | 0.98152 | -0.35491 | 0.98142 | -0.35684 | 4.063
40 | 0.0069203 | 0.0017344 | -0.00692 | -0.0017343 | 3.1301e-07 | 1.0452e-07 | 0.010492 | 0.010493 | 0.010493 | 0.98142 | -0.35684 | 0.98137 | -0.35779 | 2.8826
41 | 0.19084 | 0.048552 | -0.1902 | -0.048145 | 0.00063994 | 0.0004072 | 0.28773 | 0.28773 | 0.28773 | 0.98783 | -0.23152 | 0.98421 | -0.30136 | 26.3489
42 | 0.18535 | 0.046931 | -0.18511 | -0.046778 | 0.00023996 | 0.00015264 | 0.28041 | 0.28041 | 0.28041 | 0.98421 | -0.30136 | 0.98282 | -0.32836 | 25.6783
43 | 0.1369 | 0.034637 | -0.13682 | -0.034583 | 8.5578e-05 | 5.4165e-05 | 0.20739 | 0.20739 | 0.20739 | 0.98282 | -0.32836 | 0.98215 | -0.34139 | 18.9921
44 | 0.044939 | 0.011321 | -0.044858 | -0.01127 | 8.0936e-05 | 5.121e-05 | 0.068059 | 0.06806 | 0.06806 | 0.98282 | -0.32836 | 0.98089 | -0.36609 | 18.6977
45 | 0.056323 | 0.014217 | -0.056243 | -0.014166 | 8.0232e-05 | 5.0977e-05 | 0.085369 | 0.085369 | 0.085369 | 0.98215 | -0.34139 | 0.98062 | -0.37118 | 23.4531
46 | 0.080495 | 0.020365 | -0.08042 | -0.020318 | 7.5629e-05 | 4.6862e-05 | 0.12202 | 0.12202 | 0.12202 | 0.98215 | -0.34139 | 0.98114 | -0.36099 | 11.1744
47 | 0.039681 | 0.0099726 | -0.039657 | -0.0099573 | 2.4205e-05 | 1.5266e-05 | 0.060207 | 0.060207 | 0.060207 | 0.98089 | -0.36609 | 0.98023 | -0.37887 | 16.5404
48 | 0.053667 | 0.013521 | -0.053629 | -0.013497 | 3.8168e-05 | 2.4234e-05 | 0.081462 | 0.081462 | 0.081462 | 0.98062 | -0.37118 | 0.97986 | -0.38606 | 22.3796
49 | 0.07722 | 0.019516 | -0.077211 | -0.019511 | 8.9619e-06 | 5.5378e-06 | 0.11717 | 0.11717 | 0.11717 | 0.98114 | -0.36099 | 0.98101 | -0.36341 | 10.7301
50 | 0.0016372 | 0.00040985 | -0.0016371 | -0.00041031 | 9.5177e-08 | -4.5704e-07 | 0.0024852 | 0.0024854 | 0.0024854 | 0.98023 | -0.37887 | 0.98017 | -0.38009 | 0.6828
51 | 0.03802 | 0.0095475 | -0.037992 | -0.00953 | 2.778e-05 | 1.7499e-05 | 0.057722 | 0.057722 | 0.057722 | 0.98023 | -0.37887 | 0.97945 | -0.3942 | 15.8577
52 | -0.030519 | -0.0076518 | 0.030522 | 0.0076538 | 3.2261e-06 | 2.0144e-06 | 0.046386 | 0.046386 | 0.046386 | 0.97903 | -0.40252 | 0.97914 | -0.4003 | 12.7435
53 | 0.023883 | 0.0059887 | -0.023876 | -0.0059846 | 6.5573e-06 | 4.0298e-06 | 0.036301 | 0.036301 | 0.036301 | 0.97903 | -0.40252 | 0.97873 | -0.40828 | 9.9727
54 | -0.036204 | -0.0090779 | 0.036215 | 0.0090845 | 1.053e-05 | 6.6225e-06 | 0.055021 | 0.055021 | 0.055021 | 0.97914 | -0.4003 | 0.97945 | -0.3942 | 15.1158
55 | 0.0112 | 0.0028075 | -0.011198 | -0.0028064 | 1.9721e-06 | 1.0343e-06 | 0.017028 | 0.017028 | 0.017028 | 0.97873 | -0.40828 | 0.97854 | -0.41198 | 4.678
56 | 0.012677 | 0.0031772 | -0.012675 | -0.0031762 | 1.7454e-06 | 9.5958e-07 | 0.019273 | 0.019273 | 0.019273 | 0.97873 | -0.40828 | 0.97859 | -0.41117 | 5.2948
57 | 0.0072776 | 0.0018239 | -0.0072745 | -0.0018228 | 3.0396e-06 | 1.1143e-06 | 0.011067 | 0.011067 | 0.011067 | 0.97854 | -0.41198 | 0.9781 | -0.42075 | 3.0404
58 | 0.0074137 | 0.0018577 | -0.007413 | -0.0018574 | 7.3032e-07 | 2.7489e-07 | 0.011273 | 0.011273 | 0.011273 | 0.97859 | -0.41117 | 0.97848 | -0.41324 | 3.097
59 | 0.0050325 | 0.0012609 | -0.0050316 | -0.0012608 | 8.4908e-07 | 5.8678e-08 | 0.007656 | 0.0076561 | 0.0076561 | 0.9781 | -0.42075 | 0.97792 | -0.42429 | 2.1033
60 | 0.0055122 | 0.001381 | -0.0055122 | -0.001381 | 3.9901e-08 | 6.5162e-09 | 0.0083825 | 0.0083825 | 0.0083825 | 0.97848 | -0.41324 | 0.97847 | -0.41339 | 2.3029
61 | 0.0050316 | 0.0012608 | -0.0050306 | -0.0012608 | 1.0744e-06 | 7.4534e-08 | 0.0076561 | 0.0076564 | 0.0076564 | 0.97792 | -0.42429 | 0.97769 | -0.42877 | 2.1034
62 | 0.0030245 | 0.00075754 | -0.0030243 | -0.0007577 | 1.7562e-07 | -1.6565e-07 | 0.0045993 | 0.0045994 | 0.0045994 | 0.97847 | -0.41339 | 0.97841 | -0.41461 | 1.2636
63 | 0.0062007 | 0.0015539 | -0.0062006 | -0.0015539 | 9.7158e-08 | 2.4777e-08 | 0.0093784 | 0.0093784 | 0.0093784 | 0.98382 | -0.30997 | 0.98381 | -0.31029 | 2.5765
64 | 0.0050247 | 0.0012592 | -0.005024 | -0.0012591 | 6.9649e-07 | 3.7503e-08 | 0.0075999 | 0.0076 | 0.0076 | 0.98381 | -0.31029 | 0.98366 | -0.3132 | 2.0879
65 | -0.001233 | -0.00030901 | 0.001233 | 0.00030876 | 2.9045e-08 | -2.5804e-07 | 0.0018752 | 0.0018751 | 0.0018752 | 0.97839 | -0.41511 | 0.97841 | -0.41461 | 0.51517
66 | 0.050327 | 0.012669 | -0.050304 | -0.012654 | 2.3353e-05 | 1.4812e-05 | 0.076447 | 0.076447 | 0.076447 | 0.97986 | -0.38606 | 0.97936 | -0.39577 | 21.0019
67 | 0.074072 | 0.018724 | -0.074037 | -0.018703 | 3.4956e-05 | 2.1534e-05 | 0.11241 | 0.11241 | 0.11241 | 0.98101 | -0.36341 | 0.98051 | -0.37326 | 10.294
68 | 0.069884 | 0.017683 | -0.069846 | -0.017659 | 3.7948e-05 | 2.4173e-05 | 0.10602 | 0.10602 | 0.10602 | 0.98141 | -0.35583 | 0.98083 | -0.36715 | 29.1262
69 | 0.019796 | 0.004965 | -0.019791 | -0.0049621 | 4.8335e-06 | 2.913e-06 | 0.030028 | 0.030028 | 0.030028 | 0.98099 | -0.36415 | 0.98073 | -0.36927 | 8.2495
70 | 0.068242 | 0.017256 | -0.06822 | -0.017242 | 2.2253e-05 | 1.4172e-05 | 0.10359 | 0.10359 | 0.10359 | 0.98083 | -0.36715 | 0.98048 | -0.37396 | 28.4574
71 | 0.016941 | 0.0042478 | -0.016937 | -0.0042456 | 3.829e-06 | 2.2556e-06 | 0.025704 | 0.025704 | 0.025704 | 0.98073 | -0.36927 | 0.98048 | -0.37401 | 7.0616
72 | 0.065163 | 0.016476 | -0.065135 | -0.016458 | 2.7919e-05 | 1.7772e-05 | 0.098947 | 0.098947 | 0.098947 | 0.98048 | -0.37396 | 0.98002 | -0.38289 | 27.1831
73 | 0.0077933 | 0.0019534 | -0.0077927 | -0.0019532 | 6.0075e-07 | 2.4006e-07 | 0.011827 | 0.011827 | 0.011827 | 0.98048 | -0.37401 | 0.9804 | -0.37563 | 3.2493
74 | 0.0091436 | 0.0022921 | -0.0091415 | -0.0022912 | 2.0753e-06 | 9.6582e-07 | 0.013877 | 0.013877 | 0.013877 | 0.98048 | -0.37401 | 0.98024 | -0.37878 | 3.8124
75 | 0.063283 | 0.015994 | -0.063181 | -0.01593 | 0.00010117 | 6.4379e-05 | 0.096134 | 0.096134 | 0.096134 | 0.98002 | -0.38289 | 0.97831 | -0.41629 | 26.4104
76 | 0.017705 | 0.004452 | -0.017693 | -0.0044448 | 1.2099e-05 | 7.1851e-06 | 0.026934 | 0.026935 | 0.026935 | 0.97831 | -0.41629 | 0.97758 | -0.43061 | 7.3996
77 | 0.045477 | 0.011478 | -0.045405 | -0.011432 | 7.219e-05 | 4.5697e-05 | 0.069199 | 0.0692 | 0.0692 | 0.97831 | -0.41629 | 0.97661 | -0.44949 | 19.0109
78 | 0.016782 | 0.0042166 | -0.016765 | -0.0042064 | 1.7238e-05 | 1.015e-05 | 0.025548 | 0.025549 | 0.025549 | 0.97758 | -0.43061 | 0.97648 | -0.45215 | 7.0189
79 | 0.043824 | 0.011036 | -0.043808 | -0.011026 | 1.6152e-05 | 1.0217e-05 | 0.066792 | 0.066792 | 0.066792 | 0.97661 | -0.44949 | 0.97622 | -0.4572 | 18.3493
80 | 0.0015805 | 0.00039583 | -0.0015804 | -0.0003961 | 5.0978e-08 | -2.607e-07 | 0.002408 | 0.0024081 | 0.0024081 | 0.97661 | -0.44949 | 0.97658 | -0.45017 | 0.66157
81 | 0.014152 | 0.0035515 | -0.01415 | -0.0035506 | 1.6408e-06 | 9.3248e-07 | 0.021567 | 0.021567 | 0.021567 | 0.97648 | -0.45215 | 0.97636 | -0.45458 | 5.925
82 | 0.042732 | 0.010756 | -0.042697 | -0.010734 | 3.483e-05 | 2.2018e-05 | 0.065151 | 0.065151 | 0.065151 | 0.97622 | -0.4572 | 0.97535 | -0.47427 | 17.8986
83 | 0.012374 | 0.0031055 | -0.01236 | -0.003098 | 1.3711e-05 | 7.4913e-06 | 0.01886 | 0.018861 | 0.018861 | 0.97636 | -0.45458 | 0.97518 | -0.47784 | 5.1815
84 | 0.039548 | 0.009945 | -0.039509 | -0.0099204 | 3.903e-05 | 2.4623e-05 | 0.060347 | 0.060347 | 0.060347 | 0.97535 | -0.47427 | 0.9743 | -0.49496 | 16.5789
85 | 0.010595 | 0.0026555 | -0.010593 | -0.0026545 | 2.0974e-06 | 1.0754e-06 | 0.016167 | 0.016167 | 0.016167 | 0.97518 | -0.47784 | 0.97497 | -0.482 | 4.4414
86 | 0.0060031 | 0.0015042 | -0.0059985 | -0.0015031 | 4.5843e-06 | 1.1194e-06 | 0.0091619 | 0.0091626 | 0.0091626 | 0.97497 | -0.482 | 0.97415 | -0.49804 | 2.5172
87 | 0.0035608 | 0.00089211 | -0.0035604 | -0.00089231 | 4.1356e-07 | -1.9938e-07 | 0.005439 | 0.0054391 | 0.0054391 | 0.97415 | -0.49804 | 0.97403 | -0.50048 | 1.4943
88 | 0.037438 | 0.0094015 | -0.037422 | -0.0093909 | 1.6784e-05 | 1.0571e-05 | 0.057185 | 0.057185 | 0.057185 | 0.9743 | -0.49496 | 0.97382 | -0.50436 | 15.7102
89 | 0.027126 | 0.0068102 | -0.027114 | -0.0068032 | 1.12e-05 | 6.9517e-06 | 0.041453 | 0.041453 | 0.041453 | 0.97382 | -0.50436 | 0.97338 | -0.51302 | 11.3881
90 | 0.010296 | 0.0025807 | -0.010293 | -0.0025795 | 2.4117e-06 | 1.2203e-06 | 0.015732 | 0.015732 | 0.015732 | 0.97382 | -0.50436 | 0.97357 | -0.50927 | 4.3221
91 | 0.022337 | 0.0056059 | -0.022323 | -0.0055971 | 1.4307e-05 | 8.75e-06 | 0.034149 | 0.034149 | 0.034149 | 0.97338 | -0.51302 | 0.9727 | -0.52645 | 9.3817
92 | 0.004065 | 0.0010187 | -0.0040648 | -0.0010187 | 1.921e-07 | -4.2072e-08 | 0.0062129 | 0.006213 | 0.006213 | 0.97357 | -0.50927 | 0.97352 | -0.51027 | 1.7069
93 | 0.0062285 | 0.0015608 | -0.0062284 | -0.0015608 | 5.2858e-08 | 1.4488e-08 | 0.0095196 | 0.0095196 | 0.0095196 | 0.97357 | -0.50927 | 0.97356 | -0.50945 | 2.6153
94 | 0.018757 | 0.0047035 | -0.018753 | -0.0047011 | 4.0235e-06 | 2.4133e-06 | 0.028695 | 0.028695 | 0.028695 | 0.9727 | -0.52645 | 0.97247 | -0.53096 | 7.8833
95 | 0.0031598 | 0.00079174 | -0.0031597 | -0.00079188 | 1.7906e-07 | -1.3995e-07 | 0.0048295 | 0.0048296 | 0.0048296 | 0.97356 | -0.50945 | 0.9735 | -0.51064 | 1.3268
96 | 0.014791 | 0.0037084 | -0.014789 | -0.0037073 | 1.8223e-06 | 1.0486e-06 | 0.022632 | 0.022632 | 0.022632 | 0.97247 | -0.53096 | 0.97234 | -0.53354 | 6.2177
97 | 0.0039623 | 0.00099272 | -0.0039617 | -0.00099289 | 6.6569e-07 | -1.7301e-07 | 0.0060628 | 0.006063 | 0.006063 | 0.97247 | -0.53096 | 0.9723 | -0.53448 | 1.6657
98 | 0.012831 | 0.0032167 | -0.012828 | -0.0032152 | 2.7753e-06 | 1.5382e-06 | 0.019636 | 0.019637 | 0.019637 | 0.97234 | -0.53354 | 0.97211 | -0.53808 | 5.3947
99 | 0.007288 | 0.0018266 | -0.0072875 | -0.0018264 | 4.265e-07 | 1.5966e-07 | 0.011156 | 0.011156 | 0.011156 | 0.97211 | -0.53808 | 0.97205 | -0.53931 | 3.0648
100 | -0.0072931 | -0.0018278 | 0.0072944 | 0.0018282 | 1.2989e-06 | 4.7524e-07 | 0.011073 | 0.011073 | 0.011073 | 0.98005 | -0.38252 | 0.98024 | -0.37878 | 3.0421
101 | 0.0033764 | 0.00084616 | -0.0033764 | -0.0008462 | 6.0888e-08 | -3.8883e-08 | 0.0051264 | 0.0051265 | 0.0051265 | 0.98005 | -0.38252 | 0.98003 | -0.38289 | 1.4084
102 | 0.0077927 | 0.0019532 | -0.0077914 | -0.0019527 | 1.3106e-06 | 5.2381e-07 | 0.011827 | 0.011828 | 0.011828 | 0.9804 | -0.37563 | 0.98022 | -0.37916 | 3.2493
103 | 0.0020518 | 0.00051419 | -0.0020518 | -0.00051423 | 1.4018e-08 | -3.9597e-08 | 0.0031147 | 0.0031148 | 0.0031148 | 0.98022 | -0.37916 | 0.98021 | -0.37931 | 0.8557
104 | -0.047859 | -0.01205 | 0.047905 | 0.012079 | 4.578e-05 | 2.9012e-05 | 0.072974 | 0.072974 | 0.072974 | 0.97617 | -0.45812 | 0.97719 | -0.43813 | 20.0478
105 | 0.047859 | 0.01205 | -0.047811 | -0.012019 | 4.8631e-05 | 3.082e-05 | 0.072974 | 0.072974 | 0.072974 | 0.97617 | -0.45812 | 0.97509 | -0.47939 | 20.0478
106 | -0.050052 | -0.012617 | 0.050061 | 0.012623 | 9.0797e-06 | 5.7588e-06 | 0.076243 | 0.076243 | 0.076243 | 0.97719 | -0.43813 | 0.97738 | -0.43434 | 20.9459
107 | 0.043355 | 0.010902 | -0.043333 | -0.010889 | 2.1709e-05 | 1.3729e-05 | 0.066175 | 0.066175 | 0.066175 | 0.97509 | -0.47939 | 0.97455 | -0.48988 | 18.1799
108 | -0.036363 | -0.0091299 | 0.036378 | 0.0091397 | 1.5558e-05 | 9.79e-06 | 0.055576 | 0.055576 | 0.055576 | 0.97369 | -0.50683 | 0.97415 | -0.49787 | 15.2681
109 | 0.030186 | 0.0075819 | -0.030186 | -0.0075818 | 1.8226e-07 | 1.1381e-07 | 0.046137 | 0.046137 | 0.046137 | 0.97369 | -0.50683 | 0.97369 | -0.50696 | 12.6749
110 | -0.039558 | -0.0099368 | 0.039573 | 0.0099463 | 1.5078e-05 | 9.5126e-06 | 0.060434 | 0.060434 | 0.060434 | 0.97415 | -0.49787 | 0.97455 | -0.48988 | 16.6027
111 | 0.028646 | 0.0071958 | -0.028625 | -0.0071832 | 2.0221e-05 | 1.2592e-05 | 0.043783 | 0.043783 | 0.043783 | 0.97369 | -0.50696 | 0.97294 | -0.52176 | 12.0284
112 | 0.024481 | 0.0061445 | -0.024468 | -0.0061365 | 1.2882e-05 | 7.9402e-06 | 0.037444 | 0.037444 | 0.037444 | 0.97294 | -0.52176 | 0.97238 | -0.5328 | 10.2869
113 | 0.0076046 | 0.0019061 | -0.0076028 | -0.0019054 | 1.7575e-06 | 6.9561e-07 | 0.011637 | 0.011637 | 0.011637 | 0.97238 | -0.5328 | 0.97213 | -0.53765 | 3.1971
114 | 0.016863 | 0.0042305 | -0.016859 | -0.0042282 | 3.8672e-06 | 2.283e-06 | 0.025807 | 0.025807 | 0.025807 | 0.97238 | -0.5328 | 0.97213 | -0.53761 | 7.0899
115 | 0.0043681 | 0.0010947 | -0.0043679 | -0.0010947 | 2.1285e-07 | -2.1186e-08 | 0.0066861 | 0.0066861 | 0.0066861 | 0.97213 | -0.53765 | 0.97208 | -0.53868 | 1.8369
116 | 0.016859 | 0.0042282 | -0.016852 | -0.004224 | 7.092e-06 | 4.187e-06 | 0.025807 | 0.025807 | 0.025807 | 0.97213 | -0.53761 | 0.97169 | -0.54644 | 7.09
117 | -0.052287 | -0.01318 | 0.052313 | 0.013197 | 2.6064e-05 | 1.6544e-05 | 0.079632 | 0.079632 | 0.079632 | 0.97738 | -0.43434 | 0.97791 | -0.42393 | 21.8768
118 | 0.010414 | 0.0026104 | -0.010412 | -0.0026096 | 1.7543e-06 | 8.9494e-07 | 0.015948 | 0.015948 | 0.015948 | 0.97169 | -0.54644 | 0.97151 | -0.54998 | 4.3814
119 | 0.0084234 | 0.002111 | -0.0084227 | -0.0021108 | 6.6052e-07 | 2.9172e-07 | 0.012902 | 0.012902 | 0.012902 | 0.97151 | -0.54998 | 0.97143 | -0.55162 | 3.5444
120 | -0.055077 | -0.01389 | 0.05509 | 0.013898 | 1.3021e-05 | 8.2717e-06 | 0.083838 | 0.083838 | 0.083838 | 0.97791 | -0.42393 | 0.97817 | -0.41899 | 23.0323
121 | -0.059071 | -0.014896 | 0.059085 | 0.014904 | 1.329e-05 | 8.4506e-06 | 0.089894 | 0.089894 | 0.089894 | 0.97817 | -0.41899 | 0.97841 | -0.41429 | 24.6961
122 | -0.063662 | -0.016052 | 0.063673 | 0.016058 | 1.0801e-05 | 6.8741e-06 | 0.096856 | 0.096856 | 0.096856 | 0.97841 | -0.41429 | 0.97859 | -0.41074 | 26.6087
123 | -0.066716 | -0.016821 | 0.066794 | 0.01687 | 7.7404e-05 | 4.9287e-05 | 0.10148 | 0.10148 | 0.10148 | 0.97859 | -0.41074 | 0.97983 | -0.38653 | 27.8801
124 | -0.069107 | -0.01745 | 0.069114 | 0.017454 | 6.5051e-06 | 4.1435e-06 | 0.105 | 0.105 | 0.105 | 0.97983 | -0.38653 | 0.97993 | -0.38457 | 28.8452
125 | -0.070351 | -0.017764 | 0.070378 | 0.017782 | 2.74e-05 | 1.7214e-05 | 0.10687 | 0.10687 | 0.10687 | 0.97993 | -0.38457 | 0.98035 | -0.37644 | 14.6806
126 | -0.071765 | -0.018129 | 0.071776 | 0.018136 | 1.0951e-05 | 6.7296e-06 | 0.10898 | 0.10898 | 0.10898 | 0.98035 | -0.37644 | 0.98051 | -0.37326 | 9.9798
127 | 0.038856 | 0.0097843 | -0.038825 | -0.0097644 | 3.1576e-05 | 1.9905e-05 | 0.059054 | 0.059054 | 0.059054 | 0.97936 | -0.39577 | 0.97849 | -0.41278 | 16.2236
128 | 0.011447 | 0.0028699 | -0.011445 | -0.0028687 | 2.2426e-06 | 1.1866e-06 | 0.017393 | 0.017393 | 0.017393 | 0.97936 | -0.39577 | 0.97915 | -0.39988 | 4.7783
129 | 0.0078999 | 0.0019802 | -0.007898 | -0.0019794 | 1.9156e-06 | 7.8031e-07 | 0.012006 | 0.012006 | 0.012006 | 0.97915 | -0.39988 | 0.97889 | -0.40497 | 3.2983
130 | 0.0055341 | 0.001387 | -0.0055339 | -0.0013869 | 1.7768e-07 | 2.955e-08 | 0.0084124 | 0.0084124 | 0.0084124 | 0.97889 | -0.40497 | 0.97886 | -0.40565 | 2.3111
131 | 0.035826 | 0.0090128 | -0.035793 | -0.0089922 | 3.2769e-05 | 2.0603e-05 | 0.054493 | 0.054493 | 0.054493 | 0.97849 | -0.41278 | 0.97752 | -0.43195 | 14.9707
132 | 0.032742 | 0.0082275 | -0.032715 | -0.0082108 | 2.6639e-05 | 1.6691e-05 | 0.049849 | 0.049849 | 0.049849 | 0.97752 | -0.43195 | 0.97665 | -0.449 | 13.6947
133 | 0.0065221 | 0.0016345 | -0.0065203 | -0.001634 | 1.8456e-06 | 5.5771e-07 | 0.0099371 | 0.0099373 | 0.0099373 | 0.97665 | -0.449 | 0.97634 | -0.45495 | 2.73
134 | 0.026193 | 0.0065762 | -0.026171 | -0.0065625 | 2.2097e-05 | 1.368e-05 | 0.039912 | 0.039912 | 0.039912 | 0.97665 | -0.449 | 0.97575 | -0.4667 | 10.9648
135 | 0.0048794 | 0.0012227 | -0.0048792 | -0.0012227 | 1.4214e-07 | 6.9696e-09 | 0.0074741 | 0.0074741 | 0.0074741 | 0.97143 | -0.55162 | 0.97139 | -0.55224 | 2.0533
136 | 0.0027571 | 0.00069084 | -0.002757 | -0.00069097 | 1.0528e-07 | -1.2746e-07 | 0.0042234 | 0.0042234 | 0.0042234 | 0.97139 | -0.55224 | 0.97135 | -0.55304 | 1.1603
137 | -0.012107 | -0.0030344 | 0.01211 | 0.0030356 | 2.2356e-06 | 1.2128e-06 | 0.018473 | 0.018473 | 0.018473 | 0.97523 | -0.47686 | 0.97543 | -0.47299 | 5.0751
138 | -0.026163 | -0.0065577 | 0.026171 | 0.0065625 | 7.8315e-06 | 4.8485e-06 | 0.039912 | 0.039912 | 0.039912 | 0.97543 | -0.47299 | 0.97575 | -0.4667 | 10.9648
139 | 0.0035963 | 0.00090115 | -0.003596 | -0.00090125 | 2.1546e-07 | -1.0128e-07 | 0.0054809 | 0.005481 | 0.005481 | 0.97634 | -0.45495 | 0.97628 | -0.4562 | 1.5058

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4422 | 0.11345

## res_load
| p_mw | q_mvar
0 | 0.0062173 | 0.0015582
1 | 0.0038495 | 0.00096479
2 | 0.0034502 | 0.0008647
3 | 0.0045774 | 0.0011472
4 | 0.0037999 | 0.00095235
5 | 0.0059716 | 0.0014966
6 | 0.0016589 | 0.00041576
7 | 0.0038704 | 0.00097003
8 | 0.0048476 | 0.0012149
9 | 0.0034578 | 0.00086661
10 | 0.0037371 | 0.00093661
11 | 0.0031955 | 0.00080087
12 | 0.012697 | 0.0031822
13 | 0.025031 | 0.0062734
14 | 0.0015644 | 0.00039207
15 | 0.008598 | 0.0021548
16 | 0.001624 | 0.00040702
17 | 0.0021402 | 0.00053638
18 | 0.0030048 | 0.00075308
19 | 0.0023294 | 0.00058381
20 | 0.0022451 | 0.00056269
21 | 0.0017633 | 0.00044193
22 | 0.0019944 | 0.00049984
23 | 0.0030464 | 0.00076349
24 | 0.0018493 | 0.00046348
25 | 0.0037814 | 0.00094772
26 | 0.0069729 | 0.0017476
27 | 0.0048788 | 0.0012227
28 | 0.0028341 | 0.00071029
29 | 0.00692 | 0.0017343
30 | 0.0014085 | 0.000353
31 | 0.004844 | 0.001214
32 | 0.0032723 | 0.00082011
33 | 0.0051763 | 0.0012973
34 | 0.0025752 | 0.0006454
35 | 0.0031996 | 0.0008019
36 | 0.0066358 | 0.0016631
37 | 0.0056821 | 0.0014241
38 | 0.0017776 | 0.00044551
39 | 0.0039202 | 0.0009825
40 | 0.0052611 | 0.0013185
41 | 0.0022421 | 0.00056191
42 | 0.0019008 | 0.00047639
43 | 0.0016371 | 0.00041031
44 | 0.0024877 | 0.00062347
45 | 0.0020914 | 0.00052416
46 | 0.0011759 | 0.00029471
47 | 0.005024 | 0.0012591
48 | 0.0050306 | 0.0012608
49 | 0.001233 | 0.00030901
50 | 0.0017913 | 0.00044895
51 | 0.0033024 | 0.00082767
52 | 0.0031394 | 0.00078682
53 | 0.0016898 | 0.00042351
54 | 0.0011727 | 0.00029391
55 | 0.0016047 | 0.00040217
56 | 0.00285 | 0.00071427
57 | 0.0030564 | 0.000766
58 | 0.0018527 | 0.00046433
59 | 0.00091064 | 0.00022823
60 | 0.002613 | 0.00065488
61 | 0.0010764 | 0.00026976
62 | 0.0015804 | 0.0003961
63 | 0.0017759 | 0.00044509
64 | 0.003149 | 0.00078921
65 | 0.0017655 | 0.00044249
66 | 0.0045897 | 0.0011503
67 | 0.0024377 | 0.00061095
68 | 0.0035604 | 0.00089231
69 | 0.0020704 | 0.00051888
70 | 0.0047776 | 0.0011974
71 | 0.0035655 | 0.00089359
72 | 0.0040648 | 0.0010187
73 | 0.0030686 | 0.00076906
74 | 0.0031597 | 0.00079188
75 | 0.0019577 | 0.00049064
76 | 0.0039617 | 0.00099289
77 | 0.0055405 | 0.0013886
78 | 0.0072875 | 0.0018264
79 | 0.0039166 | 0.0009816
80 | 0.0018472 | 0.00046295
81 | 0.0033764 | 0.0008462
82 | 0.0057395 | 0.0014385
83 | 0.0021468 | 0.00053805
84 | 0.0044557 | 0.0011167
85 | 0.0020518 | 0.00051423
86 | 0.0061766 | 0.001548
87 | 0.0031803 | 0.00079705
88 | 0.0015401 | 0.000386
89 | 0.00376 | 0.00094233
90 | 0.0041447 | 0.0010388
91 | 0.0032347 | 0.0008107
92 | 0.0022257 | 0.00055782
93 | 0.0043679 | 0.0010947
94 | 0.0064381 | 0.0016136
95 | 0.0019891 | 0.00049851
96 | 0.0027642 | 0.00069277
97 | 0.0039812 | 0.00099779
98 | 0.0045776 | 0.0011472
99 | 0.0030435 | 0.00076276
100 | 0.0023133 | 0.00057976
101 | 0.0012369 | 0.00030999
102 | 0.0013866 | 0.00034752
103 | 0.0022613 | 0.00056672
104 | 0.0035451 | 0.00088847
105 | 0.0023639 | 0.00059244
106 | 0.0055339 | 0.0013869
107 | 0.002999 | 0.00075163
108 | 0.0030513 | 0.00076474
109 | 0.0035434 | 0.00088805
110 | 0.0021222 | 0.00053186
111 | 0.002757 | 0.00069097
112 | 0.012107 | 0.0030344
113 | 0.014053 | 0.0035221
114 | 0.002924 | 0.00073283
115 | 0.003596 | 0.00090125

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1