## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5219-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5219-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5219-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5219-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5219-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5219-4_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_5219-4_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_5219-4_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5219-4_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_5219-4_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_5219-4_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5219-4_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_5219-4_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_5219-4_0_4_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_5219-4_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_5219-4_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_5219-4_0_4_node_90 | 0.4 | n |  | TRUE
17 | bus_LV_5219-4_0_4_node_89 | 0.4 | n |  | TRUE
18 | bus_LV_5219-4_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_5219-4_0_4_node_121 | 0.4 | n |  | TRUE
20 | bus_LV_5219-4_0_4_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_5219-4_0_4_node_58 | 0.4 | n |  | TRUE
22 | bus_LV_5219-4_0_4_node_56 | 0.4 | n |  | TRUE
23 | bus_LV_5219-4_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_5219-4_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_5219-4_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_5219-4_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_5219-4_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_5219-4_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_5219-4_0_4_node_49 | 0.4 | n |  | TRUE
30 | bus_LV_5219-4_0_4_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_5219-4_0_4_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_5219-4_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_5219-4_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_5219-4_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_5219-4_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_5219-4_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_5219-4_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_5219-4_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_5219-4_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_5219-4_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_5219-4_0_4_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_5219-4_0_4_node_69 | 0.4 | n |  | TRUE
43 | bus_LV_5219-4_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_5219-4_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_5219-4_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_5219-4_0_4_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_5219-4_0_4_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_5219-4_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_5219-4_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_5219-4_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_5219-4_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_5219-4_0_4_node_70 | 0.4 | n |  | TRUE
53 | bus_LV_5219-4_0_4_node_122 | 0.4 | n |  | TRUE
54 | bus_LV_5219-4_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_5219-4_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_5219-4_0_4_node_113 | 0.4 | n |  | TRUE
57 | bus_LV_5219-4_0_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_5219-4_0_4_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_5219-4_0_4_node_86 | 0.4 | n |  | TRUE
60 | bus_LV_5219-4_0_4_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_5219-4_0_4_node_84 | 0.4 | n |  | TRUE
62 | bus_LV_5219-4_0_4_node_101 | 0.4 | n |  | TRUE
63 | bus_LV_5219-4_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_5219-4_0_4_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_5219-4_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_5219-4_0_4_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_5219-4_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_5219-4_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_5219-4_0_4_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_5219-4_0_4_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_5219-4_0_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_5219-4_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_5219-4_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_5219-4_0_4_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_5219-4_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_5219-4_0_4_node_68 | 0.4 | n |  | TRUE
77 | bus_LV_5219-4_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_5219-4_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_5219-4_0_4_node_120 | 0.4 | n |  | TRUE
80 | bus_LV_5219-4_0_4_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_5219-4_0_4_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_5219-4_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_5219-4_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_5219-4_0_4_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_5219-4_0_4_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_5219-4_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_5219-4_0_4_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_5219-4_0_4_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_5219-4_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_5219-4_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_5219-4_0_4_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_5219-4_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_5219-4_0_4_node_123 | 0.4 | n |  | TRUE
94 | bus_LV_5219-4_0_4_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_5219-4_0_4_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_5219-4_0_4_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_5219-4_0_4_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_5219-4_0_4_node_100 | 0.4 | n |  | TRUE
99 | bus_LV_5219-4_0_4_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_5219-4_0_4_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_5219-4_0_4_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_5219-4_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_5219-4_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_5219-4_0_4_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_5219-4_0_4_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_5219-4_0_4_node_112 | 0.4 | n |  | TRUE
107 | bus_LV_5219-4_0_4_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_5219-4_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_5219-4_0_4_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_5219-4_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_5219-4_0_4_node_110 | 0.4 | n |  | TRUE
112 | bus_LV_5219-4_0_4_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_5219-4_0_4_node_119 | 0.4 | n |  | TRUE
114 | bus_LV_5219-4_0_4_node_118 | 0.4 | n |  | TRUE
115 | bus_LV_5219-4_0_4_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_5219-4_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_5219-4_0_4_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_5219-4_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_5219-4_0_4_node_117 | 0.4 | n |  | TRUE
120 | bus_MV_68_0_node_46 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5219-4_0_4_load_0 | 0 | 0.0044921 | 0.0011258 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5219-4_0_4_load_1 | 1 | 0.0029627 | 0.00074253 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5219-4_0_4_load_2 | 2 | 0.0031734 | 0.00079534 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5219-4_0_4_load_3 | 3 | 0.0027343 | 0.00068527 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5219-4_0_4_load_4 | 4 | 0.0027716 | 0.00069464 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5219-4_0_4_load_6 | 6 | 0.0024108 | 0.0006042 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5219-4_0_4_load_5 | 7 | 0.0031471 | 0.00078873 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5219-4_0_4_load_7 | 9 | 0.0063496 | 0.0015914 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5219-4_0_4_load_8 | 10 | 0.0021853 | 0.00054768 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5219-4_0_4_load_9 | 11 | 0.0051514 | 0.0012911 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5219-4_0_4_load_17 | 12 | 0.0035354 | 0.00088606 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5219-4_0_4_load_10 | 14 | 0.015362 | 0.00385 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5219-4_0_4_load_13 | 15 | 0.0021339 | 0.0005348 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5219-4_0_4_load_90 | 16 | 0.0036838 | 0.00092326 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5219-4_0_4_load_89 | 17 | 0.01091 | 0.0027343 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5219-4_0_4_load_16 | 18 | 0.0026655 | 0.00066805 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5219-4_0_4_load_121 | 19 | 0.0019951 | 0.00050001 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5219-4_0_4_load_63 | 20 | 0.0050503 | 0.0012657 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5219-4_0_4_load_58 | 21 | 0.0056609 | 0.0014188 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5219-4_0_4_load_56 | 22 | 0.0019557 | 0.00049014 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5219-4_0_4_load_19 | 23 | 0.0033392 | 0.00083689 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5219-4_0_4_load_23 | 27 | 0.011109 | 0.0027843 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5219-4_0_4_load_24 | 28 | 0.0036922 | 0.00092535 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5219-4_0_4_load_49 | 29 | 0.0056464 | 0.0014151 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5219-4_0_4_load_46 | 30 | 0.0035733 | 0.00089556 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5219-4_0_4_load_50 | 31 | 0.010752 | 0.0026948 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5219-4_0_4_load_25 | 33 | 0.0039228 | 0.00098314 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5219-4_0_4_load_26 | 34 | 0.0087438 | 0.0021914 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5219-4_0_4_load_28 | 36 | 0.0028054 | 0.00070309 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5219-4_0_4_load_30 | 38 | 0.0021715 | 0.00054422 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5219-4_0_4_load_31 | 39 | 0.0043018 | 0.0010781 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5219-4_0_4_load_38 | 41 | 0.0023175 | 0.00058082 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5219-4_0_4_load_69 | 42 | 0.0029293 | 0.00073416 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5219-4_0_4_load_32 | 43 | 0.001531 | 0.00038371 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5219-4_0_4_load_33 | 44 | 0.002885 | 0.00072305 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5219-4_0_4_load_39 | 45 | 0.01316 | 0.0032983 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5219-4_0_4_load_43 | 47 | 0.0028458 | 0.00071322 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5219-4_0_4_load_44 | 48 | 0.0093487 | 0.002343 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5219-4_0_4_load_34 | 49 | 0.0044214 | 0.0011081 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5219-4_0_4_load_36 | 50 | 0.0053273 | 0.0013351 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5219-4_0_4_load_70 | 52 | 0.0060624 | 0.0015194 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5219-4_0_4_load_122 | 53 | 0.011938 | 0.0029919 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5219-4_0_4_load_41 | 54 | 0.010567 | 0.0026484 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5219-4_0_4_load_113 | 56 | 0.0090184 | 0.0022602 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5219-4_0_4_load_40 | 57 | 0.0049294 | 0.0012354 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5219-4_0_4_load_106 | 58 | 0.006949 | 0.0017416 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5219-4_0_4_load_88 | 60 | 0.0099318 | 0.0024891 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5219-4_0_4_load_84 | 61 | 0.0047913 | 0.0012008 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5219-4_0_4_load_45 | 63 | 0.0024084 | 0.00060361 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5219-4_0_4_load_48 | 64 | 0.0035119 | 0.00088017 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5219-4_0_4_load_51 | 65 | 0.0036735 | 0.00092067 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5219-4_0_4_load_52 | 66 | 0.012187 | 0.0030543 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5219-4_0_4_load_53 | 67 | 0.0078869 | 0.0019766 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5219-4_0_4_load_54 | 68 | 0.0052642 | 0.0013193 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5219-4_0_4_load_55 | 69 | 0.0125 | 0.0031327 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5219-4_0_4_load_57 | 73 | 0.0034081 | 0.00085416 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5219-4_0_4_load_59 | 74 | 0.0045198 | 0.0011328 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5219-4_0_4_load_60 | 75 | 0.0029008 | 0.000727 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5219-4_0_4_load_68 | 76 | 0.0070505 | 0.001767 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5219-4_0_4_load_64 | 77 | 0.0024677 | 0.00061846 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5219-4_0_4_load_65 | 78 | 0.0068642 | 0.0017203 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5219-4_0_4_load_120 | 79 | 0.00725 | 0.001817 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5219-4_0_4_load_71 | 80 | 0.0067561 | 0.0016932 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5219-4_0_4_load_72 | 81 | 0.0093237 | 0.0023367 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5219-4_0_4_load_76 | 83 | 0.0027118 | 0.00067963 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5219-4_0_4_load_80 | 84 | 0.0038944 | 0.00097604 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5219-4_0_4_load_78 | 87 | 0.0060711 | 0.0015216 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5219-4_0_4_load_79 | 88 | 0.021851 | 0.0054764 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5219-4_0_4_load_81 | 89 | 0.0086195 | 0.0021602 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5219-4_0_4_load_82 | 90 | 0.0080092 | 0.0020073 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5219-4_0_4_load_83 | 92 | 0.0038711 | 0.00097019 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5219-4_0_4_load_123 | 93 | 0.017905 | 0.0044873 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5219-4_0_4_load_99 | 95 | 0.005629 | 0.0014108 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5219-4_0_4_load_97 | 96 | 0.0024727 | 0.00061971 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5219-4_0_4_load_95 | 97 | 0.0055966 | 0.0014026 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5219-4_0_4_load_100 | 98 | 0.012686 | 0.0031795 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5219-4_0_4_load_91 | 99 | 0.0047285 | 0.0011851 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5219-4_0_4_load_92 | 100 | 0.0060256 | 0.0015102 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5219-4_0_4_load_93 | 101 | 0.0047433 | 0.0011888 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5219-4_0_4_load_94 | 102 | 0.003694 | 0.00092581 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5219-4_0_4_load_98 | 103 | 0.0026178 | 0.00065607 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5219-4_0_4_load_102 | 105 | 0.010354 | 0.0025951 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5219-4_0_4_load_103 | 107 | 0.0094964 | 0.00238 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5219-4_0_4_load_109 | 109 | 0.0038996 | 0.00097733 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5219-4_0_4_load_107 | 110 | 0.0057324 | 0.0014367 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5219-4_0_4_load_110 | 111 | 0.0046866 | 0.0011746 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5219-4_0_4_load_108 | 112 | 0.0027745 | 0.00069534 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5219-4_0_4_load_119 | 113 | 0.012188 | 0.0030545 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5219-4_0_4_load_118 | 114 | 0.0066323 | 0.0016622 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5219-4_0_4_load_111 | 115 | 0.0019813 | 0.00049655 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5219-4_0_4_load_116 | 116 | 0.0066928 | 0.0016774 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5219-4_0_4_load_114 | 117 | 0.006164 | 0.0015448 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5219-4_0_4_load_115 | 118 | 0.0035283 | 0.00088426 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5219-4_0_4_load_117 | 119 | 0.0029294 | 0.00073417 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5219-4_0_4_line_0 |  | 0 | 1 | 0.016987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5219-4_0_4_line_1 |  | 0 | 2 | 0.022729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5219-4_0_4_line_2 |  | 1 | 3 | 0.013191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5219-4_0_4_line_3 |  | 2 | 4 | 0.037458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5219-4_0_4_line_4 |  | 3 | 5 | 0.019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5219-4_0_4_line_5 |  | 4 | 7 | 0.00060053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5219-4_0_4_line_6 |  | 5 | 8 | 0.055152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5219-4_0_4_line_7 |  | 6 | 7 | 0.031872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5219-4_0_4_line_8 |  | 8 | 15 | 0.036454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5219-4_0_4_line_9 |  | 8 | 14 | 0.064375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5219-4_0_4_line_10 |  | 9 | 10 | 0.063414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5219-4_0_4_line_11 |  | 10 | 11 | 0.00048823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5219-4_0_4_line_12 |  | 11 | 12 | 0.034747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5219-4_0_4_line_13 |  | 12 | 13 | 0.018245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5219-4_0_4_line_14 |  | 13 | 21 | 0.037939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5219-4_0_4_line_15 |  | 15 | 16 | 0.046189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5219-4_0_4_line_16 |  | 16 | 17 | 0.0071277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5219-4_0_4_line_17 |  | 17 | 99 | 0.0061172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5219-4_0_4_line_18 |  | 18 | 19 | 0.08694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5219-4_0_4_line_19 |  | 19 | 20 | 0.0067102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5219-4_0_4_line_20 |  | 20 | 72 | 0.0077176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5219-4_0_4_line_21 |  | 21 | 22 | 0.030293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5219-4_0_4_line_22 |  | 22 | 73 | 0.010589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5219-4_0_4_line_23 |  | 23 | 24 | 0.060946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5219-4_0_4_line_24 |  | 23 | 25 | 0.045617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5219-4_0_4_line_25 |  | 24 | 26 | 0.020363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5219-4_0_4_line_26 |  | 25 | 27 | 0.060062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5219-4_0_4_line_27 |  | 25 | 28 | 0.079925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5219-4_0_4_line_28 |  | 26 | 29 | 0.061692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5219-4_0_4_line_29 |  | 26 | 30 | 0.010179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5219-4_0_4_line_30 |  | 29 | 31 | 0.0039478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5219-4_0_4_line_31 |  | 30 | 32 | 0.022214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5219-4_0_4_line_32 |  | 31 | 65 | 0.038245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5219-4_0_4_line_33 |  | 32 | 64 | 0.0031736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5219-4_0_4_line_34 |  | 33 | 34 | 0.0009622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5219-4_0_4_line_35 |  | 33 | 35 | 0.018597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5219-4_0_4_line_36 |  | 34 | 36 | 0.0082971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5219-4_0_4_line_37 |  | 35 | 37 | 0.006526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_5219-4_0_4_line_38 |  | 35 | 38 | 0.0061784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_5219-4_0_4_line_39 |  | 36 | 39 | 0.0078222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5219-4_0_4_line_40 |  | 37 | 40 | 0.003538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_5219-4_0_4_line_41 |  | 37 | 41 | 0.014044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5219-4_0_4_line_42 |  | 38 | 42 | 0.012138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_5219-4_0_4_line_43 |  | 39 | 43 | 0.001071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5219-4_0_4_line_44 |  | 40 | 44 | 0.0056333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_5219-4_0_4_line_45 |  | 41 | 45 | 0.0042006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5219-4_0_4_line_46 |  | 42 | 46 | 0.0018133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_5219-4_0_4_line_47 |  | 43 | 47 | 0.0024385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5219-4_0_4_line_48 |  | 44 | 49 | 0.010835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_5219-4_0_4_line_49 |  | 45 | 57 | 0.0036507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5219-4_0_4_line_50 |  | 46 | 52 | 0.010718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_5219-4_0_4_line_51 |  | 46 | 78 | 0.0071147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5219-4_0_4_line_52 |  | 47 | 48 | 0.0017536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5219-4_0_4_line_53 |  | 48 | 63 | 0.022631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5219-4_0_4_line_54 |  | 49 | 50 | 0.013244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_5219-4_0_4_line_55 |  | 51 | 52 | 0.010618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_5219-4_0_4_line_56 |  | 51 | 53 | 0.0099344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_5219-4_0_4_line_57 |  | 53 | 56 | 0.016543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_5219-4_0_4_line_58 |  | 54 | 55 | 0.0042018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5219-4_0_4_line_59 |  | 55 | 58 | 0.010509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5219-4_0_4_line_60 |  | 56 | 104 | 0.0078998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_5219-4_0_4_line_61 |  | 58 | 62 | 0.0085877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5219-4_0_4_line_62 |  | 59 | 60 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5219-4_0_4_line_63 |  | 59 | 61 | 0.0078998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5219-4_0_4_line_64 |  | 60 | 93 | 0.0035704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5219-4_0_4_line_65 |  | 61 | 85 | 0.010828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5219-4_0_4_line_66 |  | 62 | 104 | 0.014637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_5219-4_0_4_line_67 |  | 62 | 105 | 0.0093382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5219-4_0_4_line_68 |  | 62 | 98 | 0.013116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_5219-4_0_4_line_69 |  | 63 | 64 | 0.010569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5219-4_0_4_line_70 |  | 65 | 66 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5219-4_0_4_line_71 |  | 67 | 68 | 0.0018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5219-4_0_4_line_72 |  | 68 | 69 | 0.0065047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5219-4_0_4_line_73 |  | 69 | 70 | 0.032111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5219-4_0_4_line_74 |  | 70 | 71 | 0.003824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5219-4_0_4_line_75 |  | 70 | 72 | 0.004621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5219-4_0_4_line_76 |  | 71 | 76 | 0.0093053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5219-4_0_4_line_77 |  | 71 | 77 | 0.0020529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5219-4_0_4_line_78 |  | 72 | 75 | 0.0053286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5219-4_0_4_line_79 |  | 73 | 74 | 0.0076636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5219-4_0_4_line_80 |  | 74 | 75 | 0.0050291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5219-4_0_4_line_81 |  | 76 | 79 | 0.014662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5219-4_0_4_line_82 |  | 77 | 78 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5219-4_0_4_line_83 |  | 80 | 81 | 0.0037293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5219-4_0_4_line_84 |  | 81 | 82 | 0.0051689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5219-4_0_4_line_85 |  | 82 | 83 | 0.0053933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5219-4_0_4_line_86 |  | 83 | 86 | 0.007305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5219-4_0_4_line_87 |  | 84 | 85 | 0.0091063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5219-4_0_4_line_88 |  | 85 | 91 | 0.015357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5219-4_0_4_line_89 |  | 86 | 87 | 0.0064509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5219-4_0_4_line_90 |  | 86 | 88 | 0.016885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5219-4_0_4_line_91 |  | 87 | 89 | 0.0065231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5219-4_0_4_line_92 |  | 89 | 90 | 0.0053972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5219-4_0_4_line_93 |  | 90 | 92 | 0.0077022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5219-4_0_4_line_94 |  | 91 | 94 | 0.013018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5219-4_0_4_line_95 |  | 91 | 95 | 0.0047366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_5219-4_0_4_line_96 |  | 92 | 93 | 0.0072753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5219-4_0_4_line_97 |  | 94 | 96 | 0.0037086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5219-4_0_4_line_98 |  | 94 | 97 | 0.0025638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5219-4_0_4_line_99 |  | 95 | 98 | 0.0075749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_5219-4_0_4_line_100 |  | 96 | 103 | 0.01812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5219-4_0_4_line_101 |  | 97 | 102 | 0.0052686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5219-4_0_4_line_102 |  | 99 | 100 | 0.0063172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5219-4_0_4_line_103 |  | 100 | 101 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5219-4_0_4_line_104 |  | 101 | 102 | 0.0061133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5219-4_0_4_line_105 |  | 104 | 106 | 0.01062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5219-4_0_4_line_106 |  | 105 | 107 | 0.0010578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5219-4_0_4_line_107 |  | 106 | 113 | 0.017166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5219-4_0_4_line_108 |  | 106 | 114 | 0.0097791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5219-4_0_4_line_109 |  | 107 | 108 | 0.0085698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5219-4_0_4_line_110 |  | 108 | 109 | 0.0039718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_5219-4_0_4_line_111 |  | 108 | 110 | 0.014408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5219-4_0_4_line_112 |  | 109 | 111 | 0.0088331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5219-4_0_4_line_113 |  | 110 | 112 | 0.00072803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5219-4_0_4_line_114 |  | 111 | 115 | 0.012831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5219-4_0_4_line_115 |  | 114 | 116 | 0.00096197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5219-4_0_4_line_116 |  | 116 | 117 | 0.015346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5219-4_0_4_line_117 |  | 117 | 118 | 0.0010735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5219-4_0_4_line_118 |  | 118 | 119 | 0.0063731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5219-4_0_4_trafo_36 | 0.63 MVA 20/0.4 kV | 120 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2720279.6543 | 1088152.4115 | 2720262.6733 | 1088151.9787
1 | 2720279.6543 | 1088152.4115 | 2720302.3758 | 1088152.9905
2 | 2720262.6733 | 1088151.9787 | 2720252.2482 | 1088151.7131 | 2720249.607 | 1088150.9029
3 | 2720302.3758 | 1088152.9905 | 2720300.4029 | 1088190.3967
4 | 2720231.4426 | 1088145.3309 | 2720249.607 | 1088150.9029
5 | 2720300.4029 | 1088190.3967 | 2720299.8044 | 1088190.4461
6 | 2720231.4426 | 1088145.3309 | 2720230.3798 | 1088138.6497 | 2720228.1523 | 1088135.9482 | 2720224.7849 | 1088133.2131 | 2720203.9935 | 1088120.2156 | 2720189.3719 | 1088113.3998
7 | 2720299.8044 | 1088190.4461 | 2720268.0409 | 1088193.0697
8 | 2720189.3719 | 1088113.3998 | 2720193.7258 | 1088104.2905 | 2720195.0514 | 1088087.0711 | 2720192.0466 | 1088082.4752 | 2720192.456 | 1088078.9024
9 | 2720189.3719 | 1088113.3998 | 2720226.0536 | 1088116.1261 | 2720229.8632 | 1088117.291 | 2720238.2327 | 1088124.05 | 2720240.9529 | 1088124.593 | 2720251 | 1088123.8249
10 | 2720588.5631 | 1088000.809 | 2720583.7802 | 1088000.753 | 2720568.8056 | 1088002.7467 | 2720526.247 | 1088011.8646
11 | 2720526.247 | 1088011.8646 | 2720525.7696 | 1088011.9669
12 | 2720525.7696 | 1088011.9669 | 2720508.0939 | 1088015.7538 | 2720501.7165 | 1088015.7498 | 2720491.6027 | 1088013.8403
13 | 2720473.5636 | 1088012.4903 | 2720481.5354 | 1088011.9032 | 2720488.0971 | 1088013.1784 | 2720491.6027 | 1088013.8403
14 | 2720473.5636 | 1088012.4903 | 2720462.2553 | 1088010.7431 | 2720439.798 | 1088012.5333 | 2720436.0506 | 1088013.8394
15 | 2720192.456 | 1088078.9024 | 2720193.6778 | 1088068.2418 | 2720222.8455 | 1088073.1435 | 2720223.4853 | 1088067.2965
16 | 2720224.6841 | 1088060.7026 | 2720224.2089 | 1088060.6838 | 2720223.4853 | 1088067.2965
17 | 2720224.6841 | 1088060.7026 | 2720230.7965 | 1088060.9446
18 | 2720381.6407 | 1088041.6026 | 2720429.028 | 1088114.4924
19 | 2720381.6407 | 1088041.6026 | 2720379.6294 | 1088035.201
20 | 2720379.4745 | 1088027.5064 | 2720379.4791 | 1088034.7227 | 2720379.6294 | 1088035.201
21 | 2720407.7418 | 1088024.4586 | 2720412.3769 | 1088023.2541 | 2720423.3451 | 1088018.2675 | 2720436.0506 | 1088013.8394
22 | 2720407.7418 | 1088024.4586 | 2720401.4043 | 1088026.1057 | 2720397.4196 | 1088026.7789
23 | 2720358.1863 | 1087894.9138 | 2720325.0694 | 1087873.4996 | 2720307.5955 | 1087860.9577
24 | 2720264.5063 | 1087856.9801 | 2720270.9832 | 1087855.0956 | 2720284.9593 | 1087852.9925 | 2720294.5559 | 1087853.4269 | 2720301.4766 | 1087856.5658 | 2720307.5955 | 1087860.9577
25 | 2720371.5529 | 1087910.2779 | 2720364.9827 | 1087901.9754 | 2720358.1863 | 1087894.9138
26 | 2720264.5063 | 1087856.9801 | 2720254.0478 | 1087855.7949 | 2720244.1763 | 1087851.2078 | 2720240.2066 | 1087844.7915 | 2720238.8475 | 1087836.6144 | 2720240.0666 | 1087832.2465 | 2720244.6973 | 1087826.8119 | 2720254.0908 | 1087820.6487
27 | 2720264.5063 | 1087856.9801 | 2720236.2712 | 1087865.6841 | 2720230.2991 | 1087865.1881 | 2720226.2455 | 1087861.839 | 2720214.6903 | 1087843.9092 | 2720209.3398 | 1087841.4018 | 2720197.5674 | 1087838.7786
28 | 2720371.5529 | 1087910.2779 | 2720347.897 | 1087916.1588 | 2720333.3073 | 1087923.0086 | 2720315.8532 | 1087935.0388
29 | 2720371.5529 | 1087910.2779 | 2720377.1461 | 1087918.7821
30 | 2720315.8532 | 1087935.0388 | 2720312.6026 | 1087937.2792
31 | 2720386.216 | 1087938.9325 | 2720383.191 | 1087929.4772 | 2720377.4655 | 1087919.2678 | 2720377.1461 | 1087918.7821
32 | 2720312.6026 | 1087937.2792 | 2720300.8453 | 1087945.3829 | 2720291.0843 | 1087951.3053 | 2720279.5583 | 1087956.2669
33 | 2720386.216 | 1087938.9325 | 2720386.5222 | 1087942.0913
34 | 2720356.5467 | 1087984.1679 | 2720355.8238 | 1087984.8029
35 | 2720341.8507 | 1087997.0743 | 2720355.8238 | 1087984.8029
36 | 2720362.781 | 1087978.6929 | 2720356.5467 | 1087984.1679
37 | 2720336.8941 | 1088001.3349 | 2720341.8507 | 1087997.0743
38 | 2720341.8507 | 1087997.0743 | 2720345.7446 | 1088001.8713
39 | 2720362.781 | 1087978.6929 | 2720366.9116 | 1087975.0653 | 2720368.6738 | 1087973.5489
40 | 2720333.818 | 1088003.0976 | 2720336.8941 | 1088001.3349
41 | 2720336.8941 | 1088001.3349 | 2720328.952 | 1087989.7526
42 | 2720353.3941 | 1088011.2949 | 2720345.7446 | 1088001.8713
43 | 2720368.6738 | 1087973.5489 | 2720369.4857 | 1087972.8504
44 | 2720333.818 | 1088003.0976 | 2720328.4186 | 1088004.7041
45 | 2720328.952 | 1087989.7526 | 2720326.5765 | 1087986.2882
46 | 2720354.537 | 1088012.7028 | 2720353.3941 | 1088011.2949
47 | 2720371.334 | 1087971.2599 | 2720369.4857 | 1087972.8504
48 | 2720328.4186 | 1088004.7041 | 2720318.034 | 1088007.794
49 | 2720324.5119 | 1087983.2774 | 2720326.5765 | 1087986.2882
50 | 2720354.537 | 1088012.7028 | 2720344.3866 | 1088016.1437
51 | 2720354.537 | 1088012.7028 | 2720359.8609 | 1088017.4225
52 | 2720371.334 | 1087971.2599 | 2720372.6633 | 1087970.1161
53 | 2720372.6633 | 1087970.1161 | 2720380.6294 | 1087963.2615 | 2720385.725 | 1087954.7229 | 2720386.055 | 1087952.5694
54 | 2720318.034 | 1088007.794 | 2720305.3399 | 1088011.5711
55 | 2720334.3304 | 1088019.5527 | 2720344.3866 | 1088016.1437
56 | 2720334.3304 | 1088019.5527 | 2720324.9416 | 1088022.7997
57 | 2720310.4099 | 1088030.6876 | 2720324.3859 | 1088022.9919 | 2720324.9416 | 1088022.7997
58 | 2720284.0963 | 1088017.8921 | 2720288.1236 | 1088016.6938
59 | 2720284.0963 | 1088017.8921 | 2720286.7558 | 1088028.0591
60 | 2720303.4898 | 1088034.4981 | 2720310.4099 | 1088030.6876
61 | 2720288.9291 | 1088036.3673 | 2720286.7558 | 1088028.0591
62 | 2720264.6712 | 1088022.8896 | 2720261.9155 | 1088013.2505
63 | 2720264.6712 | 1088022.8896 | 2720256.9995 | 1088024.774
64 | 2720261.9155 | 1088013.2505 | 2720260.934 | 1088009.8177 | 2720260.934 | 1088009.8177
65 | 2720248.7567 | 1088031.6259 | 2720256.0407 | 1088025.0095 | 2720256.9995 | 1088024.774
66 | 2720288.9291 | 1088036.3673 | 2720303.4898 | 1088034.4981
67 | 2720288.9291 | 1088036.3673 | 2720289.9412 | 1088045.6505
68 | 2720288.9291 | 1088036.3673 | 2720275.8137 | 1088036.2112
69 | 2720386.055 | 1087952.5694 | 2720386.9634 | 1087946.6417 | 2720386.5222 | 1087942.0913
70 | 2720265.0956 | 1087962.4772 | 2720265.4258 | 1087962.3506 | 2720279.5583 | 1087956.2669
71 | 2720391.2048 | 1087998.9445 | 2720389.6324 | 1087999.8574
72 | 2720384.0069 | 1088003.1232 | 2720389.6324 | 1087999.8574
73 | 2720375.0234 | 1088026.2174 | 2720378.8486 | 1088019.1436 | 2720389.5902 | 1088013.8523 | 2720388.0132 | 1088010.819 | 2720384.0069 | 1088003.1232 | 2720384.0069 | 1088003.1232
74 | 2720375.0234 | 1088026.2174 | 2720371.3357 | 1088025.166
75 | 2720375.0234 | 1088026.2174 | 2720379.4745 | 1088027.5064
76 | 2720371.3357 | 1088025.166 | 2720362.5563 | 1088028.2499
77 | 2720371.3357 | 1088025.166 | 2720369.5815 | 1088024.0997
78 | 2720379.4745 | 1088027.5064 | 2720384.7946 | 1088027.806
79 | 2720397.4196 | 1088026.7789 | 2720393.215 | 1088027.4892 | 2720389.8187 | 1088027.6355
80 | 2720384.7946 | 1088027.806 | 2720385.2559 | 1088027.832 | 2720389.8187 | 1088027.6355
81 | 2720348.7228 | 1088033.1091 | 2720362.5563 | 1088028.2499
82 | 2720369.5815 | 1088024.0997 | 2720362.6192 | 1088019.8677 | 2720359.8609 | 1088017.4225
83 | 2720219.0661 | 1088028.2453 | 2720222.7811 | 1088028.5715
84 | 2720227.9302 | 1088029.0238 | 2720222.7811 | 1088028.5715
85 | 2720227.9302 | 1088029.0238 | 2720228.152 | 1088023.635
86 | 2720228.4525 | 1088016.3362 | 2720228.152 | 1088023.635
87 | 2720248.7567 | 1088031.6259 | 2720239.7206 | 1088030.4969
88 | 2720248.7567 | 1088031.6259 | 2720263.503 | 1088036.0647
89 | 2720228.4525 | 1088016.3362 | 2720234.8756 | 1088015.739
90 | 2720228.4525 | 1088016.3362 | 2720211.583 | 1088015.6139
91 | 2720241.3708 | 1088015.135 | 2720234.8756 | 1088015.739
92 | 2720241.3708 | 1088015.135 | 2720241.3708 | 1088015.135 | 2720246.4124 | 1088013.2085
93 | 2720253.7578 | 1088011.0139 | 2720250.9159 | 1088011.4876 | 2720246.4124 | 1088013.2085
94 | 2720252.9098 | 1088043.672 | 2720263.503 | 1088036.0647
95 | 2720263.503 | 1088036.0647 | 2720268.2393 | 1088036.1211
96 | 2720260.934 | 1088009.8177 | 2720253.7578 | 1088011.0139
97 | 2720252.9098 | 1088043.672 | 2720254.1198 | 1088047.1776
98 | 2720252.9098 | 1088043.672 | 2720250.4535 | 1088044.4063
99 | 2720268.2393 | 1088036.1211 | 2720275.8137 | 1088036.2112
100 | 2720267.6744 | 1088047.5775 | 2720255.8891 | 1088052.3036 | 2720254.1198 | 1088047.1776
101 | 2720250.4535 | 1088044.4063 | 2720245.4056 | 1088045.9154
102 | 2720230.7965 | 1088060.9446 | 2720237.1088 | 1088061.1945
103 | 2720239.5485 | 1088047.6664 | 2720239.5485 | 1088047.6664 | 2720237.1088 | 1088061.1945
104 | 2720239.5485 | 1088047.6664 | 2720245.4056 | 1088045.9154
105 | 2720303.4898 | 1088034.4981 | 2720314.1343 | 1088034.8977
106 | 2720289.9412 | 1088045.6505 | 2720290.0559 | 1088046.702
107 | 2720314.1343 | 1088034.8977 | 2720331.2993 | 1088035.0319
108 | 2720314.1343 | 1088034.8977 | 2720317.1449 | 1088044.2018
109 | 2720290.9847 | 1088055.2213 | 2720290.0559 | 1088046.702
110 | 2720290.9847 | 1088055.2213 | 2720294.0836 | 1088057.7057
111 | 2720290.9847 | 1088055.2213 | 2720276.8596 | 1088058.0643
112 | 2720294.0836 | 1088057.7057 | 2720295.7198 | 1088059.0175 | 2720302.4208 | 1088058.3319
113 | 2720276.1459 | 1088058.208 | 2720276.8596 | 1088058.0643
114 | 2720302.4208 | 1088058.3319 | 2720310.1097 | 1088057.5453 | 2720308.7013 | 1088052.6419
115 | 2720317.1449 | 1088044.2018 | 2720317.4411 | 1088045.117
116 | 2720322.1655 | 1088059.7172 | 2720317.4411 | 1088045.117
117 | 2720322.1655 | 1088059.7172 | 2720322.496 | 1088060.7385
118 | 2720324.4581 | 1088066.8021 | 2720324.4581 | 1088066.8021 | 2720322.496 | 1088060.7385

## bus_geodata
| x | y | coords
0 | 2720279.6543 | 1088152.4115
1 | 2720262.6733 | 1088151.9787
2 | 2720302.3758 | 1088152.9905
3 | 2720249.607 | 1088150.9029
4 | 2720300.4029 | 1088190.3967
5 | 2720231.4426 | 1088145.3309
6 | 2720268.0409 | 1088193.0697
7 | 2720299.8044 | 1088190.4461
8 | 2720189.3719 | 1088113.3998
9 | 2720588.5631 | 1088000.809
10 | 2720526.247 | 1088011.8646
11 | 2720525.7696 | 1088011.9669
12 | 2720491.6027 | 1088013.8403
13 | 2720473.5636 | 1088012.4903
14 | 2720251 | 1088123.8249
15 | 2720192.456 | 1088078.9024
16 | 2720223.4853 | 1088067.2965
17 | 2720224.6841 | 1088060.7026
18 | 2720429.028 | 1088114.4924
19 | 2720381.6407 | 1088041.6026
20 | 2720379.6294 | 1088035.201
21 | 2720436.0506 | 1088013.8394
22 | 2720407.7418 | 1088024.4586
23 | 2720307.5955 | 1087860.9577
24 | 2720358.1863 | 1087894.9138
25 | 2720264.5063 | 1087856.9801
26 | 2720371.5529 | 1087910.2779
27 | 2720254.0908 | 1087820.6487
28 | 2720197.5674 | 1087838.7786
29 | 2720315.8532 | 1087935.0388
30 | 2720377.1461 | 1087918.7821
31 | 2720312.6026 | 1087937.2792
32 | 2720386.216 | 1087938.9325
33 | 2720355.8238 | 1087984.8029
34 | 2720356.5467 | 1087984.1679
35 | 2720341.8507 | 1087997.0743
36 | 2720362.781 | 1087978.6929
37 | 2720336.8941 | 1088001.3349
38 | 2720345.7446 | 1088001.8713
39 | 2720368.6738 | 1087973.5489
40 | 2720333.818 | 1088003.0976
41 | 2720328.952 | 1087989.7526
42 | 2720353.3941 | 1088011.2949
43 | 2720369.4857 | 1087972.8504
44 | 2720328.4186 | 1088004.7041
45 | 2720326.5765 | 1087986.2882
46 | 2720354.537 | 1088012.7028
47 | 2720371.334 | 1087971.2599
48 | 2720372.6633 | 1087970.1161
49 | 2720318.034 | 1088007.794
50 | 2720305.3399 | 1088011.5711
51 | 2720334.3304 | 1088019.5527
52 | 2720344.3866 | 1088016.1437
53 | 2720324.9416 | 1088022.7997
54 | 2720288.1236 | 1088016.6938
55 | 2720284.0963 | 1088017.8921
56 | 2720310.4099 | 1088030.6876
57 | 2720324.5119 | 1087983.2774
58 | 2720286.7558 | 1088028.0591
59 | 2720264.6712 | 1088022.8896
60 | 2720261.9155 | 1088013.2505
61 | 2720256.9995 | 1088024.774
62 | 2720288.9291 | 1088036.3673
63 | 2720386.055 | 1087952.5694
64 | 2720386.5222 | 1087942.0913
65 | 2720279.5583 | 1087956.2669
66 | 2720265.0956 | 1087962.4772
67 | 2720391.2048 | 1087998.9445
68 | 2720389.6324 | 1087999.8574
69 | 2720384.0069 | 1088003.1232
70 | 2720375.0234 | 1088026.2174
71 | 2720371.3357 | 1088025.166
72 | 2720379.4745 | 1088027.5064
73 | 2720397.4196 | 1088026.7789
74 | 2720389.8187 | 1088027.6355
75 | 2720384.7946 | 1088027.806
76 | 2720362.5563 | 1088028.2499
77 | 2720369.5815 | 1088024.0997
78 | 2720359.8609 | 1088017.4225
79 | 2720348.7228 | 1088033.1091
80 | 2720219.0661 | 1088028.2453
81 | 2720222.7811 | 1088028.5715
82 | 2720227.9302 | 1088029.0238
83 | 2720228.152 | 1088023.635
84 | 2720239.7206 | 1088030.4969
85 | 2720248.7567 | 1088031.6259
86 | 2720228.4525 | 1088016.3362
87 | 2720234.8756 | 1088015.739
88 | 2720211.583 | 1088015.6139
89 | 2720241.3708 | 1088015.135
90 | 2720246.4124 | 1088013.2085
91 | 2720263.503 | 1088036.0647
92 | 2720253.7578 | 1088011.0139
93 | 2720260.934 | 1088009.8177
94 | 2720252.9098 | 1088043.672
95 | 2720268.2393 | 1088036.1211
96 | 2720254.1198 | 1088047.1776
97 | 2720250.4535 | 1088044.4063
98 | 2720275.8137 | 1088036.2112
99 | 2720230.7965 | 1088060.9446
100 | 2720237.1088 | 1088061.1945
101 | 2720239.5485 | 1088047.6664
102 | 2720245.4056 | 1088045.9154
103 | 2720267.6744 | 1088047.5775
104 | 2720303.4898 | 1088034.4981
105 | 2720289.9412 | 1088045.6505
106 | 2720314.1343 | 1088034.8977
107 | 2720290.0559 | 1088046.702
108 | 2720290.9847 | 1088055.2213
109 | 2720294.0836 | 1088057.7057
110 | 2720276.8596 | 1088058.0643
111 | 2720302.4208 | 1088058.3319
112 | 2720276.1459 | 1088058.208
113 | 2720331.2993 | 1088035.0319
114 | 2720317.1449 | 1088044.2018
115 | 2720308.7013 | 1088052.6419
116 | 2720317.4411 | 1088045.117
117 | 2720322.1655 | 1088059.7172
118 | 2720322.496 | 1088060.7385
119 | 2720324.4581 | 1088066.8021
120 | 2720284.0963 | 1088017.8921

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97818 | -0.42129 | 0.0044921 | 0.0011258
1 | 0.97843 | -0.41634 | 0.0029627 | 0.00074253
2 | 0.97794 | -0.42606 | 0.0031734 | 0.00079534
3 | 0.97866 | -0.41179 | 0.0027343 | 0.00068527
4 | 0.97765 | -0.43175 | 0.0027716 | 0.00069464
5 | 0.97905 | -0.40429 | 0 | 0
6 | 0.97757 | -0.43321 | 0.0024108 | 0.0006042
7 | 0.97765 | -0.43181 | 0.0031471 | 0.00078873
8 | 0.98015 | -0.38256 | 0 | 0
9 | 0.98782 | -0.23407 | 0.0063496 | 0.0015914
10 | 0.98819 | -0.22688 | 0.0021853 | 0.00054768
11 | 0.98819 | -0.2268 | 0.0051514 | 0.0012911
12 | 0.98863 | -0.21832 | 0.0035354 | 0.00088606
13 | 0.98891 | -0.21271 | 0 | 0
14 | 0.97924 | -0.40052 | 0.015362 | 0.00385
15 | 0.98141 | -0.35808 | 0.0021339 | 0.0005348
16 | 0.98308 | -0.32537 | 0.0036838 | 0.00092326
17 | 0.98337 | -0.31986 | 0.01091 | 0.0027343
18 | 0.99061 | -0.17992 | 0.0026655 | 0.00066805
19 | 0.99082 | -0.1758 | 0.0019951 | 0.00050001
20 | 0.99085 | -0.17525 | 0.0050503 | 0.0012657
21 | 0.98951 | -0.20107 | 0.0056609 | 0.0014188
22 | 0.99015 | -0.18874 | 0.0019557 | 0.00049014
23 | 0.98697 | -0.2504 | 0.0033392 | 0.00083689
24 | 0.98799 | -0.23063 | 0 | 0
25 | 0.98635 | -0.2625 | 0 | 0
26 | 0.98833 | -0.22404 | 0 | 0
27 | 0.98573 | -0.27446 | 0.011109 | 0.0027843
28 | 0.98608 | -0.26779 | 0.0036922 | 0.00092535
29 | 0.9865 | -0.25962 | 0.0056464 | 0.0014151
30 | 0.9888 | -0.21489 | 0.0035733 | 0.00089556
31 | 0.9864 | -0.2615 | 0.010752 | 0.0026948
32 | 0.9899 | -0.19353 | 0 | 0
33 | 0.99346 | -0.12482 | 0.0039228 | 0.00098314
34 | 0.99338 | -0.12635 | 0.0087438 | 0.0021914
35 | 0.99505 | -0.094198 | 0 | 0
36 | 0.99277 | -0.13819 | 0.0028054 | 0.00070309
37 | 0.99584 | -0.07926 | 0 | 0
38 | 0.99445 | -0.10582 | 0.0021715 | 0.00054422
39 | 0.99221 | -0.14897 | 0.0043018 | 0.0010781
40 | 0.99628 | -0.070855 | 0 | 0
41 | 0.99557 | -0.084298 | 0.0023175 | 0.00058082
42 | 0.99326 | -0.12857 | 0.0029293 | 0.00073416
43 | 0.99213 | -0.15037 | 0.001531 | 0.00038371
44 | 0.99698 | -0.057487 | 0.002885 | 0.00072305
45 | 0.99551 | -0.085635 | 0.01316 | 0.0032983
46 | 0.99308 | -0.13195 | 0 | 0
47 | 0.99197 | -0.15348 | 0.0028458 | 0.00071322
48 | 0.99186 | -0.15563 | 0.0093487 | 0.002343
49 | 0.99833 | -0.031692 | 0.0044214 | 0.0011081
50 | 1 | 0 | -0.55648 | -0.14162
51 | 0.99149 | -0.16257 | 0 | 0
52 | 0.99228 | -0.14746 | 0.0060624 | 0.0015194
53 | 0.99075 | -0.17673 | 0.011938 | 0.0029919
54 | 0.98786 | -0.23261 | 0.010567 | 0.0026484
55 | 0.9879 | -0.23181 | 0 | 0
56 | 0.98958 | -0.19947 | 0.0090184 | 0.0022602
57 | 0.99549 | -0.085951 | 0.0049294 | 0.0012354
58 | 0.98801 | -0.22983 | 0.006949 | 0.0017416
59 | 0.98361 | -0.31518 | 0 | 0
60 | 0.98273 | -0.33236 | 0.0099318 | 0.0024891
61 | 0.9843 | -0.30166 | 0.0047913 | 0.0012008
62 | 0.98814 | -0.22715 | 0 | 0
63 | 0.99062 | -0.17968 | 0.0024084 | 0.00060361
64 | 0.99006 | -0.19048 | 0.0035119 | 0.00088017
65 | 0.98584 | -0.27237 | 0.0036735 | 0.00092067
66 | 0.98566 | -0.27581 | 0.012187 | 0.0030543
67 | 0.99026 | -0.18659 | 0.0078869 | 0.0019766
68 | 0.99027 | -0.18634 | 0.0052642 | 0.0013193
69 | 0.99035 | -0.18482 | 0.0125 | 0.0031327
70 | 0.99111 | -0.17019 | 0 | 0
71 | 0.99136 | -0.16537 | 0 | 0
72 | 0.99091 | -0.17392 | 0 | 0
73 | 0.99039 | -0.18406 | 0.0034081 | 0.00085416
74 | 0.99059 | -0.18022 | 0.0045198 | 0.0011328
75 | 0.99074 | -0.17729 | 0.0029008 | 0.000727
76 | 0.99123 | -0.16773 | 0.0070505 | 0.001767
77 | 0.99152 | -0.16227 | 0.0024677 | 0.00061846
78 | 0.99247 | -0.14386 | 0.0068642 | 0.0017203
79 | 0.99114 | -0.16962 | 0.00725 | 0.001817
80 | 0.98044 | -0.3772 | 0.0067561 | 0.0016932
81 | 0.98046 | -0.37674 | 0.0093237 | 0.0023367
82 | 0.98054 | -0.37524 | 0 | 0
83 | 0.98062 | -0.37366 | 0.0027118 | 0.00067963
84 | 0.98527 | -0.28287 | 0.0038944 | 0.00097604
85 | 0.9853 | -0.28223 | 0 | 0
86 | 0.98074 | -0.37118 | 0 | 0
87 | 0.98099 | -0.36643 | 0.0060711 | 0.0015216
88 | 0.9804 | -0.37786 | 0.021851 | 0.0054764
89 | 0.98127 | -0.36091 | 0.0086195 | 0.0021602
90 | 0.98154 | -0.3555 | 0.0080092 | 0.0020073
91 | 0.98677 | -0.25367 | 0 | 0
92 | 0.982 | -0.34668 | 0.0038711 | 0.00097019
93 | 0.98245 | -0.33785 | 0.017905 | 0.0044873
94 | 0.98577 | -0.27319 | 0 | 0
95 | 0.98718 | -0.24573 | 0.005629 | 0.0014108
96 | 0.98575 | -0.27353 | 0.0024727 | 0.00061971
97 | 0.98558 | -0.2768 | 0.0055966 | 0.0014026
98 | 0.98752 | -0.2392 | 0.012686 | 0.0031795
99 | 0.98367 | -0.31393 | 0.0047285 | 0.0011851
100 | 0.98401 | -0.30727 | 0.0060256 | 0.0015102
101 | 0.98483 | -0.29132 | 0.0047433 | 0.0011888
102 | 0.98523 | -0.28371 | 0.003694 | 0.00092581
103 | 0.98571 | -0.27438 | 0.0026178 | 0.00065607
104 | 0.98903 | -0.21004 | 0 | 0
105 | 0.98781 | -0.23364 | 0.010354 | 0.0025951
106 | 0.98866 | -0.21726 | 0 | 0
107 | 0.98778 | -0.23418 | 0.0094964 | 0.00238
108 | 0.98763 | -0.2371 | 0 | 0
109 | 0.98759 | -0.23785 | 0.0038996 | 0.00097733
110 | 0.98752 | -0.23929 | 0.0057324 | 0.0014367
111 | 0.98754 | -0.2389 | 0.0046866 | 0.0011746
112 | 0.98752 | -0.23932 | 0.0027745 | 0.00069534
113 | 0.98847 | -0.22099 | 0.012188 | 0.0030545
114 | 0.98842 | -0.22178 | 0.0066323 | 0.0016622
115 | 0.98752 | -0.23935 | 0.0019813 | 0.00049655
116 | 0.98841 | -0.22211 | 0.0066928 | 0.0016774
117 | 0.98823 | -0.22557 | 0.006164 | 0.0015448
118 | 0.98822 | -0.22569 | 0.0035283 | 0.00088426
119 | 0.98821 | -0.22603 | 0.0029294 | 0.00073417
120 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.016 | -0.0040108 | 0.016004 | 0.004013 | 3.7737e-06 | 2.2019e-06 | 0.02434 | 0.02434 | 0.02434 | 0.97818 | -0.42129 | 0.97843 | -0.41634 | 6.6868
1 | 0.011508 | 0.002885 | -0.011505 | -0.0028836 | 2.6122e-06 | 1.3865e-06 | 0.017506 | 0.017506 | 0.017506 | 0.97818 | -0.42129 | 0.97794 | -0.42606 | 4.8095
2 | -0.018967 | -0.0047555 | 0.018971 | 0.004758 | 4.1159e-06 | 2.4685e-06 | 0.028845 | 0.028845 | 0.028845 | 0.97843 | -0.41634 | 0.97866 | -0.41179 | 7.9246
3 | 0.0083319 | 0.0020882 | -0.0083297 | -0.0020873 | 2.2577e-06 | 9.7509e-07 | 0.012678 | 0.012678 | 0.012678 | 0.97794 | -0.42606 | 0.97765 | -0.43175 | 3.4829
4 | -0.021705 | -0.0054433 | 0.021713 | 0.005448 | 7.7603e-06 | 4.7278e-06 | 0.033003 | 0.033003 | 0.033003 | 0.97866 | -0.41179 | 0.97905 | -0.40429 | 9.0667
5 | 0.005558 | 0.0013926 | -0.005558 | -0.0013926 | 1.6115e-08 | 2.7837e-09 | 0.0084594 | 0.0084594 | 0.0084594 | 0.97765 | -0.43175 | 0.97765 | -0.43181 | 2.324
6 | -0.021713 | -0.005448 | 0.021735 | 0.0054617 | 2.2526e-05 | 1.3722e-05 | 0.033003 | 0.033002 | 0.033003 | 0.97905 | -0.40429 | 0.98015 | -0.38256 | 9.0667
7 | -0.0024108 | -0.0006042 | 0.0024109 | 0.0006039 | 1.6093e-07 | -2.9662e-07 | 0.0036696 | 0.0036694 | 0.0036696 | 0.97757 | -0.43321 | 0.97765 | -0.43181 | 1.0081
8 | -0.03711 | -0.0093193 | 0.037153 | 0.0093466 | 4.34e-05 | 2.7316e-05 | 0.056345 | 0.056345 | 0.056345 | 0.98015 | -0.38256 | 0.98141 | -0.35808 | 15.4794
9 | 0.015375 | 0.0038576 | -0.015362 | -0.00385 | 1.3154e-05 | 7.6078e-06 | 0.023343 | 0.023343 | 0.023343 | 0.98015 | -0.38256 | 0.97924 | -0.40052 | 6.4129
10 | -0.0063496 | -0.0015914 | 0.0063518 | 0.0015919 | 2.1755e-06 | 5.8022e-07 | 0.0095648 | 0.0095645 | 0.0095648 | 0.98782 | -0.23407 | 0.98819 | -0.22688 | 2.6277
11 | -0.008537 | -0.0021396 | 0.0085371 | 0.0021396 | 3.0256e-08 | 1.3109e-08 | 0.012855 | 0.012855 | 0.012855 | 0.98819 | -0.22688 | 0.98819 | -0.2268 | 3.5316
12 | -0.013688 | -0.0034307 | 0.013694 | 0.0034338 | 5.5359e-06 | 3.0976e-06 | 0.020612 | 0.020612 | 0.020612 | 0.98819 | -0.2268 | 0.98863 | -0.21832 | 5.6627
13 | -0.017229 | -0.0043198 | 0.017234 | 0.0043226 | 4.6015e-06 | 2.7109e-06 | 0.025933 | 0.025933 | 0.025933 | 0.98863 | -0.21832 | 0.98891 | -0.21271 | 7.1245
14 | -0.017234 | -0.0043226 | 0.017244 | 0.0043282 | 9.5682e-06 | 5.6366e-06 | 0.025933 | 0.025933 | 0.025933 | 0.98891 | -0.21271 | 0.98951 | -0.20107 | 7.1245
15 | -0.039287 | -0.0098814 | 0.039349 | 0.0099202 | 6.1485e-05 | 3.8766e-05 | 0.05958 | 0.05958 | 0.05958 | 0.98141 | -0.35808 | 0.98308 | -0.32537 | 16.3682
16 | -0.043033 | -0.010843 | 0.043044 | 0.010851 | 1.1347e-05 | 7.1718e-06 | 0.065156 | 0.065156 | 0.065156 | 0.98308 | -0.32537 | 0.98337 | -0.31986 | 17.9
17 | -0.053954 | -0.013585 | 0.053969 | 0.013595 | 1.5299e-05 | 9.7134e-06 | 0.081665 | 0.081665 | 0.081665 | 0.98337 | -0.31986 | 0.98367 | -0.31393 | 22.4353
18 | -0.0026655 | -0.00066805 | 0.0026661 | 0.00066726 | 5.2263e-07 | -7.8501e-07 | 0.004004 | 0.0040036 | 0.004004 | 0.99061 | -0.17992 | 0.99082 | -0.1758 | 1.1
19 | -0.0046611 | -0.0011673 | 0.0046612 | 0.0011673 | 1.2329e-07 | -7.5196e-09 | 0.0069998 | 0.0069998 | 0.0069998 | 0.99082 | -0.1758 | 0.99085 | -0.17525 | 1.923
20 | -0.0097115 | -0.002433 | 0.0097121 | 0.0024333 | 6.1556e-07 | 2.9455e-07 | 0.014584 | 0.014584 | 0.014584 | 0.99085 | -0.17525 | 0.99091 | -0.17392 | 4.0066
21 | -0.022904 | -0.0057469 | 0.022918 | 0.0057552 | 1.3478e-05 | 8.2368e-06 | 0.034446 | 0.034446 | 0.034446 | 0.98951 | -0.20107 | 0.99015 | -0.18874 | 9.4631
22 | -0.024874 | -0.0062453 | 0.024879 | 0.0062487 | 5.5498e-06 | 3.4157e-06 | 0.037385 | 0.037385 | 0.037385 | 0.99015 | -0.18874 | 0.99039 | -0.18406 | 10.2705
23 | -0.018157 | -0.0045542 | 0.018174 | 0.0045644 | 1.7127e-05 | 1.0182e-05 | 0.027375 | 0.027375 | 0.027375 | 0.98697 | -0.2504 | 0.98799 | -0.23063 | 7.5207
24 | 0.014817 | 0.0037174 | -0.014809 | -0.0037125 | 8.5381e-06 | 4.8818e-06 | 0.022341 | 0.022341 | 0.022341 | 0.98697 | -0.2504 | 0.98635 | -0.2625 | 6.1377
25 | -0.018174 | -0.0045644 | 0.018179 | 0.0045678 | 5.7224e-06 | 3.4015e-06 | 0.027375 | 0.027375 | 0.027375 | 0.98799 | -0.23063 | 0.98833 | -0.22404 | 7.5206
26 | 0.011116 | 0.0027876 | -0.011109 | -0.0027843 | 6.3343e-06 | 3.2878e-06 | 0.01677 | 0.01677 | 0.01677 | 0.98635 | -0.2625 | 0.98573 | -0.27446 | 4.6072
27 | 0.0036931 | 0.00092492 | -0.0036922 | -0.00092535 | 9.3035e-07 | -4.2442e-07 | 0.0055712 | 0.0055716 | 0.0055716 | 0.98635 | -0.2625 | 0.98608 | -0.26779 | 1.5307
28 | 0.032327 | 0.0081265 | -0.032272 | -0.0080922 | 5.4822e-05 | 3.4297e-05 | 0.048679 | 0.04868 | 0.04868 | 0.98833 | -0.22404 | 0.9865 | -0.25962 | 13.3735
29 | -0.050506 | -0.012694 | 0.050528 | 0.012708 | 2.2079e-05 | 1.4e-05 | 0.076054 | 0.076054 | 0.076054 | 0.98833 | -0.22404 | 0.9888 | -0.21489 | 20.894
30 | 0.026625 | 0.0066771 | -0.026623 | -0.0066756 | 2.388e-06 | 1.4779e-06 | 0.040163 | 0.040163 | 0.040163 | 0.9865 | -0.25962 | 0.9864 | -0.2615 | 11.0337
31 | -0.054101 | -0.013604 | 0.054157 | 0.013639 | 5.5239e-05 | 3.5068e-05 | 0.081432 | 0.081432 | 0.081432 | 0.9888 | -0.21489 | 0.9899 | -0.19353 | 22.3713
32 | 0.01587 | 0.0039808 | -0.015862 | -0.003976 | 8.2213e-06 | 4.7737e-06 | 0.023942 | 0.023942 | 0.023942 | 0.9864 | -0.2615 | 0.98584 | -0.27237 | 6.5776
33 | -0.054157 | -0.013639 | 0.054164 | 0.013644 | 7.8917e-06 | 5.0099e-06 | 0.081432 | 0.081432 | 0.081432 | 0.9899 | -0.19353 | 0.99006 | -0.19048 | 22.3713
34 | 0.089876 | 0.022677 | -0.08987 | -0.022673 | 6.5441e-06 | 4.1757e-06 | 0.13467 | 0.13467 | 0.13467 | 0.99346 | -0.12482 | 0.99338 | -0.12635 | 36.9976
35 | -0.093799 | -0.02366 | 0.093937 | 0.023748 | 0.00013775 | 8.7922e-05 | 0.14055 | 0.14055 | 0.14055 | 0.99346 | -0.12482 | 0.99505 | -0.094198 | 38.6118
36 | 0.081126 | 0.020482 | -0.08108 | -0.020452 | 4.5987e-05 | 2.9325e-05 | 0.12157 | 0.12157 | 0.12157 | 0.99338 | -0.12635 | 0.99277 | -0.13819 | 33.3994
37 | -0.52463 | -0.13308 | 0.52501 | 0.13332 | 0.00037711 | 0.00024101 | 0.7851 | 0.7851 | 0.7851 | 0.99505 | -0.094198 | 0.99584 | -0.07926 | 53.922
38 | 0.43069 | 0.10933 | -0.43045 | -0.10918 | 0.00024064 | 0.00015369 | 0.64456 | 0.64456 | 0.64456 | 0.99505 | -0.094198 | 0.99445 | -0.10582 | 44.2691
39 | 0.078274 | 0.019749 | -0.078234 | -0.019723 | 4.0408e-05 | 2.576e-05 | 0.11737 | 0.11737 | 0.11737 | 0.99277 | -0.13819 | 0.99221 | -0.14897 | 32.2442
40 | -0.54542 | -0.13844 | 0.54564 | 0.13858 | 0.00022064 | 0.00014103 | 0.81561 | 0.81561 | 0.81561 | 0.99584 | -0.07926 | 0.99628 | -0.070855 | 56.017
41 | 0.020413 | 0.0051182 | -0.020408 | -0.0051152 | 4.9001e-06 | 2.9534e-06 | 0.030503 | 0.030503 | 0.030503 | 0.99584 | -0.07926 | 0.99557 | -0.084298 | 8.38
42 | 0.42828 | 0.10864 | -0.42781 | -0.10834 | 0.00046799 | 0.00029889 | 0.64131 | 0.64131 | 0.64131 | 0.99445 | -0.10582 | 0.99326 | -0.12857 | 44.046
43 | 0.073932 | 0.018645 | -0.073927 | -0.018642 | 4.9411e-06 | 3.1485e-06 | 0.11092 | 0.11092 | 0.11092 | 0.99221 | -0.14897 | 0.99213 | -0.15037 | 30.4719
44 | -0.54564 | -0.13858 | 0.54599 | 0.13881 | 0.00035131 | 0.00022455 | 0.81561 | 0.81561 | 0.81561 | 0.99628 | -0.070855 | 0.99698 | -0.057487 | 56.017
45 | 0.018091 | 0.0045344 | -0.01809 | -0.0045337 | 1.1517e-06 | 6.8246e-07 | 0.027039 | 0.027039 | 0.027039 | 0.99557 | -0.084298 | 0.99551 | -0.085635 | 7.4284
46 | 0.42488 | 0.1076 | -0.42482 | -0.10756 | 6.8963e-05 | 4.4043e-05 | 0.63692 | 0.63692 | 0.63692 | 0.99326 | -0.12857 | 0.99308 | -0.13195 | 43.7446
47 | 0.072396 | 0.018258 | -0.072385 | -0.018252 | 1.0789e-05 | 6.8735e-06 | 0.10862 | 0.10862 | 0.10862 | 0.99213 | -0.15037 | 0.99197 | -0.15348 | 29.841
48 | -0.54888 | -0.13953 | 0.54956 | 0.13997 | 0.00068284 | 0.00043645 | 0.81991 | 0.81991 | 0.81991 | 0.99698 | -0.057487 | 0.99833 | -0.031692 | 56.3127
49 | 0.0049295 | 0.0012354 | -0.0049294 | -0.0012354 | 7.4326e-08 | 1.0388e-10 | 0.0073682 | 0.0073683 | 0.0073683 | 0.99551 | -0.085635 | 0.99549 | -0.085951 | 2.0242
50 | 0.32991 | 0.083682 | -0.32966 | -0.083525 | 0.00024588 | 0.00015681 | 0.49468 | 0.49468 | 0.49468 | 0.99308 | -0.13195 | 0.99228 | -0.14746 | 33.9753
51 | 0.094908 | 0.023877 | -0.094854 | -0.023843 | 5.3981e-05 | 3.4456e-05 | 0.14224 | 0.14224 | 0.14224 | 0.99308 | -0.13195 | 0.99247 | -0.14386 | 39.0771
52 | 0.06954 | 0.017538 | -0.069533 | -0.017534 | 7.1609e-06 | 4.5604e-06 | 0.10435 | 0.10435 | 0.10435 | 0.99197 | -0.15348 | 0.99186 | -0.15563 | 28.6683
53 | 0.060184 | 0.015191 | -0.060115 | -0.015147 | 6.9244e-05 | 4.4024e-05 | 0.090327 | 0.090328 | 0.090328 | 0.99186 | -0.15563 | 0.99062 | -0.17968 | 24.8153
54 | -0.55398 | -0.14107 | 0.55483 | 0.14162 | 0.00084817 | 0.00054214 | 0.8265 | 0.8265 | 0.8265 | 0.99833 | -0.031692 | 1 | 0 | 56.7653
55 | -0.32336 | -0.081856 | 0.3236 | 0.082006 | 0.00023473 | 0.00014968 | 0.48559 | 0.48559 | 0.48559 | 0.99149 | -0.16257 | 0.99228 | -0.14746 | 33.351
56 | 0.32336 | 0.081856 | -0.32314 | -0.081716 | 0.00021961 | 0.00014004 | 0.48559 | 0.48559 | 0.48559 | 0.99149 | -0.16257 | 0.99075 | -0.17673 | 33.351
57 | 0.31121 | 0.078724 | -0.31087 | -0.078508 | 0.00033919 | 0.00021623 | 0.46766 | 0.46766 | 0.46766 | 0.99075 | -0.17673 | 0.98958 | -0.19947 | 32.1196
58 | -0.010567 | -0.0026484 | 0.010568 | 0.0026486 | 3.9923e-07 | 2.0171e-07 | 0.015918 | 0.015918 | 0.015918 | 0.98786 | -0.23261 | 0.9879 | -0.23181 | 4.373
59 | -0.010568 | -0.0026486 | 0.010569 | 0.0026491 | 9.9851e-07 | 5.0447e-07 | 0.015918 | 0.015918 | 0.015918 | 0.9879 | -0.23181 | 0.98801 | -0.22983 | 4.373
60 | 0.30185 | 0.076248 | -0.3017 | -0.07615 | 0.00015272 | 9.7335e-05 | 0.4541 | 0.4541 | 0.4541 | 0.98958 | -0.19947 | 0.98903 | -0.21004 | 31.1882
61 | -0.017518 | -0.0043907 | 0.01752 | 0.004392 | 2.2416e-06 | 1.3247e-06 | 0.026383 | 0.026383 | 0.026383 | 0.98801 | -0.22983 | 0.98814 | -0.22715 | 7.2482
62 | 0.095253 | 0.023951 | -0.095175 | -0.023901 | 7.8096e-05 | 4.9854e-05 | 0.14413 | 0.14413 | 0.14413 | 0.98361 | -0.31518 | 0.98273 | -0.33236 | 39.5956
63 | -0.095253 | -0.023951 | 0.095315 | 0.02399 | 6.1538e-05 | 3.9284e-05 | 0.14413 | 0.14413 | 0.14413 | 0.98361 | -0.31518 | 0.9843 | -0.30166 | 39.5956
64 | 0.085243 | 0.021412 | -0.085221 | -0.021397 | 2.2311e-05 | 1.4234e-05 | 0.12909 | 0.12909 | 0.12909 | 0.98273 | -0.33236 | 0.98245 | -0.33785 | 35.4642
65 | -0.10011 | -0.025191 | 0.1002 | 0.02525 | 9.3036e-05 | 5.9405e-05 | 0.15137 | 0.15137 | 0.15137 | 0.9843 | -0.30166 | 0.9853 | -0.28223 | 41.5855
66 | -0.26332 | -0.066441 | 0.26354 | 0.066579 | 0.00021593 | 0.00013745 | 0.39669 | 0.39669 | 0.39669 | 0.98814 | -0.22715 | 0.98903 | -0.21004 | 27.2451
67 | 0.038942 | 0.0097657 | -0.03893 | -0.0097581 | 1.2043e-05 | 7.588e-06 | 0.058644 | 0.058644 | 0.058644 | 0.98814 | -0.22715 | 0.98781 | -0.23364 | 16.111
68 | 0.20686 | 0.052284 | -0.20674 | -0.052208 | 0.00011944 | 7.577e-05 | 0.31166 | 0.31166 | 0.31166 | 0.98814 | -0.22715 | 0.98752 | -0.2392 | 21.4053
69 | 0.057706 | 0.014543 | -0.057676 | -0.014524 | 2.9798e-05 | 1.8935e-05 | 0.08671 | 0.08671 | 0.08671 | 0.99062 | -0.17968 | 0.99006 | -0.19048 | 23.8214
70 | 0.012189 | 0.0030554 | -0.012187 | -0.0030543 | 1.9978e-06 | 1.078e-06 | 0.018398 | 0.018398 | 0.018398 | 0.98584 | -0.27237 | 0.98566 | -0.27581 | 5.0543
71 | -0.0078869 | -0.0019766 | 0.007887 | 0.0019767 | 9.5762e-08 | 3.7896e-08 | 0.011851 | 0.011851 | 0.011851 | 0.99026 | -0.18659 | 0.99027 | -0.18634 | 3.2558
72 | -0.013151 | -0.003296 | 0.013152 | 0.0032965 | 9.5255e-07 | 5.2594e-07 | 0.019761 | 0.019761 | 0.019761 | 0.99027 | -0.18634 | 0.99035 | -0.18482 | 5.4289
73 | -0.025652 | -0.0064292 | 0.02567 | 0.0064403 | 1.7888e-05 | 1.1035e-05 | 0.038542 | 0.038542 | 0.038542 | 0.99035 | -0.18482 | 0.99111 | -0.17019 | 10.5885
74 | -0.071113 | -0.017851 | 0.07113 | 0.017861 | 1.635e-05 | 1.0414e-05 | 0.10678 | 0.10678 | 0.10678 | 0.99111 | -0.17019 | 0.99136 | -0.16537 | 29.3344
75 | 0.045444 | 0.011411 | -0.045435 | -0.011406 | 8.0683e-06 | 5.1042e-06 | 0.068235 | 0.068235 | 0.068235 | 0.99111 | -0.17019 | 0.99091 | -0.17392 | 18.7459
76 | 0.014303 | 0.0035852 | -0.014301 | -0.0035843 | 1.6083e-06 | 9.0935e-07 | 0.021469 | 0.021469 | 0.021469 | 0.99136 | -0.16537 | 0.99123 | -0.16773 | 5.898
77 | -0.085432 | -0.021447 | 0.085445 | 0.021455 | 1.2661e-05 | 8.0768e-06 | 0.12825 | 0.12825 | 0.12825 | 0.99136 | -0.16537 | 0.99152 | -0.16227 | 35.2324
78 | 0.035723 | 0.0089724 | -0.035718 | -0.0089687 | 5.7517e-06 | 3.6125e-06 | 0.053651 | 0.053651 | 0.053651 | 0.99091 | -0.17392 | 0.99074 | -0.17729 | 14.7393
79 | -0.028287 | -0.0071029 | 0.028292 | 0.0071061 | 5.1921e-06 | 3.2243e-06 | 0.042505 | 0.042505 | 0.042505 | 0.99039 | -0.18406 | 0.99059 | -0.18022 | 11.6772
80 | -0.032812 | -0.0082389 | 0.032817 | 0.0082417 | 4.5826e-06 | 2.8681e-06 | 0.049294 | 0.049294 | 0.049294 | 0.99059 | -0.18022 | 0.99074 | -0.17729 | 13.5424
81 | 0.0072507 | 0.0018173 | -0.00725 | -0.001817 | 6.514e-07 | 2.2792e-07 | 0.010885 | 0.010885 | 0.010885 | 0.99123 | -0.16773 | 0.99114 | -0.16962 | 2.9903
82 | -0.087913 | -0.022073 | 0.08799 | 0.022122 | 7.7261e-05 | 4.9295e-05 | 0.13195 | 0.13195 | 0.13195 | 0.99152 | -0.16227 | 0.99247 | -0.14386 | 36.2498
83 | -0.0067561 | -0.0016932 | 0.0067563 | 0.0016933 | 1.4704e-07 | 4.7073e-08 | 0.010254 | 0.010254 | 0.010254 | 0.98044 | -0.3772 | 0.98046 | -0.37674 | 2.817
84 | -0.01608 | -0.00403 | 0.016081 | 0.0040307 | 1.1544e-06 | 6.7363e-07 | 0.024404 | 0.024404 | 0.024404 | 0.98046 | -0.37674 | 0.98054 | -0.37524 | 6.7044
85 | -0.016081 | -0.0040307 | 0.016082 | 0.0040314 | 1.2045e-06 | 7.0286e-07 | 0.024404 | 0.024404 | 0.024404 | 0.98054 | -0.37524 | 0.98062 | -0.37366 | 6.7044
86 | -0.018794 | -0.004711 | 0.018796 | 0.0047124 | 2.228e-06 | 1.3338e-06 | 0.028519 | 0.028519 | 0.028519 | 0.98062 | -0.37366 | 0.98074 | -0.37118 | 7.8349
87 | -0.0038944 | -0.00097604 | 0.0038946 | 0.000976 | 1.1813e-07 | -4.0374e-08 | 0.0058816 | 0.0058816 | 0.0058816 | 0.98527 | -0.28287 | 0.9853 | -0.28223 | 1.6158
88 | -0.10409 | -0.026226 | 0.10424 | 0.026317 | 0.00014241 | 9.0945e-05 | 0.15725 | 0.15725 | 0.15725 | 0.9853 | -0.28223 | 0.98677 | -0.25367 | 43.2013
89 | -0.040654 | -0.010193 | 0.040664 | 0.010199 | 9.2043e-06 | 5.8093e-06 | 0.061684 | 0.061684 | 0.061684 | 0.98074 | -0.37118 | 0.98099 | -0.36643 | 16.9461
90 | 0.021858 | 0.0054806 | -0.021851 | -0.0054764 | 6.9644e-06 | 4.2442e-06 | 0.033165 | 0.033165 | 0.033165 | 0.98074 | -0.37118 | 0.9804 | -0.37786 | 9.1112
91 | -0.046735 | -0.01172 | 0.046747 | 0.011728 | 1.2294e-05 | 7.7857e-06 | 0.070893 | 0.070893 | 0.070893 | 0.98099 | -0.36643 | 0.98127 | -0.36091 | 19.476
92 | -0.055366 | -0.013888 | 0.055381 | 0.013897 | 1.4268e-05 | 9.0636e-06 | 0.083963 | 0.083963 | 0.083963 | 0.98127 | -0.36091 | 0.98154 | -0.3555 | 23.0669
93 | -0.06339 | -0.015905 | 0.063417 | 0.015922 | 2.6677e-05 | 1.6976e-05 | 0.096105 | 0.096105 | 0.096105 | 0.98154 | -0.3555 | 0.982 | -0.34668 | 26.4025
94 | 0.084057 | 0.021216 | -0.083979 | -0.021166 | 7.8501e-05 | 5.0074e-05 | 0.12681 | 0.12681 | 0.12681 | 0.98677 | -0.25367 | 0.98577 | -0.27319 | 34.8376
95 | -0.18829 | -0.047533 | 0.18836 | 0.047579 | 7.1663e-05 | 4.5743e-05 | 0.28406 | 0.28406 | 0.28406 | 0.98677 | -0.25367 | 0.98718 | -0.24573 | 39.0194
96 | -0.067288 | -0.016892 | 0.067316 | 0.01691 | 2.8368e-05 | 1.8064e-05 | 0.10197 | 0.10197 | 0.10197 | 0.982 | -0.34668 | 0.98245 | -0.33785 | 28.014
97 | 0.0050906 | 0.0012756 | -0.0050905 | -0.0012756 | 8.2119e-08 | 5.2776e-09 | 0.0076842 | 0.0076842 | 0.0076842 | 0.98577 | -0.27319 | 0.98575 | -0.27353 | 2.1111
98 | 0.078888 | 0.019891 | -0.078875 | -0.019882 | 1.3643e-05 | 8.699e-06 | 0.11912 | 0.11912 | 0.11912 | 0.98577 | -0.27319 | 0.98558 | -0.2768 | 32.7265
99 | -0.19399 | -0.04899 | 0.19405 | 0.049028 | 6.0777e-05 | 3.851e-05 | 0.29255 | 0.29255 | 0.29255 | 0.98718 | -0.24573 | 0.98752 | -0.2392 | 20.0925
100 | 0.0026179 | 0.00065591 | -0.0026178 | -0.00065607 | 1.0611e-07 | -1.6308e-07 | 0.0039517 | 0.0039518 | 0.0039518 | 0.98575 | -0.27353 | 0.98571 | -0.27438 | 1.0856
101 | 0.073278 | 0.018479 | -0.073254 | -0.018464 | 2.42e-05 | 1.5421e-05 | 0.11068 | 0.11068 | 0.11068 | 0.98558 | -0.2768 | 0.98523 | -0.28371 | 30.4052
102 | -0.058698 | -0.01478 | 0.058716 | 0.014792 | 1.8688e-05 | 1.188e-05 | 0.088817 | 0.088817 | 0.088817 | 0.98367 | -0.31393 | 0.98401 | -0.30727 | 24.4004
103 | -0.064742 | -0.016302 | 0.064791 | 0.016333 | 4.9436e-05 | 3.1464e-05 | 0.097929 | 0.097929 | 0.097929 | 0.98401 | -0.30727 | 0.98483 | -0.29132 | 26.9036
104 | -0.069535 | -0.017522 | 0.06956 | 0.017538 | 2.5321e-05 | 1.6128e-05 | 0.1051 | 0.1051 | 0.1051 | 0.98483 | -0.29132 | 0.98523 | -0.28371 | 28.8725
105 | 0.038158 | 0.0095715 | -0.038145 | -0.0095633 | 1.3127e-05 | 8.265e-06 | 0.057412 | 0.057412 | 0.057412 | 0.98903 | -0.21004 | 0.98866 | -0.21726 | 15.7726
106 | 0.028576 | 0.0071631 | -0.028575 | -0.0071626 | 7.35e-07 | 4.5686e-07 | 0.043046 | 0.043046 | 0.043046 | 0.98781 | -0.23364 | 0.98778 | -0.23418 | 11.8259
107 | 0.01219 | 0.0030557 | -0.012188 | -0.0030545 | 2.1668e-06 | 1.1667e-06 | 0.018347 | 0.018347 | 0.018347 | 0.98866 | -0.21726 | 0.98847 | -0.22099 | 5.0404
108 | 0.025955 | 0.0065076 | -0.025949 | -0.0065041 | 5.5964e-06 | 3.4563e-06 | 0.039065 | 0.039065 | 0.039065 | 0.98866 | -0.21726 | 0.98842 | -0.22178 | 10.7322
109 | 0.019079 | 0.0047826 | -0.019076 | -0.004781 | 2.6546e-06 | 1.5893e-06 | 0.028741 | 0.028741 | 0.028741 | 0.98778 | -0.23418 | 0.98763 | -0.2371 | 7.8958
110 | 0.010568 | 0.0026486 | -0.010568 | -0.0026484 | 3.7761e-07 | 1.9085e-07 | 0.015923 | 0.015923 | 0.015923 | 0.98763 | -0.2371 | 0.98759 | -0.23785 | 4.3743
111 | 0.0085078 | 0.0021324 | -0.0085069 | -0.002132 | 8.8778e-07 | 3.8382e-07 | 0.012818 | 0.012818 | 0.012818 | 0.98763 | -0.2371 | 0.98752 | -0.23929 | 3.5215
112 | 0.0066682 | 0.0016711 | -0.0066679 | -0.001671 | 3.3437e-07 | 1.0097e-07 | 0.010047 | 0.010047 | 0.010047 | 0.98759 | -0.23785 | 0.98754 | -0.2389 | 2.7602
113 | 0.0027745 | 0.00069534 | -0.0027745 | -0.00069534 | 4.7715e-09 | -6.2606e-09 | 0.0041806 | 0.0041806 | 0.0041806 | 0.98752 | -0.23929 | 0.98752 | -0.23932 | 1.1485
114 | 0.0019813 | 0.00049642 | -0.0019813 | -0.00049655 | 4.2883e-08 | -1.3671e-07 | 0.0029854 | 0.0029854 | 0.0029854 | 0.98754 | -0.2389 | 0.98752 | -0.23935 | 0.82017
115 | 0.019317 | 0.0048419 | -0.019317 | -0.0048417 | 3.0507e-07 | 1.8292e-07 | 0.029081 | 0.029081 | 0.029081 | 0.98842 | -0.22178 | 0.98841 | -0.22211 | 7.9892
116 | 0.012624 | 0.0031644 | -0.012622 | -0.0031632 | 2.0785e-06 | 1.1336e-06 | 0.019005 | 0.019005 | 0.019005 | 0.98841 | -0.22211 | 0.98823 | -0.22557 | 5.2212
117 | 0.0064577 | 0.0016184 | -0.0064577 | -0.0016184 | 3.8061e-08 | 1.0605e-08 | 0.0097236 | 0.0097236 | 0.0097236 | 0.98823 | -0.22557 | 0.98822 | -0.22569 | 2.6713
118 | 0.0029294 | 0.00073412 | -0.0029294 | -0.00073417 | 4.6499e-08 | -5.1892e-08 | 0.0044109 | 0.004411 | 0.004411 | 0.98822 | -0.22569 | 0.98821 | -0.22603 | 1.2118

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56181 | 0.14295

## res_load
| p_mw | q_mvar
0 | 0.0044921 | 0.0011258
1 | 0.0029627 | 0.00074253
2 | 0.0031734 | 0.00079534
3 | 0.0027343 | 0.00068527
4 | 0.0027716 | 0.00069464
5 | 0.0024108 | 0.0006042
6 | 0.0031471 | 0.00078873
7 | 0.0063496 | 0.0015914
8 | 0.0021853 | 0.00054768
9 | 0.0051514 | 0.0012911
10 | 0.0035354 | 0.00088606
11 | 0.015362 | 0.00385
12 | 0.0021339 | 0.0005348
13 | 0.0036838 | 0.00092326
14 | 0.01091 | 0.0027343
15 | 0.0026655 | 0.00066805
16 | 0.0019951 | 0.00050001
17 | 0.0050503 | 0.0012657
18 | 0.0056609 | 0.0014188
19 | 0.0019557 | 0.00049014
20 | 0.0033392 | 0.00083689
21 | 0.011109 | 0.0027843
22 | 0.0036922 | 0.00092535
23 | 0.0056464 | 0.0014151
24 | 0.0035733 | 0.00089556
25 | 0.010752 | 0.0026948
26 | 0.0039228 | 0.00098314
27 | 0.0087438 | 0.0021914
28 | 0.0028054 | 0.00070309
29 | 0.0021715 | 0.00054422
30 | 0.0043018 | 0.0010781
31 | 0.0023175 | 0.00058082
32 | 0.0029293 | 0.00073416
33 | 0.001531 | 0.00038371
34 | 0.002885 | 0.00072305
35 | 0.01316 | 0.0032983
36 | 0.0028458 | 0.00071322
37 | 0.0093487 | 0.002343
38 | 0.0044214 | 0.0011081
39 | 0.0053273 | 0.0013351
40 | 0.0060624 | 0.0015194
41 | 0.011938 | 0.0029919
42 | 0.010567 | 0.0026484
43 | 0.0090184 | 0.0022602
44 | 0.0049294 | 0.0012354
45 | 0.006949 | 0.0017416
46 | 0.0099318 | 0.0024891
47 | 0.0047913 | 0.0012008
48 | 0.0024084 | 0.00060361
49 | 0.0035119 | 0.00088017
50 | 0.0036735 | 0.00092067
51 | 0.012187 | 0.0030543
52 | 0.0078869 | 0.0019766
53 | 0.0052642 | 0.0013193
54 | 0.0125 | 0.0031327
55 | 0.0034081 | 0.00085416
56 | 0.0045198 | 0.0011328
57 | 0.0029008 | 0.000727
58 | 0.0070505 | 0.001767
59 | 0.0024677 | 0.00061846
60 | 0.0068642 | 0.0017203
61 | 0.00725 | 0.001817
62 | 0.0067561 | 0.0016932
63 | 0.0093237 | 0.0023367
64 | 0.0027118 | 0.00067963
65 | 0.0038944 | 0.00097604
66 | 0.0060711 | 0.0015216
67 | 0.021851 | 0.0054764
68 | 0.0086195 | 0.0021602
69 | 0.0080092 | 0.0020073
70 | 0.0038711 | 0.00097019
71 | 0.017905 | 0.0044873
72 | 0.005629 | 0.0014108
73 | 0.0024727 | 0.00061971
74 | 0.0055966 | 0.0014026
75 | 0.012686 | 0.0031795
76 | 0.0047285 | 0.0011851
77 | 0.0060256 | 0.0015102
78 | 0.0047433 | 0.0011888
79 | 0.003694 | 0.00092581
80 | 0.0026178 | 0.00065607
81 | 0.010354 | 0.0025951
82 | 0.0094964 | 0.00238
83 | 0.0038996 | 0.00097733
84 | 0.0057324 | 0.0014367
85 | 0.0046866 | 0.0011746
86 | 0.0027745 | 0.00069534
87 | 0.012188 | 0.0030545
88 | 0.0066323 | 0.0016622
89 | 0.0019813 | 0.00049655
90 | 0.0066928 | 0.0016774
91 | 0.006164 | 0.0015448
92 | 0.0035283 | 0.00088426
93 | 0.0029294 | 0.00073417

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1