## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5269-2_1_3_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_5269-2_1_3_node_102 | 0.4 | n |  | TRUE
2 | bus_LV_5269-2_1_3_node_30 | 0.4 | n |  | TRUE
3 | bus_LV_5269-2_1_3_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_5269-2_1_3_node_32 | 0.4 | n |  | TRUE
5 | bus_LV_5269-2_1_3_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_5269-2_1_3_node_33 | 0.4 | n |  | TRUE
7 | bus_LV_5269-2_1_3_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_5269-2_1_3_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_5269-2_1_3_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_5269-2_1_3_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_5269-2_1_3_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_5269-2_1_3_node_45 | 0.4 | n |  | TRUE
13 | bus_LV_5269-2_1_3_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_5269-2_1_3_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_5269-2_1_3_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_5269-2_1_3_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_5269-2_1_3_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_5269-2_1_3_node_59 | 0.4 | n |  | TRUE
19 | bus_LV_5269-2_1_3_node_57 | 0.4 | n |  | TRUE
20 | bus_LV_5269-2_1_3_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_5269-2_1_3_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_5269-2_1_3_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_5269-2_1_3_node_48 | 0.4 | n |  | TRUE
24 | bus_LV_5269-2_1_3_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_5269-2_1_3_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_5269-2_1_3_node_65 | 0.4 | n |  | TRUE
27 | bus_LV_5269-2_1_3_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_5269-2_1_3_node_96 | 0.4 | n |  | TRUE
29 | bus_LV_5269-2_1_3_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_5269-2_1_3_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_5269-2_1_3_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_5269-2_1_3_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_5269-2_1_3_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_5269-2_1_3_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_5269-2_1_3_node_120 | 0.4 | n |  | TRUE
36 | bus_LV_5269-2_1_3_node_118 | 0.4 | n |  | TRUE
37 | bus_LV_5269-2_1_3_node_115 | 0.4 | n |  | TRUE
38 | bus_LV_5269-2_1_3_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_5269-2_1_3_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_5269-2_1_3_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_5269-2_1_3_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_5269-2_1_3_node_122 | 0.4 | n |  | TRUE
43 | bus_LV_5269-2_1_3_node_98 | 0.4 | n |  | TRUE
44 | bus_LV_5269-2_1_3_node_100 | 0.4 | n |  | TRUE
45 | bus_LV_5269-2_1_3_node_103 | 0.4 | n |  | TRUE
46 | bus_LV_5269-2_1_3_node_127 | 0.4 | n |  | TRUE
47 | bus_LV_5269-2_1_3_node_116 | 0.4 | n |  | TRUE
48 | bus_LV_5269-2_1_3_node_117 | 0.4 | n |  | TRUE
49 | bus_LV_5269-2_1_3_node_121 | 0.4 | n |  | TRUE
50 | bus_LV_5269-2_1_3_node_119 | 0.4 | n |  | TRUE
51 | bus_LV_5269-2_1_3_node_123 | 0.4 | n |  | TRUE
52 | bus_LV_5269-2_1_3_node_124 | 0.4 | n |  | TRUE
53 | bus_LV_5269-2_1_3_node_125 | 0.4 | n |  | TRUE
54 | bus_LV_5269-2_1_3_node_126 | 0.4 | n |  | TRUE
55 | bus_MV_76_0_node_165 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5269-2_1_3_load_128 | 0 | 0.0023791 | 0.00059626 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5269-2_1_3_load_30 | 2 | 0.0048307 | 0.0012107 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5269-2_1_3_load_31 | 3 | 0.005665 | 0.0014198 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5269-2_1_3_load_32 | 4 | 0.0020649 | 0.00051751 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5269-2_1_3_load_44 | 5 | 0.0020427 | 0.00051194 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5269-2_1_3_load_33 | 6 | 0.0056506 | 0.0014162 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5269-2_1_3_load_34 | 7 | 0.0042475 | 0.0010645 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5269-2_1_3_load_36 | 9 | 0.0023179 | 0.00058092 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5269-2_1_3_load_43 | 11 | 0.0031471 | 0.00078873 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5269-2_1_3_load_45 | 12 | 0.0020735 | 0.00051966 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5269-2_1_3_load_38 | 13 | 0.0049107 | 0.0012307 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5269-2_1_3_load_42 | 14 | 0.0035427 | 0.00088789 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5269-2_1_3_load_40 | 16 | 0.0037743 | 0.00094594 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5269-2_1_3_load_41 | 17 | 0.0021588 | 0.00054106 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5269-2_1_3_load_59 | 18 | 0.0022464 | 0.000563 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5269-2_1_3_load_57 | 19 | 0.004504 | 0.0011288 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5269-2_1_3_load_60 | 20 | 0.0026195 | 0.0006565 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5269-2_1_3_load_46 | 21 | 0.003919 | 0.00098218 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5269-2_1_3_load_48 | 23 | 0.0036419 | 0.00091276 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5269-2_1_3_load_49 | 24 | 0.0031811 | 0.00079727 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5269-2_1_3_load_50 | 25 | 0.0038637 | 0.00096833 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5269-2_1_3_load_65 | 26 | 0.0028182 | 0.0007063 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5269-2_1_3_load_96 | 28 | 0.0039586 | 0.00099213 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5269-2_1_3_load_97 | 29 | 0.0022813 | 0.00057175 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5269-2_1_3_load_52 | 30 | 0.0087138 | 0.0021839 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5269-2_1_3_load_53 | 31 | 0.0062704 | 0.0015715 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5269-2_1_3_load_56 | 34 | 0.0019407 | 0.00048638 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5269-2_1_3_load_118 | 36 | 0.0047658 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5269-2_1_3_load_115 | 37 | 0.0047366 | 0.0011871 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5269-2_1_3_load_58 | 38 | 0.0039956 | 0.0010014 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5269-2_1_3_load_66 | 39 | 0.0023921 | 0.00059952 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5269-2_1_3_load_63 | 40 | 0.002954 | 0.00074033 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5269-2_1_3_load_64 | 41 | 0.0025421 | 0.00063711 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5269-2_1_3_load_122 | 42 | 0.0046512 | 0.0011657 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5269-2_1_3_load_98 | 43 | 0.0015001 | 0.00037596 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5269-2_1_3_load_103 | 45 | 0.0016789 | 0.00042077 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5269-2_1_3_load_127 | 46 | 0.0040448 | 0.0010137 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5269-2_1_3_load_116 | 47 | 0.003144 | 0.00078796 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5269-2_1_3_load_117 | 48 | 0.0035857 | 0.00089866 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5269-2_1_3_load_121 | 49 | 0.0034356 | 0.00086105 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5269-2_1_3_load_119 | 50 | 0.0038867 | 0.00097409 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5269-2_1_3_load_123 | 51 | 0.0075386 | 0.0018893 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5269-2_1_3_load_124 | 52 | 0.0040041 | 0.0010035 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5269-2_1_3_load_125 | 53 | 0.0048809 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5269-2_1_3_load_126 | 54 | 0.0063586 | 0.0015936 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5269-2_1_3_line_0 |  | 0 | 1 | 0.036608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5269-2_1_3_line_1 |  | 1 | 29 | 0.011652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5269-2_1_3_line_2 |  | 1 | 44 | 0.014562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5269-2_1_3_line_3 |  | 2 | 3 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5269-2_1_3_line_4 |  | 3 | 4 | 0.01759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5269-2_1_3_line_5 |  | 4 | 5 | 0.020411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5269-2_1_3_line_6 |  | 5 | 10 | 0.012088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5269-2_1_3_line_7 |  | 6 | 7 | 0.0089643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5269-2_1_3_line_8 |  | 6 | 8 | 0.042956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5269-2_1_3_line_9 |  | 8 | 9 | 0.0080596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5269-2_1_3_line_10 |  | 8 | 10 | 0.037027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5269-2_1_3_line_11 |  | 9 | 11 | 0.012143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5269-2_1_3_line_12 |  | 10 | 12 | 0.013662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5269-2_1_3_line_13 |  | 12 | 21 | 0.021418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5269-2_1_3_line_14 |  | 13 | 14 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5269-2_1_3_line_15 |  | 14 | 16 | 0.027756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5269-2_1_3_line_16 |  | 15 | 16 | 0.069718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5269-2_1_3_line_17 |  | 15 | 17 | 0.013921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5269-2_1_3_line_18 |  | 15 | 18 | 0.030008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5269-2_1_3_line_19 |  | 17 | 19 | 0.036914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5269-2_1_3_line_20 |  | 17 | 20 | 0.024559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5269-2_1_3_line_21 |  | 19 | 38 | 0.011993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5269-2_1_3_line_22 |  | 21 | 22 | 0.019803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5269-2_1_3_line_23 |  | 22 | 23 | 0.0074151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5269-2_1_3_line_24 |  | 22 | 24 | 0.025338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5269-2_1_3_line_25 |  | 23 | 25 | 0.028096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5269-2_1_3_line_26 |  | 24 | 26 | 0.063916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5269-2_1_3_line_27 |  | 25 | 27 | 0.034702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5269-2_1_3_line_28 |  | 26 | 40 | 0.020549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5269-2_1_3_line_29 |  | 27 | 28 | 0.020717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5269-2_1_3_line_30 |  | 27 | 29 | 0.015399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5269-2_1_3_line_31 |  | 28 | 42 | 0.022878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5269-2_1_3_line_32 |  | 30 | 31 | 0.01693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5269-2_1_3_line_33 |  | 31 | 32 | 0.026893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5269-2_1_3_line_34 |  | 32 | 33 | 0.014977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5269-2_1_3_line_35 |  | 32 | 34 | 0.0075736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5269-2_1_3_line_36 |  | 33 | 35 | 0.017904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5269-2_1_3_line_37 |  | 33 | 36 | 0.032014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5269-2_1_3_line_38 |  | 34 | 37 | 0.019862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5269-2_1_3_line_39 |  | 35 | 42 | 0.068019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5269-2_1_3_line_40 |  | 36 | 50 | 0.0099833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5269-2_1_3_line_41 |  | 37 | 47 | 0.053932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5269-2_1_3_line_42 |  | 38 | 39 | 0.061083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5269-2_1_3_line_43 |  | 39 | 41 | 0.021949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5269-2_1_3_line_44 |  | 40 | 41 | 0.0015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5269-2_1_3_line_45 |  | 43 | 44 | 0.016774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5269-2_1_3_line_46 |  | 44 | 45 | 0.038565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5269-2_1_3_line_47 |  | 45 | 46 | 0.0036518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5269-2_1_3_line_48 |  | 46 | 54 | 0.031678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5269-2_1_3_line_49 |  | 47 | 48 | 0.01292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5269-2_1_3_line_50 |  | 48 | 49 | 0.035678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5269-2_1_3_line_51 |  | 49 | 51 | 0.030248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5269-2_1_3_line_52 |  | 51 | 52 | 0.050769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5269-2_1_3_line_53 |  | 53 | 54 | 0.039393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5269-2_1_3_trafo_47 | 0.63 MVA 20/0.4 kV | 55 | 22 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2723119.8776 | 1079750.1189 | 2723153.4431 | 1079764.9633
1 | 2723119.8776 | 1079750.1189 | 2723127.0407 | 1079740.9291
2 | 2723110.5993 | 1079761.3619 | 2723119.8776 | 1079750.1189
3 | 2723247.1815 | 1079578.9083 | 2723238.8309 | 1079588.0492 | 2723234.996 | 1079593.6217
4 | 2723227.4455 | 1079609.3849 | 2723231.5707 | 1079598.599 | 2723234.996 | 1079593.6217
5 | 2723223.7431 | 1079629.4209 | 2723226.7472 | 1079611.2107 | 2723227.4455 | 1079609.3849
6 | 2723224.3255 | 1079641.4392 | 2723223.4088 | 1079631.4468 | 2723223.7431 | 1079629.4209
7 | 2723279.5422 | 1079584.7177 | 2723287.1637 | 1079579.9984
8 | 2723246.9154 | 1079612.4081 | 2723270.2791 | 1079590.4535 | 2723279.5422 | 1079584.7177
9 | 2723246.9154 | 1079612.4081 | 2723249.7474 | 1079604.8625
10 | 2723224.3255 | 1079641.4392 | 2723232.0823 | 1079634.7579 | 2723238.7494 | 1079624.7187 | 2723246.9154 | 1079612.4081
11 | 2723255.0131 | 1079593.9942 | 2723252.1465 | 1079598.4704 | 2723249.7474 | 1079604.8625
12 | 2723224.3255 | 1079641.4392 | 2723217.3674 | 1079649.3488 | 2723215.5455 | 1079651.8913
13 | 2723215.5455 | 1079651.8913 | 2723203.0703 | 1079669.3005
14 | 2723301.4273 | 1079665.6464 | 2723316.2849 | 1079638.9429
15 | 2723301.4273 | 1079665.6464 | 2723300.5374 | 1079669.6897 | 2723299.7302 | 1079675.7889 | 2723301.4641 | 1079693.1665
16 | 2723310.6842 | 1079762.1733 | 2723305.5503 | 1079737.1512 | 2723304.8609 | 1079728.6089 | 2723302.7917 | 1079706.4731 | 2723301.4641 | 1079693.1665
17 | 2723310.6842 | 1079762.1733 | 2723302.7919 | 1079773.6404
18 | 2723310.6842 | 1079762.1733 | 2723332.413 | 1079741.4764
19 | 2723302.7919 | 1079773.6404 | 2723281.8635 | 1079804.048
20 | 2723302.7919 | 1079773.6404 | 2723314.3836 | 1079795.2912
21 | 2723281.8635 | 1079804.048 | 2723276.9533 | 1079811.1822 | 2723275.6802 | 1079814.2615
22 | 2723191.5359 | 1079685.3974 | 2723193.2948 | 1079682.9422 | 2723203.0703 | 1079669.3005
23 | 2723191.5359 | 1079685.3974 | 2723188.7946 | 1079688.4108 | 2723186.3595 | 1079690.6988
24 | 2723210.4456 | 1079702.3252 | 2723191.5359 | 1079685.3974
25 | 2723186.3595 | 1079690.6988 | 2723184.5892 | 1079692.3621 | 2723173.4666 | 1079699.5203 | 2723163.7136 | 1079707.2425
26 | 2723210.4456 | 1079702.3252 | 2723230.3569 | 1079763.0607
27 | 2723136.5075 | 1079728.7838 | 2723163.7136 | 1079707.2425
28 | 2723230.3569 | 1079763.0607 | 2723223.1173 | 1079782.2923
29 | 2723136.5075 | 1079728.7838 | 2723147.3187 | 1079711.1109
30 | 2723136.5075 | 1079728.7838 | 2723127.0407 | 1079740.9291
31 | 2723159.2577 | 1079691.5947 | 2723147.3187 | 1079711.1109
32 | 2723184.1511 | 1079562.3856 | 2723179.5592 | 1079578.6812
33 | 2723174.2593 | 1079604.9898 | 2723175.4954 | 1079594.5739 | 2723179.3358 | 1079579.4739 | 2723179.5592 | 1079578.6812
34 | 2723174.2593 | 1079604.9898 | 2723177.668 | 1079606.6266 | 2723183.9677 | 1079615.905
35 | 2723174.2593 | 1079604.9898 | 2723167.6364 | 1079604.3889 | 2723166.7289 | 1079604.5601
36 | 2723191.7213 | 1079632.0512 | 2723183.9677 | 1079615.905
37 | 2723183.9677 | 1079615.905 | 2723156.2698 | 1079631.958
38 | 2723166.7289 | 1079604.5601 | 2723160.5549 | 1079605.7246 | 2723148.443 | 1079611.8653
39 | 2723191.7213 | 1079632.0512 | 2723189.4534 | 1079639.3107 | 2723186.7658 | 1079645.0494 | 2723176.9222 | 1079662.7189 | 2723159.2577 | 1079691.5947
40 | 2723147.6323 | 1079636.964 | 2723156.2698 | 1079631.958
41 | 2723148.443 | 1079611.8653 | 2723137.4609 | 1079617.4332 | 2723099.2595 | 1079633.9488
42 | 2723275.6802 | 1079814.2615 | 2723215.3947 | 1079804.4246
43 | 2723215.3947 | 1079804.4246 | 2723216.4323 | 1079800.0505 | 2723222.5814 | 1079783.7157
44 | 2723223.1173 | 1079782.2923 | 2723222.5814 | 1079783.7157
45 | 2723110.5993 | 1079761.3619 | 2723100.6253 | 1079774.8489
46 | 2723110.5993 | 1079761.3619 | 2723082.8184 | 1079734.6137
47 | 2723082.8184 | 1079734.6137 | 2723080.1878 | 1079732.0809
48 | 2723080.1878 | 1079732.0809 | 2723074.9871 | 1079727.0735 | 2723057.5118 | 1079724.1185 | 2723051.6242 | 1079720.8477
49 | 2723099.2595 | 1079633.9488 | 2723092.8405 | 1079636.7239 | 2723088.2129 | 1079640.4274
50 | 2723060.3575 | 1079662.7202 | 2723088.2129 | 1079640.4274
51 | 2723060.3575 | 1079662.7202 | 2723060.005 | 1079663.0023 | 2723053.2689 | 1079664.1671 | 2723034.7628 | 1079675.3128 | 2723033.7196 | 1079676.1812
52 | 2723033.7196 | 1079676.1812 | 2723026.0389 | 1079682.5753 | 2723009.7132 | 1079696.556 | 2723000.6577 | 1079713.578
53 | 2723069.5818 | 1079710.3836 | 2723059.4421 | 1079702.4084 | 2723046.9344 | 1079712.3743 | 2723048.4767 | 1079719.0992 | 2723051.6242 | 1079720.8477

## bus_geodata
| x | y | coords
0 | 2723153.4431 | 1079764.9633
1 | 2723119.8776 | 1079750.1189
2 | 2723247.1815 | 1079578.9083
3 | 2723234.996 | 1079593.6217
4 | 2723227.4455 | 1079609.3849
5 | 2723223.7431 | 1079629.4209
6 | 2723279.5422 | 1079584.7177
7 | 2723287.1637 | 1079579.9984
8 | 2723246.9154 | 1079612.4081
9 | 2723249.7474 | 1079604.8625
10 | 2723224.3255 | 1079641.4392
11 | 2723255.0131 | 1079593.9942
12 | 2723215.5455 | 1079651.8913
13 | 2723316.2849 | 1079638.9429
14 | 2723301.4273 | 1079665.6464
15 | 2723310.6842 | 1079762.1733
16 | 2723301.4641 | 1079693.1665
17 | 2723302.7919 | 1079773.6404
18 | 2723332.413 | 1079741.4764
19 | 2723281.8635 | 1079804.048
20 | 2723314.3836 | 1079795.2912
21 | 2723203.0703 | 1079669.3005
22 | 2723191.5359 | 1079685.3974
23 | 2723186.3595 | 1079690.6988
24 | 2723210.4456 | 1079702.3252
25 | 2723163.7136 | 1079707.2425
26 | 2723230.3569 | 1079763.0607
27 | 2723136.5075 | 1079728.7838
28 | 2723147.3187 | 1079711.1109
29 | 2723127.0407 | 1079740.9291
30 | 2723184.1511 | 1079562.3856
31 | 2723179.5592 | 1079578.6812
32 | 2723174.2593 | 1079604.9898
33 | 2723183.9677 | 1079615.905
34 | 2723166.7289 | 1079604.5601
35 | 2723191.7213 | 1079632.0512
36 | 2723156.2698 | 1079631.958
37 | 2723148.443 | 1079611.8653
38 | 2723275.6802 | 1079814.2615
39 | 2723215.3947 | 1079804.4246
40 | 2723223.1173 | 1079782.2923
41 | 2723222.5814 | 1079783.7157
42 | 2723159.2577 | 1079691.5947
43 | 2723100.6253 | 1079774.8489
44 | 2723110.5993 | 1079761.3619
45 | 2723082.8184 | 1079734.6137
46 | 2723080.1878 | 1079732.0809
47 | 2723099.2595 | 1079633.9488
48 | 2723088.2129 | 1079640.4274
49 | 2723060.3575 | 1079662.7202
50 | 2723147.6323 | 1079636.964
51 | 2723033.7196 | 1079676.1812
52 | 2723000.6577 | 1079713.578
53 | 2723069.5818 | 1079710.3836
54 | 2723051.6242 | 1079720.8477
55 | 2723210.4456 | 1079702.3252

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1