## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5396-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5396-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5396-1_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5396-1_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_5396-1_0_3_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_5396-1_0_3_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_5396-1_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5396-1_0_3_node_55 | 0.4 | n |  | TRUE
8 | bus_LV_5396-1_0_3_node_56 | 0.4 | n |  | TRUE
9 | bus_LV_5396-1_0_3_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_5396-1_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_5396-1_0_3_node_99 | 0.4 | n |  | TRUE
12 | bus_LV_5396-1_0_3_node_102 | 0.4 | n |  | TRUE
13 | bus_LV_5396-1_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_5396-1_0_3_node_96 | 0.4 | n |  | TRUE
15 | bus_LV_5396-1_0_3_node_95 | 0.4 | n |  | TRUE
16 | bus_LV_5396-1_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_5396-1_0_3_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_5396-1_0_3_node_94 | 0.4 | n |  | TRUE
19 | bus_LV_5396-1_0_3_node_92 | 0.4 | n |  | TRUE
20 | bus_LV_5396-1_0_3_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_5396-1_0_3_node_97 | 0.4 | n |  | TRUE
22 | bus_LV_5396-1_0_3_node_104 | 0.4 | n |  | TRUE
23 | bus_LV_5396-1_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_5396-1_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_5396-1_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_5396-1_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_5396-1_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_5396-1_0_3_node_111 | 0.4 | n |  | TRUE
29 | bus_LV_5396-1_0_3_node_122 | 0.4 | n |  | TRUE
30 | bus_LV_5396-1_0_3_node_112 | 0.4 | n |  | TRUE
31 | bus_LV_5396-1_0_3_node_110 | 0.4 | n |  | TRUE
32 | bus_LV_5396-1_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_5396-1_0_3_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_5396-1_0_3_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_5396-1_0_3_node_18 | 0.4 | n |  | TRUE
36 | bus_LV_5396-1_0_3_node_19 | 0.4 | n |  | TRUE
37 | bus_LV_5396-1_0_3_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_5396-1_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_5396-1_0_3_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_5396-1_0_3_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_5396-1_0_3_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_5396-1_0_3_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_5396-1_0_3_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_5396-1_0_3_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_5396-1_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_5396-1_0_3_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_5396-1_0_3_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_5396-1_0_3_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_5396-1_0_3_node_121 | 0.4 | n |  | TRUE
50 | bus_LV_5396-1_0_3_node_123 | 0.4 | n |  | TRUE
51 | bus_LV_5396-1_0_3_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_5396-1_0_3_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_5396-1_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_5396-1_0_3_node_120 | 0.4 | n |  | TRUE
55 | bus_LV_5396-1_0_3_node_124 | 0.4 | n |  | TRUE
56 | bus_LV_5396-1_0_3_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_5396-1_0_3_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_5396-1_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_5396-1_0_3_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_5396-1_0_3_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_5396-1_0_3_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_5396-1_0_3_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_5396-1_0_3_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_5396-1_0_3_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_5396-1_0_3_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_5396-1_0_3_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_5396-1_0_3_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_5396-1_0_3_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_5396-1_0_3_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_5396-1_0_3_node_156 | 0.4 | n |  | TRUE
71 | bus_LV_5396-1_0_3_node_117 | 0.4 | n |  | TRUE
72 | bus_LV_5396-1_0_3_node_77 | 0.4 | n |  | TRUE
73 | bus_LV_5396-1_0_3_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_5396-1_0_3_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_5396-1_0_3_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_5396-1_0_3_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_5396-1_0_3_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_5396-1_0_3_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_5396-1_0_3_node_65 | 0.4 | n |  | TRUE
80 | bus_LV_5396-1_0_3_node_78 | 0.4 | n |  | TRUE
81 | bus_LV_5396-1_0_3_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_5396-1_0_3_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_5396-1_0_3_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_5396-1_0_3_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_5396-1_0_3_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_5396-1_0_3_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_5396-1_0_3_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_5396-1_0_3_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_5396-1_0_3_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_5396-1_0_3_node_71 | 0.4 | n |  | TRUE
91 | bus_LV_5396-1_0_3_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_5396-1_0_3_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_5396-1_0_3_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_5396-1_0_3_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_5396-1_0_3_node_85 | 0.4 | n |  | TRUE
96 | bus_LV_5396-1_0_3_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_5396-1_0_3_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_5396-1_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_5396-1_0_3_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_5396-1_0_3_node_108 | 0.4 | n |  | TRUE
101 | bus_LV_5396-1_0_3_node_73 | 0.4 | n |  | TRUE
102 | bus_LV_5396-1_0_3_node_74 | 0.4 | n |  | TRUE
103 | bus_LV_5396-1_0_3_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_5396-1_0_3_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_5396-1_0_3_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_5396-1_0_3_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_5396-1_0_3_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_5396-1_0_3_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_5396-1_0_3_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_5396-1_0_3_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_5396-1_0_3_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_5396-1_0_3_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_5396-1_0_3_node_113 | 0.4 | n |  | TRUE
114 | bus_LV_5396-1_0_3_node_154 | 0.4 | n |  | TRUE
115 | bus_LV_5396-1_0_3_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_5396-1_0_3_node_155 | 0.4 | n |  | TRUE
117 | bus_LV_5396-1_0_3_node_116 | 0.4 | n |  | TRUE
118 | bus_LV_5396-1_0_3_node_114 | 0.4 | n |  | TRUE
119 | bus_LV_5396-1_0_3_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_5396-1_0_3_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_5396-1_0_3_node_118 | 0.4 | n |  | TRUE
122 | bus_MV_65_1_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5396-1_0_3_load_0 | 0 | 0.0033148 | 0.00083076 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5396-1_0_3_load_4 | 3 | 0.0039933 | 0.0010008 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5396-1_0_3_load_37 | 4 | 0.0068722 | 0.0017223 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5396-1_0_3_load_26 | 5 | 0.0051368 | 0.0012874 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5396-1_0_3_load_55 | 7 | 0.0050889 | 0.0012754 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5396-1_0_3_load_54 | 9 | 0.0051353 | 0.001287 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5396-1_0_3_load_99 | 11 | 0.0023454 | 0.00058782 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5396-1_0_3_load_96 | 14 | 0.0072136 | 0.0018079 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5396-1_0_3_load_95 | 15 | 0.0012402 | 0.00031083 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5396-1_0_3_load_94 | 18 | 0.0045787 | 0.0011475 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5396-1_0_3_load_92 | 19 | 0.0046843 | 0.001174 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5396-1_0_3_load_97 | 21 | 0.0011972 | 0.00030005 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5396-1_0_3_load_11 | 23 | 0.004033 | 0.0010108 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5396-1_0_3_load_13 | 24 | 0.0010456 | 0.00026206 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5396-1_0_3_load_12 | 25 | 0.0036178 | 0.00090671 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5396-1_0_3_load_14 | 26 | 0.0015361 | 0.00038498 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5396-1_0_3_load_15 | 27 | 0.0013389 | 0.00033556 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5396-1_0_3_load_122 | 29 | 0.0018383 | 0.00046072 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5396-1_0_3_load_112 | 30 | 0.0014602 | 0.00036595 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5396-1_0_3_load_16 | 33 | 0.0025815 | 0.00064698 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5396-1_0_3_load_17 | 34 | 0.0056398 | 0.0014135 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5396-1_0_3_load_18 | 35 | 0.0027277 | 0.00068362 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5396-1_0_3_load_20 | 37 | 0.0033601 | 0.00084213 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5396-1_0_3_load_29 | 38 | 0.0041549 | 0.0010413 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5396-1_0_3_load_57 | 39 | 0.0031961 | 0.00080103 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5396-1_0_3_load_27 | 40 | 0.004337 | 0.001087 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5396-1_0_3_load_21 | 41 | 0.0031356 | 0.00078584 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5396-1_0_3_load_22 | 42 | 0.0062721 | 0.0015719 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5396-1_0_3_load_23 | 43 | 0.0038709 | 0.00097014 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5396-1_0_3_load_25 | 44 | 0.0039762 | 0.00099654 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5396-1_0_3_load_42 | 47 | 0.0038696 | 0.0009698 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5396-1_0_3_load_123 | 50 | 0.00601 | 0.0015062 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5396-1_0_3_load_28 | 51 | 0.0031258 | 0.0007834 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5396-1_0_3_load_30 | 52 | 0.0032992 | 0.00082686 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5396-1_0_3_load_120 | 54 | 0.002152 | 0.00053935 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5396-1_0_3_load_124 | 55 | 0.0034854 | 0.00087353 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5396-1_0_3_load_60 | 56 | 0.0031962 | 0.00080103 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5396-1_0_3_load_39 | 57 | 0.0026615 | 0.00066704 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5396-1_0_3_load_41 | 58 | 0.0026603 | 0.00066674 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5396-1_0_3_load_44 | 60 | 0.0024514 | 0.00061437 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5396-1_0_3_load_45 | 61 | 0.0061116 | 0.0015317 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5396-1_0_3_load_53 | 62 | 0.0043194 | 0.0010825 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5396-1_0_3_load_46 | 64 | 0.0031247 | 0.00078311 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5396-1_0_3_load_47 | 65 | 0.0021589 | 0.00054106 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5396-1_0_3_load_48 | 66 | 0.0024067 | 0.00060317 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5396-1_0_3_load_49 | 67 | 0.0031233 | 0.00078278 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5396-1_0_3_load_50 | 68 | 0.003124 | 0.00078296 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5396-1_0_3_load_156 | 70 | 0.015255 | 0.0038233 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5396-1_0_3_load_77 | 72 | 0.0045976 | 0.0011523 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5396-1_0_3_load_59 | 73 | 0.0078652 | 0.0019712 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5396-1_0_3_load_93 | 74 | 0.0058222 | 0.0014592 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5396-1_0_3_load_61 | 75 | 0.0031962 | 0.00080103 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5396-1_0_3_load_63 | 77 | 0.003369 | 0.00084436 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5396-1_0_3_load_64 | 78 | 0.003371 | 0.00084486 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5396-1_0_3_load_65 | 79 | 0.0094213 | 0.0023612 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5396-1_0_3_load_78 | 80 | 0.003369 | 0.00084436 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5396-1_0_3_load_79 | 82 | 0.0094382 | 0.0023654 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5396-1_0_3_load_67 | 83 | 0.0019506 | 0.00048885 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5396-1_0_3_load_68 | 84 | 0.0020606 | 0.00051643 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5396-1_0_3_load_69 | 85 | 0.010144 | 0.0025424 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5396-1_0_3_load_81 | 89 | 0.0041266 | 0.0010342 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5396-1_0_3_load_71 | 90 | 0.00261 | 0.00065413 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5396-1_0_3_load_91 | 92 | 0.0026097 | 0.00065405 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5396-1_0_3_load_76 | 93 | 0.0031641 | 0.00079301 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5396-1_0_3_load_107 | 94 | 0.0039472 | 0.00098926 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5396-1_0_3_load_90 | 98 | 0.0055367 | 0.0013876 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5396-1_0_3_load_88 | 99 | 0.0025244 | 0.00063268 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5396-1_0_3_load_108 | 100 | 0.0037644 | 0.00094345 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5396-1_0_3_load_73 | 101 | 0.0037017 | 0.00092773 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5396-1_0_3_load_74 | 102 | 0.004679 | 0.0011727 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5396-1_0_3_load_80 | 103 | 0.0020599 | 0.00051627 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5396-1_0_3_load_84 | 105 | 0.0025243 | 0.00063264 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5396-1_0_3_load_87 | 106 | 0.0041287 | 0.0010347 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5396-1_0_3_load_100 | 107 | 0.0013618 | 0.00034129 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5396-1_0_3_load_98 | 108 | 0.0020665 | 0.00051792 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5396-1_0_3_load_101 | 109 | 0.001736 | 0.00043507 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5396-1_0_3_load_105 | 111 | 0.0082117 | 0.002058 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5396-1_0_3_load_113 | 113 | 0.0078051 | 0.0019561 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5396-1_0_3_load_154 | 114 | 0.0044825 | 0.0011234 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5396-1_0_3_load_155 | 116 | 0.0024229 | 0.00060723 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5396-1_0_3_load_114 | 118 | 0.0028763 | 0.00072086 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5396-1_0_3_load_109 | 119 | 0.0032022 | 0.00080256 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5396-1_0_3_load_119 | 120 | 0.0026701 | 0.0006692 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5396-1_0_3_load_118 | 121 | 0.0025829 | 0.00064733 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5396-1_0_3_line_0 |  | 0 | 1 | 0.027292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5396-1_0_3_line_1 |  | 1 | 2 | 0.031231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5396-1_0_3_line_2 |  | 1 | 3 | 0.034146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5396-1_0_3_line_3 |  | 2 | 4 | 0.056547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5396-1_0_3_line_4 |  | 3 | 5 | 0.012348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5396-1_0_3_line_5 |  | 5 | 16 | 0.035451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5396-1_0_3_line_6 |  | 6 | 7 | 0.015359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5396-1_0_3_line_7 |  | 6 | 8 | 0.083024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5396-1_0_3_line_8 |  | 6 | 9 | 0.019265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5396-1_0_3_line_9 |  | 7 | 17 | 0.04693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5396-1_0_3_line_10 |  | 8 | 18 | 0.019596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5396-1_0_3_line_11 |  | 8 | 19 | 0.013833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5396-1_0_3_line_12 |  | 9 | 20 | 0.013523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5396-1_0_3_line_13 |  | 10 | 11 | 0.061204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5396-1_0_3_line_14 |  | 10 | 12 | 0.064408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5396-1_0_3_line_15 |  | 11 | 21 | 0.040673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5396-1_0_3_line_16 |  | 12 | 22 | 0.056865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5396-1_0_3_line_17 |  | 13 | 14 | 0.048962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5396-1_0_3_line_18 |  | 13 | 15 | 0.022548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5396-1_0_3_line_19 |  | 15 | 18 | 0.01614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5396-1_0_3_line_20 |  | 16 | 42 | 0.011976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5396-1_0_3_line_21 |  | 17 | 73 | 0.014937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5396-1_0_3_line_22 |  | 19 | 74 | 0.036396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5396-1_0_3_line_23 |  | 20 | 39 | 0.023627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5396-1_0_3_line_24 |  | 20 | 36 | 0.022291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5396-1_0_3_line_25 |  | 21 | 108 | 0.018798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5396-1_0_3_line_26 |  | 22 | 113 | 0.065731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5396-1_0_3_line_27 |  | 23 | 24 | 0.0020459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5396-1_0_3_line_28 |  | 24 | 27 | 0.013056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5396-1_0_3_line_29 |  | 25 | 26 | 0.02805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5396-1_0_3_line_30 |  | 26 | 28 | 0.027505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5396-1_0_3_line_31 |  | 27 | 29 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5396-1_0_3_line_32 |  | 28 | 30 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5396-1_0_3_line_33 |  | 28 | 31 | 0.025402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5396-1_0_3_line_34 |  | 29 | 32 | 0.075799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5396-1_0_3_line_35 |  | 30 | 120 | 0.01069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5396-1_0_3_line_36 |  | 31 | 119 | 0.022853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5396-1_0_3_line_37 |  | 31 | 112 | 0.006405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5396-1_0_3_line_38 |  | 32 | 48 | 0.29101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5396-1_0_3_line_39 |  | 32 | 49 | 0.019056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5396-1_0_3_line_40 |  | 33 | 34 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5396-1_0_3_line_41 |  | 33 | 35 | 0.016552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5396-1_0_3_line_42 |  | 34 | 36 | 0.045618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5396-1_0_3_line_43 |  | 35 | 37 | 0.0043768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5396-1_0_3_line_44 |  | 36 | 38 | 0.021813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5396-1_0_3_line_45 |  | 38 | 40 | 0.01511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5396-1_0_3_line_46 |  | 39 | 56 | 0.013875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5396-1_0_3_line_47 |  | 40 | 51 | 0.018116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5396-1_0_3_line_48 |  | 41 | 42 | 0.038599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5396-1_0_3_line_49 |  | 41 | 43 | 0.008136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5396-1_0_3_line_50 |  | 43 | 44 | 0.03668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5396-1_0_3_line_51 |  | 44 | 45 | 0.030579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5396-1_0_3_line_52 |  | 45 | 46 | 0.032551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5396-1_0_3_line_53 |  | 46 | 47 | 0.051896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5396-1_0_3_line_54 |  | 47 | 53 | 0.0050521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5396-1_0_3_line_55 |  | 48 | 50 | 0.23788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5396-1_0_3_line_56 |  | 49 | 54 | 0.04999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5396-1_0_3_line_57 |  | 50 | 55 | 0.031018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5396-1_0_3_line_58 |  | 51 | 52 | 0.012593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5396-1_0_3_line_59 |  | 53 | 58 | 0.0081595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5396-1_0_3_line_60 |  | 53 | 57 | 0.019501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5396-1_0_3_line_61 |  | 54 | 61 | 0.022554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5396-1_0_3_line_62 |  | 55 | 117 | 0.044737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5396-1_0_3_line_63 |  | 56 | 75 | 0.015306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5396-1_0_3_line_64 |  | 58 | 59 | 0.040158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5396-1_0_3_line_65 |  | 59 | 60 | 0.040892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5396-1_0_3_line_66 |  | 59 | 61 | 0.014588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5396-1_0_3_line_67 |  | 60 | 62 | 0.0033876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5396-1_0_3_line_68 |  | 62 | 63 | 0.015456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5396-1_0_3_line_69 |  | 63 | 69 | 0.010117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5396-1_0_3_line_70 |  | 63 | 68 | 0.013248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5396-1_0_3_line_71 |  | 64 | 65 | 0.00081042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5396-1_0_3_line_72 |  | 64 | 66 | 0.021855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5396-1_0_3_line_73 |  | 66 | 67 | 0.00040285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5396-1_0_3_line_74 |  | 67 | 68 | 0.018763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5396-1_0_3_line_75 |  | 69 | 70 | 0.006689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5396-1_0_3_line_76 |  | 69 | 71 | 0.014291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5396-1_0_3_line_77 |  | 71 | 72 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5396-1_0_3_line_78 |  | 72 | 96 | 0.0044895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5396-1_0_3_line_79 |  | 73 | 76 | 0.0068404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5396-1_0_3_line_80 |  | 76 | 77 | 0.010952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5396-1_0_3_line_81 |  | 76 | 78 | 0.018508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5396-1_0_3_line_82 |  | 77 | 79 | 0.0043233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5396-1_0_3_line_83 |  | 78 | 80 | 0.011182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5396-1_0_3_line_84 |  | 79 | 81 | 0.0099754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_5396-1_0_3_line_85 |  | 80 | 82 | 0.0043204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5396-1_0_3_line_86 |  | 81 | 83 | 0.010786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_5396-1_0_3_line_87 |  | 81 | 84 | 0.018166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5396-1_0_3_line_88 |  | 83 | 85 | 0.0089316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_5396-1_0_3_line_89 |  | 85 | 86 | 0.0051364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_5396-1_0_3_line_90 |  | 86 | 90 | 0.010334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5396-1_0_3_line_91 |  | 86 | 91 | 0.019246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_5396-1_0_3_line_92 |  | 87 | 88 | 0.004893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5396-1_0_3_line_93 |  | 87 | 89 | 0.0033149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5396-1_0_3_line_94 |  | 88 | 106 | 0.021506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5396-1_0_3_line_95 |  | 89 | 103 | 0.0071802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5396-1_0_3_line_96 |  | 90 | 92 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5396-1_0_3_line_97 |  | 91 | 93 | 0.024754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5396-1_0_3_line_98 |  | 91 | 94 | 0.014718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5396-1_0_3_line_99 |  | 92 | 95 | 0.011692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5396-1_0_3_line_100 |  | 93 | 96 | 0.024467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5396-1_0_3_line_101 |  | 94 | 100 | 0.014402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5396-1_0_3_line_102 |  | 95 | 99 | 0.0020926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5396-1_0_3_line_103 |  | 95 | 104 | 0.005988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5396-1_0_3_line_104 |  | 96 | 102 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5396-1_0_3_line_105 |  | 97 | 98 | 0.0083501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5396-1_0_3_line_106 |  | 97 | 99 | 0.016109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5396-1_0_3_line_107 |  | 98 | 107 | 0.028546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5396-1_0_3_line_108 |  | 100 | 119 | 0.0089859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5396-1_0_3_line_109 |  | 101 | 102 | 0.022978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5396-1_0_3_line_110 |  | 103 | 104 | 0.0087129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_5396-1_0_3_line_111 |  | 104 | 105 | 0.016187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5396-1_0_3_line_112 |  | 107 | 108 | 0.015948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5396-1_0_3_line_113 |  | 109 | 110 | 0.057785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5396-1_0_3_line_114 |  | 110 | 111 | 0.021901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5396-1_0_3_line_115 |  | 110 | 112 | 0.028681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5396-1_0_3_line_116 |  | 112 | 114 | 0.065807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5396-1_0_3_line_117 |  | 113 | 118 | 0.013635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5396-1_0_3_line_118 |  | 115 | 116 | 0.10575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5396-1_0_3_line_119 |  | 115 | 117 | 0.017351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5396-1_0_3_line_120 |  | 120 | 121 | 0.0092558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5396-1_0_3_trafo_65 | 0.63 MVA 20/0.4 kV | 122 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2699768.8809 | 1115579.2951 | 2699774.3066 | 1115573.8588 | 2699782.0759 | 1115572.8861 | 2699793.8271 | 1115573.734
1 | 2699768.8809 | 1115579.2951 | 2699766.2062 | 1115610.4038
2 | 2699768.8809 | 1115579.2951 | 2699738.4965 | 1115563.7147
3 | 2699766.2062 | 1115610.4038 | 2699710.3106 | 1115601.8457
4 | 2699738.4965 | 1115563.7147 | 2699727.5091 | 1115558.0807
5 | 2699695.9641 | 1115541.9052 | 2699727.5091 | 1115558.0807
6 | 2699813.4303 | 1115508.1174 | 2699816.5288 | 1115493.074
7 | 2699895.4622 | 1115522.389 | 2699813.4303 | 1115508.1174
8 | 2699813.4303 | 1115508.1174 | 2699794.5346 | 1115504.3634
9 | 2699825.9963 | 1115447.1084 | 2699816.5288 | 1115493.074
10 | 2699895.4622 | 1115522.389 | 2699914.7711 | 1115525.7316
11 | 2699895.4622 | 1115522.389 | 2699897.9592 | 1115508.7832
12 | 2699781.2712 | 1115501.7283 | 2699794.5346 | 1115504.3634
13 | 2699991.4475 | 1115387.9432 | 2700051.6062 | 1115400.1214
14 | 2700051.6062 | 1115400.1214 | 2700059.481 | 1115336.2114
15 | 2699991.4475 | 1115387.9432 | 2699951.5833 | 1115379.8732
16 | 2700073.22 | 1115281.037 | 2700059.481 | 1115336.2114
17 | 2699952.8921 | 1115532.3309 | 2699961.8852 | 1115484.202
18 | 2699952.8921 | 1115532.3309 | 2699930.6742 | 1115528.4847
19 | 2699914.7711 | 1115525.7316 | 2699930.6742 | 1115528.4847
20 | 2699695.9641 | 1115541.9052 | 2699699.1783 | 1115530.3687
21 | 2699825.9963 | 1115447.1084 | 2699829.0077 | 1115432.4785
22 | 2699897.9592 | 1115508.7832 | 2699904.5291 | 1115472.985
23 | 2699781.2712 | 1115501.7283 | 2699785.562 | 1115478.4945
24 | 2699759.0477 | 1115500.2171 | 2699774.4976 | 1115500.3826 | 2699781.2712 | 1115501.7283
25 | 2699951.5833 | 1115379.8732 | 2699933.1595 | 1115376.1435
26 | 2700073.22 | 1115281.037 | 2700023.9052 | 1115277.1316 | 2700009.2435 | 1115270.0983
27 | 2699692.8521 | 1115257.8668 | 2699690.907 | 1115258.5013
28 | 2699678.6382 | 1115262.9172 | 2699681.7283 | 1115261.4958 | 2699690.907 | 1115258.5013
29 | 2699834.9037 | 1115266.2173 | 2699840.4301 | 1115238.717
30 | 2699829.6987 | 1115293.2176 | 2699830.0129 | 1115290.5545 | 2699834.9037 | 1115266.2173
31 | 2699659.2603 | 1115271.8313 | 2699678.6382 | 1115262.9172
32 | 2699829.6987 | 1115293.2176 | 2699821.3975 | 1115291.7689 | 2699818.5397 | 1115294.1344 | 2699817.6697 | 1115299.4417
33 | 2699829.6987 | 1115293.2176 | 2699854.7608 | 1115297.7889
34 | 2699591.3223 | 1115305.3815 | 2699606.3649 | 1115297.0012 | 2699647.4968 | 1115277.2427 | 2699659.2603 | 1115271.8313
35 | 2699815.9402 | 1115309.9911 | 2699817.6697 | 1115299.4417
36 | 2699854.7608 | 1115297.7889 | 2699850.8662 | 1115320.3074
37 | 2699861.0739 | 1115298.9714 | 2699854.7608 | 1115297.7889
38 | 2699399.885 | 1115249.3484 | 2699444.7259 | 1115322.5741 | 2699473.9946 | 1115331.9936 | 2699484.7649 | 1115350.9711 | 2699499.5133 | 1115376.9405 | 2699505.1097 | 1115369.5722 | 2699540.6704 | 1115322.6935 | 2699565.8849 | 1115308.5989 | 2699576.0487 | 1115306.2088 | 2699591.3223 | 1115305.3815
39 | 2699610.0071 | 1115309.391 | 2699591.3223 | 1115305.3815
40 | 2699781.6321 | 1115531.8279 | 2699783.7321 | 1115532.8216 | 2699794.2571 | 1115534.9859
41 | 2699810.47 | 1115538.3197 | 2699794.2571 | 1115534.9859
42 | 2699759.0477 | 1115500.2171 | 2699756.5745 | 1115509.2487 | 2699757.6003 | 1115516.8259 | 2699766.3761 | 1115524.6085 | 2699781.6321 | 1115531.8279
43 | 2699810.47 | 1115538.3197 | 2699814.7571 | 1115539.2013
44 | 2699759.0477 | 1115500.2171 | 2699747.5962 | 1115493.1242 | 2699742.5546 | 1115486.4767
45 | 2699742.5546 | 1115486.4767 | 2699733.4239 | 1115474.4378
46 | 2699785.562 | 1115478.4945 | 2699788.0817 | 1115464.8507
47 | 2699733.4239 | 1115474.4378 | 2699722.4764 | 1115460.0034
48 | 2699699.1783 | 1115530.3687 | 2699709.5379 | 1115493.1857
49 | 2699711.7215 | 1115485.3482 | 2699709.5379 | 1115493.1857
50 | 2699711.7215 | 1115485.3482 | 2699713.0928 | 1115480.4263 | 2699683.3845 | 1115469.7433
51 | 2699654.609 | 1115459.3957 | 2699683.3845 | 1115469.7433
52 | 2699654.609 | 1115459.3957 | 2699664.3484 | 1115428.3364
53 | 2699664.3484 | 1115428.3364 | 2699679.5565 | 1115378.7183
54 | 2699681.0371 | 1115373.888 | 2699679.5565 | 1115378.7183
55 | 2699399.885 | 1115249.3484 | 2699542.2886 | 1115214.3524 | 2699561.1545 | 1115209.715 | 2699585.1148 | 1115203.8271 | 2699604.8647 | 1115198.9708 | 2699630.8919 | 1115192.5765
56 | 2699610.0071 | 1115309.391 | 2699658.8823 | 1115319.8908
57 | 2699630.8919 | 1115192.5765 | 2699642.232 | 1115189.7904 | 2699661.0141 | 1115185.1761
58 | 2699713.7403 | 1115451.3658 | 2699717.1208 | 1115452.9421 | 2699722.4764 | 1115460.0034
59 | 2699681.0371 | 1115373.888 | 2699683.4282 | 1115366.0866
60 | 2699681.0371 | 1115373.888 | 2699662.2071 | 1115368.8152
61 | 2699658.8823 | 1115319.8908 | 2699680.9333 | 1115324.6279
62 | 2699704.823 | 1115177.7566 | 2699692.1536 | 1115177.5259 | 2699661.0141 | 1115185.1761
63 | 2699788.0817 | 1115464.8507 | 2699790.8614 | 1115449.7993
64 | 2699695.1961 | 1115327.692 | 2699683.4282 | 1115366.0866
65 | 2699695.1961 | 1115327.692 | 2699735.2774 | 1115335.7953
66 | 2699695.1961 | 1115327.692 | 2699680.9333 | 1115324.6279
67 | 2699738.5978 | 1115336.4666 | 2699735.2774 | 1115335.7953
68 | 2699753.7476 | 1115339.5294 | 2699738.5978 | 1115336.4666
69 | 2699753.7476 | 1115339.5294 | 2699763.6922 | 1115341.5388
70 | 2699753.7476 | 1115339.5294 | 2699751.1619 | 1115352.5225
71 | 2699742.9973 | 1115393.5494 | 2699743.1555 | 1115392.7546
72 | 2699743.1555 | 1115392.7546 | 2699747.4211 | 1115371.3201
73 | 2699747.4211 | 1115371.3201 | 2699747.4997 | 1115370.925
74 | 2699747.4997 | 1115370.925 | 2699751.1619 | 1115352.5225
75 | 2699764.8586 | 1115334.9539 | 2699763.6922 | 1115341.5388
76 | 2699763.6922 | 1115341.5388 | 2699777.7392 | 1115344.3829
77 | 2699777.7392 | 1115344.3829 | 2699791.7269 | 1115347.2098
78 | 2699796.1274 | 1115348.0991 | 2699791.7269 | 1115347.2098
79 | 2699830.3867 | 1115425.7785 | 2699829.0077 | 1115432.4785
80 | 2699830.3867 | 1115425.7785 | 2699832.5967 | 1115415.0516
81 | 2699830.3867 | 1115425.7785 | 2699848.5277 | 1115429.4477
82 | 2699833.4691 | 1115410.8172 | 2699832.5967 | 1115415.0516
83 | 2699848.5277 | 1115429.4477 | 2699859.4873 | 1115431.6643
84 | 2699835.482 | 1115401.047 | 2699833.4691 | 1115410.8172
85 | 2699863.722 | 1115432.5208 | 2699859.4873 | 1115431.6643
86 | 2699835.482 | 1115401.047 | 2699837.6569 | 1115390.4823
87 | 2699835.482 | 1115401.047 | 2699853.3229 | 1115404.4678
88 | 2699839.4579 | 1115381.7341 | 2699837.6569 | 1115390.4823
89 | 2699840.4936 | 1115376.7032 | 2699839.4579 | 1115381.7341
90 | 2699840.4936 | 1115376.7032 | 2699850.6598 | 1115378.5575
91 | 2699840.4936 | 1115376.7032 | 2699844.3721 | 1115357.8553
92 | 2699871.9591 | 1115413.0221 | 2699872.9109 | 1115408.2237
93 | 2699872.9109 | 1115408.2237 | 2699873.5575 | 1115404.9725
94 | 2699871.9591 | 1115413.0221 | 2699893.1235 | 1115416.8379
95 | 2699874.9583 | 1115397.9302 | 2699873.5575 | 1115404.9725
96 | 2699850.6598 | 1115378.5575 | 2699866.3184 | 1115381.4134
97 | 2699844.3721 | 1115357.8553 | 2699820.1092 | 1115352.9488
98 | 2699844.3721 | 1115357.8553 | 2699846.8804 | 1115343.3529
99 | 2699877.8206 | 1115383.5114 | 2699866.3184 | 1115381.4134
100 | 2699796.1274 | 1115348.0991 | 2699820.1092 | 1115352.9488
101 | 2699846.8804 | 1115343.3529 | 2699849.3348 | 1115329.1618
102 | 2699877.8206 | 1115383.5114 | 2699878.2282 | 1115381.4589
103 | 2699877.8206 | 1115383.5114 | 2699876.658 | 1115389.3848
104 | 2699796.1274 | 1115348.0991 | 2699792.6855 | 1115365.512
105 | 2699881.3662 | 1115365.6586 | 2699889.5503 | 1115367.3154
106 | 2699881.3662 | 1115365.6586 | 2699878.2282 | 1115381.4589
107 | 2699917.5289 | 1115372.9793 | 2699889.5503 | 1115367.3154
108 | 2699850.8662 | 1115320.3074 | 2699849.3348 | 1115329.1618
109 | 2699780.1453 | 1115376.2195 | 2699790.2131 | 1115378.0204 | 2699792.6855 | 1115365.512
110 | 2699876.658 | 1115389.3848 | 2699874.9583 | 1115397.9302
111 | 2699876.658 | 1115389.3848 | 2699892.6012 | 1115392.4383
112 | 2699933.1595 | 1115376.1435 | 2699917.5289 | 1115372.9793
113 | 2699889.3443 | 1115304.2739 | 2699946.1371 | 1115314.9349
114 | 2699885.5983 | 1115325.8479 | 2699889.3443 | 1115304.2739
115 | 2699861.0739 | 1115298.9714 | 2699889.3443 | 1115304.2739
116 | 2699873.1683 | 1115234.2969 | 2699861.0739 | 1115298.9714
117 | 2699996.95 | 1115264.201 | 2700009.2435 | 1115270.0983
118 | 2699722.095 | 1115179.4085 | 2699827.7814 | 1115188.376
119 | 2699704.823 | 1115177.7566 | 2699720.8149 | 1115179.2984 | 2699722.095 | 1115179.4085
120 | 2699814.4429 | 1115319.1251 | 2699815.9402 | 1115309.9911

## bus_geodata
| x | y | coords
0 | 2699793.8271 | 1115573.734
1 | 2699768.8809 | 1115579.2951
2 | 2699766.2062 | 1115610.4038
3 | 2699738.4965 | 1115563.7147
4 | 2699710.3106 | 1115601.8457
5 | 2699727.5091 | 1115558.0807
6 | 2699813.4303 | 1115508.1174
7 | 2699816.5288 | 1115493.074
8 | 2699895.4622 | 1115522.389
9 | 2699794.5346 | 1115504.3634
10 | 2700051.6062 | 1115400.1214
11 | 2699991.4475 | 1115387.9432
12 | 2700059.481 | 1115336.2114
13 | 2699952.8921 | 1115532.3309
14 | 2699961.8852 | 1115484.202
15 | 2699930.6742 | 1115528.4847
16 | 2699695.9641 | 1115541.9052
17 | 2699825.9963 | 1115447.1084
18 | 2699914.7712 | 1115525.7316
19 | 2699897.9592 | 1115508.7832
20 | 2699781.2712 | 1115501.7283
21 | 2699951.5833 | 1115379.8732
22 | 2700073.22 | 1115281.037
23 | 2699692.8521 | 1115257.8668
24 | 2699690.907 | 1115258.5013
25 | 2699840.4301 | 1115238.717
26 | 2699834.9037 | 1115266.2173
27 | 2699678.6382 | 1115262.9172
28 | 2699829.6987 | 1115293.2176
29 | 2699659.2603 | 1115271.8313
30 | 2699817.6697 | 1115299.4417
31 | 2699854.7608 | 1115297.7889
32 | 2699591.3223 | 1115305.3815
33 | 2699794.2571 | 1115534.9859
34 | 2699781.6321 | 1115531.8279
35 | 2699810.47 | 1115538.3197
36 | 2699759.0477 | 1115500.2171
37 | 2699814.7571 | 1115539.2013
38 | 2699742.5546 | 1115486.4767
39 | 2699785.562 | 1115478.4945
40 | 2699733.4239 | 1115474.4378
41 | 2699709.5379 | 1115493.1857
42 | 2699699.1783 | 1115530.3687
43 | 2699711.7215 | 1115485.3482
44 | 2699683.3845 | 1115469.7433
45 | 2699654.609 | 1115459.3957
46 | 2699664.3484 | 1115428.3364
47 | 2699679.5565 | 1115378.7183
48 | 2699399.885 | 1115249.3484
49 | 2699610.0071 | 1115309.391
50 | 2699630.8919 | 1115192.5765
51 | 2699722.4764 | 1115460.0034
52 | 2699713.7403 | 1115451.3658
53 | 2699681.0371 | 1115373.888
54 | 2699658.8823 | 1115319.8908
55 | 2699661.0141 | 1115185.1761
56 | 2699788.0817 | 1115464.8507
57 | 2699662.2071 | 1115368.8152
58 | 2699683.4282 | 1115366.0866
59 | 2699695.1961 | 1115327.692
60 | 2699735.2774 | 1115335.7953
61 | 2699680.9333 | 1115324.6279
62 | 2699738.5978 | 1115336.4666
63 | 2699753.7476 | 1115339.5294
64 | 2699743.1555 | 1115392.7546
65 | 2699742.9973 | 1115393.5494
66 | 2699747.4211 | 1115371.3201
67 | 2699747.4997 | 1115370.925
68 | 2699751.1619 | 1115352.5225
69 | 2699763.6922 | 1115341.5388
70 | 2699764.8586 | 1115334.9539
71 | 2699777.7392 | 1115344.3829
72 | 2699791.7268 | 1115347.2098
73 | 2699829.0077 | 1115432.4785
74 | 2699904.5291 | 1115472.985
75 | 2699790.8614 | 1115449.7993
76 | 2699830.3867 | 1115425.7785
77 | 2699832.5967 | 1115415.0516
78 | 2699848.5277 | 1115429.4477
79 | 2699833.4691 | 1115410.8172
80 | 2699859.4873 | 1115431.6643
81 | 2699835.482 | 1115401.047
82 | 2699863.722 | 1115432.5208
83 | 2699837.6569 | 1115390.4823
84 | 2699853.3229 | 1115404.4678
85 | 2699839.4579 | 1115381.7341
86 | 2699840.4936 | 1115376.7032
87 | 2699872.9109 | 1115408.2237
88 | 2699871.9591 | 1115413.0221
89 | 2699873.5575 | 1115404.9725
90 | 2699850.6598 | 1115378.5575
91 | 2699844.3721 | 1115357.8553
92 | 2699866.3184 | 1115381.4134
93 | 2699820.1092 | 1115352.9488
94 | 2699846.8804 | 1115343.3529
95 | 2699877.8206 | 1115383.5114
96 | 2699796.1274 | 1115348.0991
97 | 2699881.3662 | 1115365.6586
98 | 2699889.5503 | 1115367.3154
99 | 2699878.2282 | 1115381.4589
100 | 2699849.3348 | 1115329.1618
101 | 2699780.1453 | 1115376.2195
102 | 2699792.6855 | 1115365.512
103 | 2699874.9583 | 1115397.9302
104 | 2699876.658 | 1115389.3848
105 | 2699892.6012 | 1115392.4383
106 | 2699893.1235 | 1115416.8379
107 | 2699917.5289 | 1115372.9793
108 | 2699933.1595 | 1115376.1435
109 | 2699946.1371 | 1115314.9349
110 | 2699889.3443 | 1115304.2739
111 | 2699885.5983 | 1115325.8479
112 | 2699861.0739 | 1115298.9714
113 | 2700009.2435 | 1115270.0983
114 | 2699873.1683 | 1115234.2969
115 | 2699722.095 | 1115179.4085
116 | 2699827.7814 | 1115188.376
117 | 2699704.823 | 1115177.7566
118 | 2699996.95 | 1115264.201
119 | 2699850.8662 | 1115320.3074
120 | 2699815.9402 | 1115309.9912
121 | 2699814.4429 | 1115319.1251
122 | 2699833.4691 | 1115410.8172

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1