## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5397-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5397-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5397-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5397-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5397-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5397-4_0_4_node_60 | 0.4 | n |  | TRUE
6 | bus_LV_5397-4_0_4_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_5397-4_0_4_node_70 | 0.4 | n |  | TRUE
8 | bus_LV_5397-4_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_5397-4_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_5397-4_0_4_node_53 | 0.4 | n |  | TRUE
11 | bus_LV_5397-4_0_4_node_59 | 0.4 | n |  | TRUE
12 | bus_LV_5397-4_0_4_node_58 | 0.4 | n |  | TRUE
13 | bus_LV_5397-4_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_5397-4_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_5397-4_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5397-4_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_5397-4_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_5397-4_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_5397-4_0_4_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_5397-4_0_4_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_5397-4_0_4_node_72 | 0.4 | n |  | TRUE
22 | bus_LV_5397-4_0_4_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_5397-4_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_5397-4_0_4_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_5397-4_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_5397-4_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_5397-4_0_4_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_5397-4_0_4_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_5397-4_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_5397-4_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_5397-4_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_5397-4_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_5397-4_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_5397-4_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_5397-4_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_5397-4_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_5397-4_0_4_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_5397-4_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_5397-4_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_5397-4_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_5397-4_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_5397-4_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_5397-4_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_5397-4_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_5397-4_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_5397-4_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_5397-4_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_5397-4_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_5397-4_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_5397-4_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_5397-4_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_5397-4_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_5397-4_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_5397-4_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_5397-4_0_4_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_5397-4_0_4_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_5397-4_0_4_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_5397-4_0_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_5397-4_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_5397-4_0_4_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_5397-4_0_4_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_5397-4_0_4_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_5397-4_0_4_node_64 | 0.4 | n |  | TRUE
64 | bus_LV_5397-4_0_4_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_5397-4_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_5397-4_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_5397-4_0_4_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_5397-4_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_5397-4_0_4_node_69 | 0.4 | n |  | TRUE
70 | bus_MV_65_1_node_54 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5397-4_0_4_load_0 | 0 | 0.0017496 | 0.00043849 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5397-4_0_4_load_60 | 5 | 0.001361 | 0.00034109 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5397-4_0_4_load_71 | 6 | 0.0078495 | 0.0019673 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5397-4_0_4_load_70 | 7 | 0.0055933 | 0.0014018 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5397-4_0_4_load_5 | 8 | 0.0016468 | 0.00041274 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5397-4_0_4_load_59 | 11 | 0.0021127 | 0.00052949 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5397-4_0_4_load_6 | 14 | 0.0027052 | 0.00067799 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5397-4_0_4_load_7 | 16 | 0.0014352 | 0.0003597 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5397-4_0_4_load_9 | 17 | 0.0024998 | 0.0006265 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5397-4_0_4_load_10 | 18 | 0.0012111 | 0.00030352 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5397-4_0_4_load_72 | 21 | 0.007381 | 0.0018498 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5397-4_0_4_load_43 | 23 | 0.0011819 | 0.00029622 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5397-4_0_4_load_41 | 24 | 0.001361 | 0.00034111 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5397-4_0_4_load_11 | 25 | 0.0041236 | 0.0010335 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5397-4_0_4_load_55 | 27 | 0.0019582 | 0.00049076 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5397-4_0_4_load_54 | 28 | 0.0023611 | 0.00059176 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5397-4_0_4_load_16 | 29 | 0.022716 | 0.0056932 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5397-4_0_4_load_18 | 31 | 0.032215 | 0.0080737 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5397-4_0_4_load_22 | 32 | 0.07003 | 0.017551 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5397-4_0_4_load_28 | 34 | 0.00094872 | 0.00023777 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5397-4_0_4_load_25 | 35 | 0.0012168 | 0.00030497 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5397-4_0_4_load_23 | 36 | 0.011785 | 0.0029535 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5397-4_0_4_load_50 | 37 | 0.036095 | 0.0090463 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5397-4_0_4_load_24 | 39 | 0.00090473 | 0.00022675 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5397-4_0_4_load_26 | 40 | 0.0008237 | 0.00020644 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5397-4_0_4_load_27 | 41 | 0.0012573 | 0.00031512 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5397-4_0_4_load_29 | 42 | 0.0019951 | 0.00050002 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5397-4_0_4_load_30 | 43 | 0.0012741 | 0.00031931 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5397-4_0_4_load_33 | 44 | 0.0018952 | 0.00047498 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5397-4_0_4_load_34 | 45 | 0.00091043 | 0.00022818 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5397-4_0_4_load_38 | 46 | 0.00087345 | 0.00021891 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5397-4_0_4_load_40 | 47 | 0.0015802 | 0.00039604 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5397-4_0_4_load_39 | 48 | 0.0065316 | 0.001637 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5397-4_0_4_load_35 | 49 | 0.034957 | 0.0087611 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5397-4_0_4_load_36 | 50 | 0.024726 | 0.0061969 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5397-4_0_4_load_37 | 51 | 0.051425 | 0.012888 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5397-4_0_4_load_47 | 53 | 0.029369 | 0.0073605 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5397-4_0_4_load_44 | 55 | 0.00080929 | 0.00020283 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5397-4_0_4_load_45 | 56 | 0.001074 | 0.00026916 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5397-4_0_4_load_57 | 57 | 0.0018225 | 0.00045676 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5397-4_0_4_load_56 | 58 | 0.0029633 | 0.00074267 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5397-4_0_4_load_63 | 60 | 0.0011029 | 0.0002764 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5397-4_0_4_load_65 | 62 | 0.084299 | 0.021127 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5397-4_0_4_load_64 | 63 | 0.001063 | 0.00026642 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5397-4_0_4_load_61 | 64 | 0.0020644 | 0.00051739 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5397-4_0_4_load_62 | 66 | 0.013969 | 0.0035009 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5397-4_0_4_load_69 | 69 | 0.012099 | 0.0030323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5397-4_0_4_line_0 |  | 0 | 1 | 0.058578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5397-4_0_4_line_1 |  | 0 | 2 | 0.12112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5397-4_0_4_line_2 |  | 1 | 3 | 0.021107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5397-4_0_4_line_3 |  | 2 | 4 | 0.024527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5397-4_0_4_line_4 |  | 3 | 5 | 0.011008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5397-4_0_4_line_5 |  | 4 | 6 | 0.025808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5397-4_0_4_line_6 |  | 4 | 7 | 0.021685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5397-4_0_4_line_7 |  | 5 | 10 | 0.011502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5397-4_0_4_line_8 |  | 7 | 13 | 0.020123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5397-4_0_4_line_9 |  | 8 | 9 | 0.0057459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5397-4_0_4_line_10 |  | 9 | 13 | 0.020309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5397-4_0_4_line_11 |  | 10 | 63 | 0.0066205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5397-4_0_4_line_12 |  | 10 | 61 | 0.032188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5397-4_0_4_line_13 |  | 11 | 12 | 0.03993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5397-4_0_4_line_14 |  | 12 | 58 | 0.034903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5397-4_0_4_line_15 |  | 12 | 59 | 0.011242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5397-4_0_4_line_16 |  | 13 | 26 | 0.022313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5397-4_0_4_line_17 |  | 14 | 15 | 0.028523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5397-4_0_4_line_18 |  | 15 | 18 | 0.066936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5397-4_0_4_line_19 |  | 16 | 17 | 0.0070564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5397-4_0_4_line_20 |  | 17 | 19 | 0.011661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5397-4_0_4_line_21 |  | 18 | 20 | 0.0097268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5397-4_0_4_line_22 |  | 19 | 21 | 0.01024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5397-4_0_4_line_23 |  | 19 | 22 | 0.0194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5397-4_0_4_line_24 |  | 20 | 23 | 0.011342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5397-4_0_4_line_25 |  | 20 | 24 | 0.025283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5397-4_0_4_line_26 |  | 22 | 44 | 0.011527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5397-4_0_4_line_27 |  | 22 | 45 | 0.018391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_5397-4_0_4_line_28 |  | 22 | 43 | 0.012286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_5397-4_0_4_line_29 |  | 23 | 55 | 0.010681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_5397-4_0_4_line_30 |  | 24 | 47 | 0.01635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_5397-4_0_4_line_31 |  | 25 | 26 | 0.009751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5397-4_0_4_line_32 |  | 27 | 28 | 0.056907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5397-4_0_4_line_33 |  | 28 | 54 | 0.020995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5397-4_0_4_line_34 |  | 29 | 30 | 0.0095136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5397-4_0_4_line_35 |  | 30 | 31 | 0.012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5397-4_0_4_line_36 |  | 31 | 32 | 0.0025344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5397-4_0_4_line_37 |  | 32 | 36 | 0.0087413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5397-4_0_4_line_38 |  | 33 | 34 | 0.0082714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5397-4_0_4_line_39 |  | 33 | 35 | 0.0026364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5397-4_0_4_line_40 |  | 34 | 39 | 0.00091701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5397-4_0_4_line_41 |  | 35 | 40 | 0.016727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5397-4_0_4_line_42 |  | 36 | 39 | 0.0051983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5397-4_0_4_line_43 |  | 37 | 38 | 0.00948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5397-4_0_4_line_44 |  | 38 | 53 | 0.046993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5397-4_0_4_line_45 |  | 40 | 41 | 0.0031324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_5397-4_0_4_line_46 |  | 41 | 42 | 0.0014792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_5397-4_0_4_line_47 |  | 42 | 43 | 0.0053805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_5397-4_0_4_line_48 |  | 44 | 46 | 0.0042031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5397-4_0_4_line_49 |  | 45 | 47 | 0.01227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_5397-4_0_4_line_50 |  | 46 | 48 | 0.00088182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5397-4_0_4_line_51 |  | 49 | 50 | 0.0020276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5397-4_0_4_line_52 |  | 50 | 51 | 0.015389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5397-4_0_4_line_53 |  | 51 | 52 | 0.0058454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_5397-4_0_4_line_54 |  | 52 | 53 | 0.033837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5397-4_0_4_line_55 |  | 52 | 54 | 0.034098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_5397-4_0_4_line_56 |  | 54 | 58 | 0.0078362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_5397-4_0_4_line_57 |  | 54 | 57 | 0.039955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_5397-4_0_4_line_58 |  | 55 | 56 | 0.0027897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_5397-4_0_4_line_59 |  | 56 | 57 | 0.053354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_5397-4_0_4_line_60 |  | 59 | 60 | 0.0055422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5397-4_0_4_line_61 |  | 60 | 64 | 0.0040315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5397-4_0_4_line_62 |  | 61 | 62 | 0.0018346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5397-4_0_4_line_63 |  | 62 | 65 | 0.0053677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5397-4_0_4_line_64 |  | 63 | 66 | 0.0044686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5397-4_0_4_line_65 |  | 64 | 66 | 0.011114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5397-4_0_4_line_66 |  | 65 | 67 | 0.015933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5397-4_0_4_line_67 |  | 67 | 68 | 0.01856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5397-4_0_4_line_68 |  | 68 | 69 | 0.011229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5397-4_0_4_trafo_37 | 0.63 MVA 20/0.4 kV | 70 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2697501.1955 | 1114913.2553 | 2697498.9937 | 1114916.6553 | 2697484.9949 | 1114935.175 | 2697477.1193 | 1114944.6542 | 2697471.5518 | 1114948.9229 | 2697466.5951 | 1114951.7115 | 2697460.4798 | 1114953.1647
1 | 2697346.4493 | 1114919.8722 | 2697357.2129 | 1114920.023 | 2697373.9782 | 1114925.4067 | 2697399.9696 | 1114940.5781 | 2697426.287 | 1114949.3954 | 2697439.9428 | 1114953.6287 | 2697452.5784 | 1114954.0654 | 2697460.4161 | 1114953.1798 | 2697460.4798 | 1114953.1647
2 | 2697501.1955 | 1114913.2553 | 2697480.713 | 1114918.5847
3 | 2697346.4493 | 1114919.8722 | 2697338.8305 | 1114943.1865
4 | 2697480.713 | 1114918.5847 | 2697475.4831 | 1114908.8987
5 | 2697338.8305 | 1114943.1865 | 2697363.492 | 1114950.7918
6 | 2697338.8305 | 1114943.1865 | 2697335.4568 | 1114944.5443 | 2697332.0409 | 1114944.6895 | 2697328.4263 | 1114944.2201 | 2697317.9404 | 1114940.9497
7 | 2697470.0185 | 1114898.7783 | 2697475.4831 | 1114908.8987
8 | 2697298.6759 | 1114935.1591 | 2697301.2153 | 1114935.7335 | 2697317.9404 | 1114940.9497
9 | 2697304.8562 | 1114915.813 | 2697308.2517 | 1114915.9787 | 2697310.5859 | 1114916.2166
10 | 2697298.6759 | 1114935.1591 | 2697304.8562 | 1114915.813
11 | 2697470.0185 | 1114898.7783 | 2697463.4076 | 1114898.4231
12 | 2697470.0185 | 1114898.7783 | 2697465.8414 | 1114887.6709 | 2697465.1811 | 1114886.4706 | 2697481.0414 | 1114876.097
13 | 2697429.588 | 1114898.2946 | 2697426.5074 | 1114902.5589 | 2697424.9304 | 1114906.0134 | 2697423.481 | 1114910.6597 | 2697423.2442 | 1114914.814 | 2697424.0265 | 1114918.5178 | 2697425.6749 | 1114921.6684 | 2697428.5461 | 1114924.6609 | 2697431.9017 | 1114926.8273 | 2697436.0622 | 1114927.9282 | 2697438.1195 | 1114927.9662
14 | 2697429.588 | 1114898.2946 | 2697424.4745 | 1114895.9443 | 2697408.2529 | 1114890.8471 | 2697396.7503 | 1114886.5707
15 | 2697439.4525 | 1114892.8832 | 2697434.7126 | 1114895.1528 | 2697429.588 | 1114898.2946
16 | 2697276.5845 | 1114933.4479 | 2697283.1371 | 1114932.7526 | 2697288.9338 | 1114932.9569 | 2697298.6759 | 1114935.1591
17 | 2697223.1896 | 1114822.6115 | 2697242.202 | 1114819.3812 | 2697251.4344 | 1114819.0588
18 | 2697223.1896 | 1114822.6115 | 2697226.3174 | 1114832.2454 | 2697230.6331 | 1114836.673 | 2697241.9605 | 1114833.9419 | 2697252.6852 | 1114836.5266 | 2697262.9968 | 1114835.4915 | 2697280.0803 | 1114831.3573
19 | 2697320.0965 | 1114808.6915 | 2697324.2812 | 1114808.047 | 2697327.093 | 1114808.2901
20 | 2697338.718 | 1114808.8794 | 2697335.6571 | 1114809.0303 | 2697327.093 | 1114808.2901
21 | 2697289.4589 | 1114832.4587 | 2697283.1167 | 1114830.6224 | 2697280.0803 | 1114831.3573
22 | 2697338.718 | 1114808.8794 | 2697340.6109 | 1114802.1056 | 2697341.9302 | 1114799.1833
23 | 2697357.8032 | 1114812.6549 | 2697338.718 | 1114808.8794
24 | 2697289.4589 | 1114832.4587 | 2697289.4307 | 1114834.2149 | 2697290.3952 | 1114835.231 | 2697292.1826 | 1114835.5043 | 2697298.5514 | 1114835.1912
25 | 2697289.4589 | 1114832.4587 | 2697290.1691 | 1114831.0359 | 2697295.7547 | 1114828.524 | 2697312.455 | 1114823.0709
26 | 2697357.8032 | 1114812.6549 | 2697359.5623 | 1114815.6516 | 2697359.6947 | 1114821.3462 | 2697359.8809 | 1114823.6951
27 | 2697357.8032 | 1114812.6549 | 2697352.2948 | 1114815.646 | 2697342.0194 | 1114818.7496 | 2697340.6379 | 1114818.8946
28 | 2697357.8032 | 1114812.6549 | 2697362.0129 | 1114808.2976 | 2697368.1918 | 1114809.076
29 | 2697298.5514 | 1114835.1912 | 2697304.6268 | 1114834.8925 | 2697309.1891 | 1114835.0214 | 2697309.2232 | 1114835.026
30 | 2697328.428 | 1114820.1038 | 2697319.0233 | 1114820.9261 | 2697312.455 | 1114823.0709
31 | 2697276.5845 | 1114933.4479 | 2697268.2305 | 1114938.4771
32 | 2697368.889 | 1114879.3828 | 2697362.8224 | 1114878.0649 | 2697351.7374 | 1114874.8404 | 2697344.2473 | 1114872.3519 | 2697329.411 | 1114867.5551 | 2697319.779 | 1114866.1885 | 2697313.8612 | 1114865.6635
33 | 2697389.4053 | 1114883.8399 | 2697368.889 | 1114879.3828
34 | 2697430.0423 | 1114801.8644 | 2697439.4406 | 1114803.3406
35 | 2697430.0423 | 1114801.8644 | 2697417.5128 | 1114799.9573
36 | 2697415.0073 | 1114799.576 | 2697417.5128 | 1114799.9573
37 | 2697406.3516 | 1114798.3705 | 2697408.5624 | 1114798.595 | 2697415.0073 | 1114799.576
38 | 2697392.0384 | 1114796.9173 | 2697400.2675 | 1114797.7528
39 | 2697392.0384 | 1114796.9173 | 2697389.4997 | 1114797.6281
40 | 2697400.2675 | 1114797.7528 | 2697401.1798 | 1114797.8454
41 | 2697376.0012 | 1114805.728 | 2697379.5323 | 1114800.4186 | 2697389.4997 | 1114797.6281
42 | 2697401.1798 | 1114797.8454 | 2697406.3516 | 1114798.3705
43 | 2697473.8256 | 1114839.7696 | 2697473.084 | 1114833.5427 | 2697472.8033 | 1114830.3473
44 | 2697473.8256 | 1114839.7696 | 2697469.2843 | 1114840.7305 | 2697468.6398 | 1114845.7455 | 2697468.1249 | 1114857.1109 | 2697465.5164 | 1114866.1079 | 2697459.434 | 1114875.4936 | 2697455.2546 | 1114878.8599
45 | 2697374.2666 | 1114808.3363 | 2697376.0012 | 1114805.728
46 | 2697374.2666 | 1114808.3363 | 2697373.4474 | 1114809.568
47 | 2697373.4474 | 1114809.568 | 2697373.3431 | 1114809.7249 | 2697368.1918 | 1114809.076
48 | 2697359.8809 | 1114823.6951 | 2697359.8809 | 1114823.6951 | 2697362.5554 | 1114824.5163 | 2697363.9014 | 1114824.9205
49 | 2697328.428 | 1114820.1038 | 2697332.5579 | 1114819.7427 | 2697340.6379 | 1114818.8946
50 | 2697364.746 | 1114825.1741 | 2697363.9014 | 1114824.9205
51 | 2697402.9232 | 1114877.0438 | 2697404.9028 | 1114877.4822
52 | 2697419.8799 | 1114881.0168 | 2697419.8799 | 1114881.0168 | 2697409.3556 | 1114878.4683 | 2697404.9028 | 1114877.4822
53 | 2697423.2951 | 1114885.719 | 2697421.7092 | 1114883.003 | 2697419.8799 | 1114881.0168
54 | 2697423.2951 | 1114885.719 | 2697426.1405 | 1114885.9983 | 2697440.6847 | 1114885.8987 | 2697450.4749 | 1114882.7096 | 2697455.2546 | 1114878.8599
55 | 2697389.4053 | 1114883.8399 | 2697391.2726 | 1114882.9805 | 2697405.575 | 1114883.9999 | 2697423.2951 | 1114885.719
56 | 2697389.4053 | 1114883.8399 | 2697396.7503 | 1114886.5707
57 | 2697389.4053 | 1114883.8399 | 2697387.2386 | 1114880.7365 | 2697384.9218 | 1114878.8092 | 2697366.9829 | 1114874.3627 | 2697363.8391 | 1114872.4666 | 2697355.5219 | 1114865.2624
58 | 2697311.9882 | 1114835.3967 | 2697309.2232 | 1114835.026
59 | 2697355.5219 | 1114865.2624 | 2697340.5992 | 1114852.3365 | 2697330.2687 | 1114844.4546 | 2697323.8945 | 1114840.283 | 2697319.8328 | 1114837.8385 | 2697314.183 | 1114835.6909 | 2697311.9882 | 1114835.3967
60 | 2697439.4525 | 1114892.8832 | 2697443.3819 | 1114895.8704 | 2697443.9793 | 1114895.9734
61 | 2697447.9523 | 1114896.658 | 2697443.9793 | 1114895.9734
62 | 2697481.0414 | 1114876.097 | 2697482.7044 | 1114875.3223
63 | 2697487.5701 | 1114873.0557 | 2697482.7044 | 1114875.3223
64 | 2697458.9454 | 1114898.1835 | 2697463.4076 | 1114898.4231
65 | 2697447.9523 | 1114896.658 | 2697455.8357 | 1114898.0164 | 2697458.9454 | 1114898.1835
66 | 2697487.5701 | 1114873.0557 | 2697486.1495 | 1114857.1897
67 | 2697504.2195 | 1114861.6498 | 2697486.1495 | 1114857.1897
68 | 2697504.2195 | 1114861.6498 | 2697504.6802 | 1114858.4552 | 2697502.1146 | 1114850.8759

## bus_geodata
| x | y | coords
0 | 2697460.4798 | 1114953.1647
1 | 2697501.1955 | 1114913.2553
2 | 2697346.4493 | 1114919.8722
3 | 2697480.713 | 1114918.5847
4 | 2697338.8305 | 1114943.1865
5 | 2697475.4831 | 1114908.8987
6 | 2697363.492 | 1114950.7918
7 | 2697317.9404 | 1114940.9497
8 | 2697310.5859 | 1114916.2166
9 | 2697304.8562 | 1114915.813
10 | 2697470.0185 | 1114898.7783
11 | 2697438.1195 | 1114927.9662
12 | 2697429.588 | 1114898.2946
13 | 2697298.6759 | 1114935.1591
14 | 2697251.4344 | 1114819.0588
15 | 2697223.1896 | 1114822.6115
16 | 2697320.0965 | 1114808.6915
17 | 2697327.093 | 1114808.2901
18 | 2697280.0803 | 1114831.3573
19 | 2697338.718 | 1114808.8794
20 | 2697289.4589 | 1114832.4587
21 | 2697341.9302 | 1114799.1833
22 | 2697357.8032 | 1114812.6549
23 | 2697298.5514 | 1114835.1912
24 | 2697312.455 | 1114823.0709
25 | 2697268.2305 | 1114938.4771
26 | 2697276.5845 | 1114933.4479
27 | 2697313.8612 | 1114865.6635
28 | 2697368.889 | 1114879.3828
29 | 2697439.4406 | 1114803.3406
30 | 2697430.0423 | 1114801.8644
31 | 2697417.5128 | 1114799.9573
32 | 2697415.0073 | 1114799.576
33 | 2697392.0384 | 1114796.9173
34 | 2697400.2675 | 1114797.7528
35 | 2697389.4997 | 1114797.6281
36 | 2697406.3516 | 1114798.3705
37 | 2697472.8033 | 1114830.3473
38 | 2697473.8256 | 1114839.7696
39 | 2697401.1799 | 1114797.8454
40 | 2697376.0012 | 1114805.728
41 | 2697374.2666 | 1114808.3363
42 | 2697373.4474 | 1114809.568
43 | 2697368.1918 | 1114809.076
44 | 2697359.8809 | 1114823.6951
45 | 2697340.6379 | 1114818.8946
46 | 2697363.9014 | 1114824.9205
47 | 2697328.428 | 1114820.1038
48 | 2697364.746 | 1114825.1741
49 | 2697402.9232 | 1114877.0438
50 | 2697404.9028 | 1114877.4822
51 | 2697419.8799 | 1114881.0168
52 | 2697423.2951 | 1114885.719
53 | 2697455.2546 | 1114878.8599
54 | 2697389.4053 | 1114883.8399
55 | 2697309.2232 | 1114835.026
56 | 2697311.9882 | 1114835.3967
57 | 2697355.5219 | 1114865.2624
58 | 2697396.7503 | 1114886.5707
59 | 2697439.4525 | 1114892.8832
60 | 2697443.9793 | 1114895.9734
61 | 2697481.0414 | 1114876.097
62 | 2697482.7044 | 1114875.3223
63 | 2697463.4076 | 1114898.4231
64 | 2697447.9523 | 1114896.658
65 | 2697487.5701 | 1114873.0557
66 | 2697458.9454 | 1114898.1835
67 | 2697486.1495 | 1114857.1897
68 | 2697504.2195 | 1114861.6498
69 | 2697502.1146 | 1114850.8759
70 | 2697423.2951 | 1114885.719

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1