## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6008-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6008-10_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6008-10_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6008-10_0_3_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_6008-10_0_3_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_6008-10_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_6008-10_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_6008-10_0_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_6008-10_0_3_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_6008-10_0_3_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_6008-10_0_3_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_6008-10_0_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_6008-10_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_6008-10_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_6008-10_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_6008-10_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_6008-10_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_6008-10_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_6008-10_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6008-10_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_6008-10_0_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_6008-10_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_6008-10_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_6008-10_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6008-10_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_6008-10_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_6008-10_0_3_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_6008-10_0_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_6008-10_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_6008-10_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_6008-10_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_6008-10_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_6008-10_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_6008-10_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_6008-10_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_6008-10_0_3_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_6008-10_0_3_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_6008-10_0_3_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_6008-10_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6008-10_0_3_node_56 | 0.4 | n |  | TRUE
40 | bus_LV_6008-10_0_3_node_57 | 0.4 | n |  | TRUE
41 | bus_LV_6008-10_0_3_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_6008-10_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_6008-10_0_3_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_6008-10_0_3_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_6008-10_0_3_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_6008-10_0_3_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_6008-10_0_3_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_6008-10_0_3_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_6008-10_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_6008-10_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_6008-10_0_3_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_6008-10_0_3_node_51 | 0.4 | n |  | TRUE
53 | bus_LV_6008-10_0_3_node_58 | 0.4 | n |  | TRUE
54 | bus_LV_6008-10_0_3_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_6008-10_0_3_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_6008-10_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_6008-10_0_3_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_6008-10_0_3_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_6008-10_0_3_node_60 | 0.4 | n |  | TRUE
60 | bus_LV_6008-10_0_3_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_6008-10_0_3_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_6008-10_0_3_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_6008-10_0_3_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_6008-10_0_3_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_6008-10_0_3_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_6008-10_0_3_node_65 | 0.4 | n |  | TRUE
67 | bus_MV_86_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6008-10_0_3_load_0 | 0 | 0.0015074 | 0.00037779 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6008-10_0_3_load_5 | 3 | 0.0040778 | 0.001022 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6008-10_0_3_load_3 | 5 | 0.0044971 | 0.0011271 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6008-10_0_3_load_38 | 7 | 0.013018 | 0.0032627 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6008-10_0_3_load_39 | 8 | 0.0041002 | 0.0010276 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6008-10_0_3_load_37 | 9 | 0.00502 | 0.0012581 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6008-10_0_3_load_40 | 10 | 0.004065 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6008-10_0_3_load_36 | 11 | 0.0027515 | 0.00068959 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6008-10_0_3_load_13 | 12 | 0.0098938 | 0.0024796 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6008-10_0_3_load_11 | 13 | 0.003885 | 0.00097366 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6008-10_0_3_load_6 | 14 | 0.0054806 | 0.0013736 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6008-10_0_3_load_9 | 16 | 0.0077539 | 0.0019433 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6008-10_0_3_load_10 | 17 | 0.0059356 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6008-10_0_3_load_14 | 18 | 0.0045652 | 0.0011441 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6008-10_0_3_load_20 | 20 | 0.0047582 | 0.0011925 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6008-10_0_3_load_18 | 21 | 0.0057767 | 0.0014478 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6008-10_0_3_load_15 | 22 | 0.0060397 | 0.0015137 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6008-10_0_3_load_16 | 23 | 0.0033372 | 0.00083638 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6008-10_0_3_load_17 | 24 | 0.0036199 | 0.00090724 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6008-10_0_3_load_21 | 25 | 0.0035547 | 0.0008909 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6008-10_0_3_load_29 | 26 | 0.0044309 | 0.0011105 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6008-10_0_3_load_30 | 27 | 0.004215 | 0.0010564 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6008-10_0_3_load_22 | 28 | 0.0049182 | 0.0012326 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6008-10_0_3_load_23 | 29 | 0.0075577 | 0.0018941 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6008-10_0_3_load_24 | 30 | 0.0085435 | 0.0021412 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6008-10_0_3_load_25 | 31 | 0.0024167 | 0.00060568 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6008-10_0_3_load_26 | 32 | 0.0052252 | 0.0013096 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6008-10_0_3_load_27 | 33 | 0.0036341 | 0.00091079 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6008-10_0_3_load_28 | 34 | 0.0069139 | 0.0017328 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6008-10_0_3_load_47 | 37 | 0.0022451 | 0.00056267 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6008-10_0_3_load_56 | 39 | 0.010932 | 0.0027397 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6008-10_0_3_load_57 | 40 | 0.003955 | 0.00099122 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6008-10_0_3_load_31 | 41 | 0.0057381 | 0.0014381 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6008-10_0_3_load_45 | 42 | 0.0051608 | 0.0012934 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6008-10_0_3_load_44 | 43 | 0.0023004 | 0.00057654 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6008-10_0_3_load_33 | 44 | 0.0074431 | 0.0018654 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6008-10_0_3_load_34 | 45 | 0.0035879 | 0.00089922 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6008-10_0_3_load_35 | 46 | 0.0034619 | 0.00086762 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6008-10_0_3_load_41 | 47 | 0.006609 | 0.0016564 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6008-10_0_3_load_42 | 48 | 0.0030113 | 0.00075469 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6008-10_0_3_load_43 | 49 | 0.0043056 | 0.0010791 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6008-10_0_3_load_48 | 50 | 0.0021519 | 0.00053933 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6008-10_0_3_load_50 | 51 | 0.0024008 | 0.00060171 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6008-10_0_3_load_51 | 52 | 0.0065842 | 0.0016501 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6008-10_0_3_load_58 | 53 | 0.015085 | 0.0037807 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6008-10_0_3_load_59 | 54 | 0.0022527 | 0.00056457 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6008-10_0_3_load_52 | 55 | 0.0024716 | 0.00061945 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6008-10_0_3_load_53 | 56 | 0.0094938 | 0.0023794 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6008-10_0_3_load_54 | 57 | 0.0048632 | 0.0012188 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6008-10_0_3_load_55 | 58 | 0.0055149 | 0.0013822 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6008-10_0_3_load_60 | 59 | 0.0051459 | 0.0012897 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6008-10_0_3_load_61 | 60 | 0.004566 | 0.0011444 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6008-10_0_3_load_66 | 61 | 0.0014966 | 0.00037509 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6008-10_0_3_load_62 | 62 | 0.0063921 | 0.001602 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6008-10_0_3_load_67 | 63 | 0.0031042 | 0.00077798 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6008-10_0_3_load_63 | 64 | 0.0052566 | 0.0013174 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6008-10_0_3_load_64 | 65 | 0.0057359 | 0.0014375 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6008-10_0_3_load_65 | 66 | 0.0043542 | 0.0010913 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6008-10_0_3_line_0 |  | 0 | 1 | 0.10316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6008-10_0_3_line_1 |  | 1 | 2 | 0.077698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6008-10_0_3_line_2 |  | 2 | 3 | 0.10836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6008-10_0_3_line_3 |  | 3 | 4 | 0.058033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6008-10_0_3_line_4 |  | 4 | 12 | 0.017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6008-10_0_3_line_5 |  | 4 | 13 | 0.0050039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6008-10_0_3_line_6 |  | 5 | 6 | 0.051606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6008-10_0_3_line_7 |  | 6 | 7 | 0.032119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6008-10_0_3_line_8 |  | 6 | 8 | 0.0058958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6008-10_0_3_line_9 |  | 6 | 9 | 0.030258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6008-10_0_3_line_10 |  | 8 | 10 | 0.016393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6008-10_0_3_line_11 |  | 9 | 11 | 0.0018265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6008-10_0_3_line_12 |  | 10 | 47 | 0.0016873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6008-10_0_3_line_13 |  | 11 | 46 | 0.011038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6008-10_0_3_line_14 |  | 12 | 18 | 0.0047566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6008-10_0_3_line_15 |  | 13 | 17 | 0.0026201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6008-10_0_3_line_16 |  | 14 | 15 | 0.017135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6008-10_0_3_line_17 |  | 15 | 16 | 0.0074144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6008-10_0_3_line_18 |  | 15 | 17 | 0.022855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6008-10_0_3_line_19 |  | 18 | 19 | 0.015996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6008-10_0_3_line_20 |  | 19 | 20 | 0.0080598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6008-10_0_3_line_21 |  | 19 | 21 | 0.024861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6008-10_0_3_line_22 |  | 20 | 25 | 0.0070756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6008-10_0_3_line_23 |  | 21 | 23 | 0.027618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6008-10_0_3_line_24 |  | 22 | 23 | 0.0028529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6008-10_0_3_line_25 |  | 22 | 24 | 0.0021401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6008-10_0_3_line_26 |  | 25 | 26 | 0.0093237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6008-10_0_3_line_27 |  | 26 | 27 | 0.012862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6008-10_0_3_line_28 |  | 27 | 41 | 0.0086925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6008-10_0_3_line_29 |  | 28 | 29 | 0.0019376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6008-10_0_3_line_30 |  | 28 | 30 | 0.010212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6008-10_0_3_line_31 |  | 29 | 31 | 0.0081423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6008-10_0_3_line_32 |  | 30 | 32 | 0.0060353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6008-10_0_3_line_33 |  | 31 | 33 | 0.0032245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6008-10_0_3_line_34 |  | 32 | 34 | 0.016808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6008-10_0_3_line_35 |  | 33 | 35 | 0.018737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6008-10_0_3_line_36 |  | 34 | 36 | 0.02485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6008-10_0_3_line_37 |  | 35 | 37 | 0.0084343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_6008-10_0_3_line_38 |  | 35 | 38 | 0.011534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_6008-10_0_3_line_39 |  | 36 | 39 | 0.024352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6008-10_0_3_line_40 |  | 36 | 40 | 0.034598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6008-10_0_3_line_41 |  | 37 | 50 | 0.0060262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_6008-10_0_3_line_42 |  | 38 | 42 | 0.021667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6008-10_0_3_line_43 |  | 38 | 41 | 0.0036672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6008-10_0_3_line_44 |  | 39 | 53 | 0.0066399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6008-10_0_3_line_45 |  | 40 | 54 | 0.0031743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6008-10_0_3_line_46 |  | 42 | 43 | 0.0040903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6008-10_0_3_line_47 |  | 43 | 49 | 0.0070644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6008-10_0_3_line_48 |  | 44 | 45 | 0.00075305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6008-10_0_3_line_49 |  | 44 | 46 | 0.019525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6008-10_0_3_line_50 |  | 47 | 48 | 0.0087065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6008-10_0_3_line_51 |  | 48 | 49 | 0.013309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6008-10_0_3_line_52 |  | 50 | 51 | 0.0038013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6008-10_0_3_line_53 |  | 51 | 52 | 0.0085813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6008-10_0_3_line_54 |  | 52 | 55 | 0.015991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6008-10_0_3_line_55 |  | 53 | 61 | 0.15307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6008-10_0_3_line_56 |  | 54 | 62 | 0.014103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6008-10_0_3_line_57 |  | 55 | 56 | 0.023079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6008-10_0_3_line_58 |  | 56 | 57 | 0.0069517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6008-10_0_3_line_59 |  | 57 | 58 | 0.031818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6008-10_0_3_line_60 |  | 58 | 59 | 0.014086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6008-10_0_3_line_61 |  | 59 | 60 | 0.0044695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6008-10_0_3_line_62 |  | 60 | 65 | 0.0072712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6008-10_0_3_line_63 |  | 61 | 63 | 0.051703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6008-10_0_3_line_64 |  | 62 | 64 | 0.023106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6008-10_0_3_line_65 |  | 65 | 66 | 0.008768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6008-10_0_3_trafo_48 | 0.63 MVA 20/0.4 kV | 67 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2643803.6083 | 1128519.8884 | 2643771.5752 | 1128587.9248 | 2643755.1025 | 1128610.5217
1 | 2643881.0631 | 1128512.8569 | 2643858.7136 | 1128517.0637 | 2643825.907 | 1128518.4379 | 2643803.6083 | 1128519.8884
2 | 2643881.0631 | 1128512.8569 | 2643925.0922 | 1128565.9479 | 2643936.0376 | 1128576.8552 | 2643952.9915 | 1128593.7566
3 | 2643994.0909 | 1128634.7288 | 2643952.9915 | 1128593.7566
4 | 2643994.0909 | 1128634.7288 | 2643984.6935 | 1128649.5992
5 | 2643994.0909 | 1128634.7288 | 2643997.5323 | 1128631.0963
6 | 2643929.9329 | 1128766.119 | 2643919.2593 | 1128777.2362 | 2643912.2775 | 1128781.7767 | 2643888.9239 | 1128796.98
7 | 2643929.9329 | 1128766.119 | 2643937.2575 | 1128781.2022 | 2643936.3899 | 1128787.1656 | 2643929.939 | 1128793.9222
8 | 2643929.9329 | 1128766.119 | 2643935.1355 | 1128763.3455
9 | 2643929.9329 | 1128766.119 | 2643924.5589 | 1128765.6576 | 2643918.3202 | 1128741.589
10 | 2643935.1355 | 1128763.3455 | 2643940.3426 | 1128760.5695 | 2643948.712 | 1128754.242
11 | 2643918.3202 | 1128741.589 | 2643917.8618 | 1128739.8209
12 | 2643948.712 | 1128754.242 | 2643950.0579 | 1128753.2244
13 | 2643912.6967 | 1128730.1944 | 2643917.1249 | 1128736.9778 | 2643917.8618 | 1128739.8209
14 | 2643982.1524 | 1128653.6202 | 2643984.6935 | 1128649.5992
15 | 2643999.3343 | 1128629.1942 | 2643997.5323 | 1128631.0963
16 | 2644015.0527 | 1128612.6032 | 2644016.6274 | 1128609.0128 | 2644017.3792 | 1128605.2052 | 2644016.6797 | 1128595.8984
17 | 2644015.0527 | 1128612.6032 | 2644021.9598 | 1128609.9076
18 | 2644015.0527 | 1128612.6032 | 2643999.3343 | 1128629.1942
19 | 2643975.7277 | 1128668.2014 | 2643979.9297 | 1128657.1374 | 2643982.1524 | 1128653.6202
20 | 2643975.7277 | 1128668.2014 | 2643975.0129 | 1128676.2294
21 | 2643975.7277 | 1128668.2014 | 2643963.3734 | 1128657.1949 | 2643956.7983 | 1128652.1045
22 | 2643975.0129 | 1128676.2294 | 2643974.3854 | 1128683.2772 | 2643974.3854 | 1128683.2772
23 | 2643956.7983 | 1128652.1045 | 2643952.8933 | 1128649.0813 | 2643941.1324 | 1128646.5279 | 2643930.5921 | 1128645.0439
24 | 2643927.767 | 1128644.6461 | 2643930.5921 | 1128645.0439
25 | 2643925.6478 | 1128644.3477 | 2643927.767 | 1128644.6461
26 | 2643974.3854 | 1128683.2772 | 2643976.3456 | 1128692.3925
27 | 2643976.3456 | 1128692.3925 | 2643976.3751 | 1128692.5297 | 2643980.9729 | 1128704.3914
28 | 2643980.9729 | 1128704.3914 | 2643980.9729 | 1128704.3914 | 2643985.9709 | 1128711.5034
29 | 2644029.1189 | 1128725.1987 | 2644027.208 | 1128724.8777
30 | 2644029.1189 | 1128725.1987 | 2644032.5646 | 1128725.7775 | 2644038.2159 | 1128729.4094 | 2644038.2159 | 1128729.4094
31 | 2644027.208 | 1128724.8777 | 2644024.9547 | 1128724.4992 | 2644019.1115 | 1128724.0913
32 | 2644038.2159 | 1128729.4094 | 2644040.9815 | 1128734.7737
33 | 2644015.8948 | 1128723.8667 | 2644019.1115 | 1128724.0913
34 | 2644040.9815 | 1128734.7737 | 2644048.6839 | 1128749.7135
35 | 2643997.3751 | 1128721.2637 | 2644007.7144 | 1128723.2955 | 2644015.8948 | 1128723.8667
36 | 2644060.0713 | 1128771.8013 | 2644048.6839 | 1128749.7135
37 | 2643997.3751 | 1128721.2637 | 2643995.4049 | 1128729.4647
38 | 2643988.0794 | 1128714.5038 | 2643991.9442 | 1128718.0448 | 2643997.3751 | 1128721.2637
39 | 2644060.0713 | 1128771.8013 | 2644082.5432 | 1128762.4175
40 | 2644060.0713 | 1128771.8013 | 2644068.1528 | 1128805.4423
41 | 2643995.4049 | 1128729.4647 | 2643996.692 | 1128733.6317 | 2643997.7267 | 1128734.9361
42 | 2643988.0794 | 1128714.5038 | 2643975.4312 | 1128732.0954
43 | 2643988.0794 | 1128714.5038 | 2643985.9709 | 1128711.5034
44 | 2644088.6703 | 1128759.859 | 2644082.5432 | 1128762.4175
45 | 2644068.1528 | 1128805.4423 | 2644068.8943 | 1128808.5288
46 | 2643975.4312 | 1128732.0954 | 2643973.0434 | 1128735.4164
47 | 2643967.539 | 1128739.8444 | 2643973.0434 | 1128735.4164 | 2643973.0434 | 1128735.4164
48 | 2643901.6118 | 1128713.2138 | 2643902.0235 | 1128713.8443
49 | 2643902.0235 | 1128713.8443 | 2643912.6967 | 1128730.1944
50 | 2643957.003 | 1128747.9738 | 2643950.0579 | 1128753.2244
51 | 2643957.003 | 1128747.9738 | 2643964.1551 | 1128742.5666 | 2643967.539 | 1128739.8444
52 | 2643997.7267 | 1128734.9361 | 2644000.0891 | 1128737.9142
53 | 2644000.0891 | 1128737.9142 | 2644000.0891 | 1128737.9142 | 2644001.152 | 1128741.1236 | 2644000.9409 | 1128746.3198
54 | 2643999.455 | 1128762.229 | 2644000.7015 | 1128752.2149 | 2644000.9409 | 1128746.3198
55 | 2644088.6703 | 1128759.859 | 2644241.7343 | 1128758.5457
56 | 2644068.8943 | 1128808.5288 | 2644068.8943 | 1128808.5288 | 2644069.1627 | 1128816.1013 | 2644069.3965 | 1128822.6227
57 | 2643999.455 | 1128762.229 | 2643996.6044 | 1128785.1311
58 | 2643996.6044 | 1128785.1311 | 2643996.3896 | 1128786.8568 | 2643996.4615 | 1128792.069
59 | 2643996.4615 | 1128792.069 | 2643996.9007 | 1128823.8845
60 | 2643994.3927 | 1128837.7173 | 2643996.9194 | 1128825.2359 | 2643996.9007 | 1128823.8845
61 | 2643993.5059 | 1128842.0979 | 2643994.3927 | 1128837.7173
62 | 2643992.0632 | 1128849.2246 | 2643993.5059 | 1128842.0979
63 | 2644267.6844 | 1128715.7541 | 2644245.9352 | 1128740.1076 | 2644241.6197 | 1128755.0393 | 2644241.7343 | 1128758.5457
64 | 2644069.3965 | 1128822.6227 | 2644070.2245 | 1128845.7141
65 | 2643992.0632 | 1128849.2246 | 2643991.2858 | 1128853.0648 | 2643990.3783 | 1128857.829

## bus_geodata
| x | y | coords
0 | 2643755.1025 | 1128610.5217
1 | 2643803.6083 | 1128519.8884
2 | 2643881.0631 | 1128512.8569
3 | 2643952.9915 | 1128593.7566
4 | 2643994.0909 | 1128634.7288
5 | 2643888.9239 | 1128796.98
6 | 2643929.9329 | 1128766.119
7 | 2643929.939 | 1128793.9222
8 | 2643935.1355 | 1128763.3455
9 | 2643918.3201 | 1128741.589
10 | 2643948.712 | 1128754.242
11 | 2643917.8618 | 1128739.8209
12 | 2643984.6935 | 1128649.5992
13 | 2643997.5323 | 1128631.0963
14 | 2644016.6797 | 1128595.8984
15 | 2644015.0527 | 1128612.6032
16 | 2644021.9598 | 1128609.9076
17 | 2643999.3343 | 1128629.1942
18 | 2643982.1524 | 1128653.6202
19 | 2643975.7277 | 1128668.2014
20 | 2643975.0129 | 1128676.2294
21 | 2643956.7983 | 1128652.1045
22 | 2643927.767 | 1128644.6461
23 | 2643930.5921 | 1128645.0439
24 | 2643925.6478 | 1128644.3477
25 | 2643974.3854 | 1128683.2772
26 | 2643976.3456 | 1128692.3925
27 | 2643980.9729 | 1128704.3914
28 | 2644029.1189 | 1128725.1987
29 | 2644027.208 | 1128724.8777
30 | 2644038.2159 | 1128729.4094
31 | 2644019.1115 | 1128724.0913
32 | 2644040.9815 | 1128734.7737
33 | 2644015.8948 | 1128723.8667
34 | 2644048.6839 | 1128749.7135
35 | 2643997.3751 | 1128721.2637
36 | 2644060.0713 | 1128771.8013
37 | 2643995.4049 | 1128729.4647
38 | 2643988.0794 | 1128714.5038
39 | 2644082.5432 | 1128762.4175
40 | 2644068.1528 | 1128805.4423
41 | 2643985.9709 | 1128711.5034
42 | 2643975.4312 | 1128732.0954
43 | 2643973.0434 | 1128735.4164
44 | 2643902.0235 | 1128713.8443
45 | 2643901.6118 | 1128713.2138
46 | 2643912.6967 | 1128730.1944
47 | 2643950.0579 | 1128753.2244
48 | 2643957.003 | 1128747.9738
49 | 2643967.539 | 1128739.8444
50 | 2643997.7267 | 1128734.9361
51 | 2644000.0891 | 1128737.9142
52 | 2644000.9409 | 1128746.3198
53 | 2644088.6703 | 1128759.859
54 | 2644068.8943 | 1128808.5288
55 | 2643999.455 | 1128762.229
56 | 2643996.6044 | 1128785.1311
57 | 2643996.4615 | 1128792.069
58 | 2643996.9007 | 1128823.8845
59 | 2643994.3927 | 1128837.7173
60 | 2643993.5059 | 1128842.0979
61 | 2644241.7343 | 1128758.5457
62 | 2644069.3965 | 1128822.6227
63 | 2644267.6844 | 1128715.7541
64 | 2644070.2245 | 1128845.7141
65 | 2643992.0632 | 1128849.2246
66 | 2643990.3783 | 1128857.829
67 | 2643997.3751 | 1128721.2637

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1