## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6008-3_1_4_node_62 | 0.4 | n |  | TRUE
1 | bus_LV_6008-3_1_4_node_70 | 0.4 | n |  | TRUE
2 | bus_LV_6008-3_1_4_node_69 | 0.4 | n |  | TRUE
3 | bus_LV_6008-3_1_4_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_6008-3_1_4_node_19 | 0.4 | n |  | TRUE
5 | bus_LV_6008-3_1_4_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_6008-3_1_4_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_6008-3_1_4_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_6008-3_1_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_6008-3_1_4_node_113 | 0.4 | n |  | TRUE
10 | bus_LV_6008-3_1_4_node_127 | 0.4 | n |  | TRUE
11 | bus_LV_6008-3_1_4_node_92 | 0.4 | n |  | TRUE
12 | bus_LV_6008-3_1_4_node_134 | 0.4 | n |  | TRUE
13 | bus_LV_6008-3_1_4_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_6008-3_1_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_6008-3_1_4_node_130 | 0.4 | n |  | TRUE
16 | bus_LV_6008-3_1_4_node_139 | 0.4 | n |  | TRUE
17 | bus_LV_6008-3_1_4_node_131 | 0.4 | n |  | TRUE
18 | bus_LV_6008-3_1_4_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_6008-3_1_4_node_136 | 0.4 | n |  | TRUE
20 | bus_LV_6008-3_1_4_node_135 | 0.4 | n |  | TRUE
21 | bus_LV_6008-3_1_4_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_6008-3_1_4_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_6008-3_1_4_node_67 | 0.4 | n |  | TRUE
24 | bus_LV_6008-3_1_4_node_68 | 0.4 | n |  | TRUE
25 | bus_LV_6008-3_1_4_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_6008-3_1_4_node_73 | 0.4 | n |  | TRUE
27 | bus_LV_6008-3_1_4_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_6008-3_1_4_node_64 | 0.4 | n |  | TRUE
29 | bus_LV_6008-3_1_4_node_65 | 0.4 | n |  | TRUE
30 | bus_LV_6008-3_1_4_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_6008-3_1_4_node_74 | 0.4 | n |  | TRUE
32 | bus_LV_6008-3_1_4_node_115 | 0.4 | n |  | TRUE
33 | bus_LV_6008-3_1_4_node_112 | 0.4 | n |  | TRUE
34 | bus_LV_6008-3_1_4_node_122 | 0.4 | n |  | TRUE
35 | bus_LV_6008-3_1_4_node_77 | 0.4 | n |  | TRUE
36 | bus_LV_6008-3_1_4_node_121 | 0.4 | n |  | TRUE
37 | bus_LV_6008-3_1_4_node_79 | 0.4 | n |  | TRUE
38 | bus_LV_6008-3_1_4_node_80 | 0.4 | n |  | TRUE
39 | bus_LV_6008-3_1_4_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_6008-3_1_4_node_82 | 0.4 | n |  | TRUE
41 | bus_LV_6008-3_1_4_node_123 | 0.4 | n |  | TRUE
42 | bus_LV_6008-3_1_4_node_100 | 0.4 | n |  | TRUE
43 | bus_LV_6008-3_1_4_node_114 | 0.4 | n |  | TRUE
44 | bus_LV_6008-3_1_4_node_120 | 0.4 | n |  | TRUE
45 | bus_LV_6008-3_1_4_node_75 | 0.4 | n |  | TRUE
46 | bus_LV_6008-3_1_4_node_76 | 0.4 | n |  | TRUE
47 | bus_LV_6008-3_1_4_node_99 | 0.4 | n |  | TRUE
48 | bus_LV_6008-3_1_4_node_83 | 0.4 | n |  | TRUE
49 | bus_LV_6008-3_1_4_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_6008-3_1_4_node_85 | 0.4 | n |  | TRUE
51 | bus_LV_6008-3_1_4_node_86 | 0.4 | n |  | TRUE
52 | bus_LV_6008-3_1_4_node_87 | 0.4 | n |  | TRUE
53 | bus_LV_6008-3_1_4_node_110 | 0.4 | n |  | TRUE
54 | bus_LV_6008-3_1_4_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_6008-3_1_4_node_108 | 0.4 | n |  | TRUE
56 | bus_LV_6008-3_1_4_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_6008-3_1_4_node_89 | 0.4 | n |  | TRUE
58 | bus_LV_6008-3_1_4_node_90 | 0.4 | n |  | TRUE
59 | bus_LV_6008-3_1_4_node_91 | 0.4 | n |  | TRUE
60 | bus_LV_6008-3_1_4_node_93 | 0.4 | n |  | TRUE
61 | bus_LV_6008-3_1_4_node_96 | 0.4 | n |  | TRUE
62 | bus_LV_6008-3_1_4_node_94 | 0.4 | n |  | TRUE
63 | bus_LV_6008-3_1_4_node_97 | 0.4 | n |  | TRUE
64 | bus_LV_6008-3_1_4_node_95 | 0.4 | n |  | TRUE
65 | bus_LV_6008-3_1_4_node_101 | 0.4 | n |  | TRUE
66 | bus_LV_6008-3_1_4_node_119 | 0.4 | n |  | TRUE
67 | bus_LV_6008-3_1_4_node_98 | 0.4 | n |  | TRUE
68 | bus_LV_6008-3_1_4_node_102 | 0.4 | n |  | TRUE
69 | bus_LV_6008-3_1_4_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_6008-3_1_4_node_104 | 0.4 | n |  | TRUE
71 | bus_LV_6008-3_1_4_node_105 | 0.4 | n |  | TRUE
72 | bus_LV_6008-3_1_4_node_106 | 0.4 | n |  | TRUE
73 | bus_LV_6008-3_1_4_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_6008-3_1_4_node_109 | 0.4 | n |  | TRUE
75 | bus_LV_6008-3_1_4_node_117 | 0.4 | n |  | TRUE
76 | bus_LV_6008-3_1_4_node_118 | 0.4 | n |  | TRUE
77 | bus_LV_6008-3_1_4_node_116 | 0.4 | n |  | TRUE
78 | bus_LV_6008-3_1_4_node_128 | 0.4 | n |  | TRUE
79 | bus_LV_6008-3_1_4_node_126 | 0.4 | n |  | TRUE
80 | bus_LV_6008-3_1_4_node_138 | 0.4 | n |  | TRUE
81 | bus_LV_6008-3_1_4_node_129 | 0.4 | n |  | TRUE
82 | bus_LV_6008-3_1_4_node_124 | 0.4 | n |  | TRUE
83 | bus_LV_6008-3_1_4_node_125 | 0.4 | n |  | TRUE
84 | bus_MV_86_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6008-3_1_4_load_70 | 1 | 0.010959 | 0.0027466 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6008-3_1_4_load_69 | 2 | 0.0019361 | 0.00048523 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6008-3_1_4_load_19 | 4 | 0.00093699 | 0.00023483 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6008-3_1_4_load_127 | 10 | 0.00088808 | 0.00022258 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6008-3_1_4_load_134 | 12 | 0.0010124 | 0.00025372 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6008-3_1_4_load_130 | 15 | 0.0024034 | 0.00060234 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6008-3_1_4_load_139 | 16 | 0.0013608 | 0.00034105 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6008-3_1_4_load_135 | 20 | 0.0006739 | 0.00016889 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6008-3_1_4_load_60 | 21 | 0.0081334 | 0.0020384 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6008-3_1_4_load_68 | 24 | 0.0079379 | 0.0019894 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6008-3_1_4_load_66 | 25 | 0.0015373 | 0.00038528 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6008-3_1_4_load_73 | 26 | 0.015114 | 0.0037879 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6008-3_1_4_load_63 | 27 | 0.0020861 | 0.00052282 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6008-3_1_4_load_64 | 28 | 0.0015493 | 0.00038829 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6008-3_1_4_load_65 | 29 | 0.0022163 | 0.00055546 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6008-3_1_4_load_78 | 30 | 0.010649 | 0.002669 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6008-3_1_4_load_115 | 32 | 0.01003 | 0.0025139 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6008-3_1_4_load_77 | 35 | 0.0056999 | 0.0014285 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6008-3_1_4_load_121 | 36 | 0.0084189 | 0.00211 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6008-3_1_4_load_80 | 38 | 0.0069665 | 0.001746 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6008-3_1_4_load_81 | 39 | 0.0068979 | 0.0017288 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6008-3_1_4_load_82 | 40 | 0.0050944 | 0.0012768 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6008-3_1_4_load_123 | 41 | 0.0068246 | 0.0017104 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6008-3_1_4_load_100 | 42 | 0.0045285 | 0.001135 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6008-3_1_4_load_114 | 43 | 0.0070033 | 0.0017552 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6008-3_1_4_load_120 | 44 | 0.0086574 | 0.0021697 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6008-3_1_4_load_75 | 45 | 0.011053 | 0.0027702 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6008-3_1_4_load_76 | 46 | 0.010659 | 0.0026715 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6008-3_1_4_load_99 | 47 | 0.0048299 | 0.0012105 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6008-3_1_4_load_83 | 48 | 0.0073243 | 0.0018356 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6008-3_1_4_load_84 | 49 | 0.010181 | 0.0025517 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6008-3_1_4_load_85 | 50 | 0.0069665 | 0.001746 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6008-3_1_4_load_86 | 51 | 0.0044846 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6008-3_1_4_load_110 | 53 | 0.0044591 | 0.0011176 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6008-3_1_4_load_88 | 54 | 0.0085621 | 0.0021459 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6008-3_1_4_load_108 | 55 | 0.0032492 | 0.00081433 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6008-3_1_4_load_111 | 56 | 0.0019223 | 0.00048177 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6008-3_1_4_load_90 | 58 | 0.041012 | 0.010279 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6008-3_1_4_load_91 | 59 | 0.011022 | 0.0027624 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6008-3_1_4_load_93 | 60 | 0.027474 | 0.0068855 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6008-3_1_4_load_96 | 61 | 0.0086803 | 0.0021755 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6008-3_1_4_load_94 | 62 | 0.0062336 | 0.0015623 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6008-3_1_4_load_97 | 63 | 0.014107 | 0.0035355 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6008-3_1_4_load_95 | 64 | 0.006512 | 0.0016321 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6008-3_1_4_load_101 | 65 | 0.0018044 | 0.00045222 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6008-3_1_4_load_119 | 66 | 0.0034273 | 0.00085896 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6008-3_1_4_load_98 | 67 | 0.0059468 | 0.0014904 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6008-3_1_4_load_102 | 68 | 0.0043507 | 0.0010904 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6008-3_1_4_load_103 | 69 | 0.0035825 | 0.00089787 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6008-3_1_4_load_104 | 70 | 0.0028321 | 0.00070979 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6008-3_1_4_load_105 | 71 | 0.0018183 | 0.00045571 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6008-3_1_4_load_106 | 72 | 0.0030781 | 0.00077145 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6008-3_1_4_load_107 | 73 | 0.0017727 | 0.00044427 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6008-3_1_4_load_109 | 74 | 0.0021629 | 0.00054206 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6008-3_1_4_load_117 | 75 | 0.0017824 | 0.00044672 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6008-3_1_4_load_118 | 76 | 0.0038994 | 0.00097727 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6008-3_1_4_load_116 | 77 | 0.0009641 | 0.00024163 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6008-3_1_4_load_128 | 78 | 0.0014408 | 0.00036111 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6008-3_1_4_load_126 | 79 | 0.0010469 | 0.00026238 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6008-3_1_4_load_138 | 80 | 0.0021576 | 0.00054074 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6008-3_1_4_load_129 | 81 | 0.0019894 | 0.00049858 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6008-3_1_4_load_124 | 82 | 0.0012603 | 0.00031587 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6008-3_1_4_load_125 | 83 | 0.00085874 | 0.00021522 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6008-3_1_4_line_0 |  | 0 | 1 | 0.04131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6008-3_1_4_line_1 |  | 0 | 2 | 0.019825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6008-3_1_4_line_2 |  | 0 | 3 | 0.077698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6008-3_1_4_line_3 |  | 1 | 26 | 0.04692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6008-3_1_4_line_4 |  | 2 | 22 | 0.022462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6008-3_1_4_line_5 |  | 3 | 21 | 0.021144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6008-3_1_4_line_6 |  | 4 | 5 | 0.4393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6008-3_1_4_line_7 |  | 4 | 6 | 0.013886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6008-3_1_4_line_8 |  | 5 | 7 | 0.32271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6008-3_1_4_line_9 |  | 6 | 8 | 0.25169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6008-3_1_4_line_10 |  | 7 | 12 | 0.073716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6008-3_1_4_line_11 |  | 8 | 16 | 0.27307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6008-3_1_4_line_12 |  | 8 | 9 | 0.70636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6008-3_1_4_line_13 |  | 9 | 10 | 0.10831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6008-3_1_4_line_14 |  | 9 | 11 | 0.32378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6008-3_1_4_line_15 |  | 10 | 79 | 0.021144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6008-3_1_4_line_16 |  | 11 | 56 | 0.21993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6008-3_1_4_line_17 |  | 12 | 13 | 0.027843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6008-3_1_4_line_18 |  | 13 | 14 | 0.094288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6008-3_1_4_line_19 |  | 14 | 15 | 0.028028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6008-3_1_4_line_20 |  | 15 | 17 | 0.061798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6008-3_1_4_line_21 |  | 17 | 18 | 0.13958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6008-3_1_4_line_22 |  | 18 | 19 | 0.48332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6008-3_1_4_line_23 |  | 18 | 20 | 0.21399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6008-3_1_4_line_24 |  | 19 | 80 | 0.030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6008-3_1_4_line_25 |  | 22 | 23 | 0.031512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6008-3_1_4_line_26 |  | 23 | 24 | 0.10246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6008-3_1_4_line_27 |  | 23 | 25 | 0.045034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6008-3_1_4_line_28 |  | 24 | 30 | 0.014896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6008-3_1_4_line_29 |  | 25 | 28 | 0.025537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6008-3_1_4_line_30 |  | 26 | 31 | 0.054568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6008-3_1_4_line_31 |  | 27 | 28 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6008-3_1_4_line_32 |  | 27 | 29 | 0.0065455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6008-3_1_4_line_33 |  | 31 | 37 | 0.064547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6008-3_1_4_line_34 |  | 31 | 38 | 0.033676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_6008-3_1_4_line_35 |  | 31 | 39 | 0.026816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_6008-3_1_4_line_36 |  | 31 | 40 | 0.027414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6008-3_1_4_line_37 |  | 32 | 33 | 0.057707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6008-3_1_4_line_38 |  | 33 | 77 | 0.14703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6008-3_1_4_line_39 |  | 33 | 43 | 0.026275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6008-3_1_4_line_40 |  | 33 | 56 | 0.089006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6008-3_1_4_line_41 |  | 34 | 35 | 0.029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6008-3_1_4_line_42 |  | 34 | 36 | 0.043778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6008-3_1_4_line_43 |  | 35 | 46 | 0.01932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6008-3_1_4_line_44 |  | 36 | 37 | 0.003902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6008-3_1_4_line_45 |  | 37 | 41 | 0.043993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6008-3_1_4_line_46 |  | 38 | 42 | 0.0039853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_6008-3_1_4_line_47 |  | 39 | 43 | 0.0085765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6008-3_1_4_line_48 |  | 40 | 44 | 0.023542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6008-3_1_4_line_49 |  | 42 | 47 | 0.0098604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_6008-3_1_4_line_50 |  | 45 | 46 | 0.029903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6008-3_1_4_line_51 |  | 47 | 67 | 0.03025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_6008-3_1_4_line_52 |  | 48 | 49 | 0.025733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6008-3_1_4_line_53 |  | 48 | 50 | 0.044801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6008-3_1_4_line_54 |  | 49 | 51 | 0.02208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6008-3_1_4_line_55 |  | 50 | 52 | 0.033397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6008-3_1_4_line_56 |  | 51 | 53 | 0.022989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6008-3_1_4_line_57 |  | 52 | 54 | 0.079884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6008-3_1_4_line_58 |  | 53 | 55 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6008-3_1_4_line_59 |  | 54 | 57 | 0.01153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6008-3_1_4_line_60 |  | 55 | 72 | 0.015915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6008-3_1_4_line_61 |  | 57 | 58 | 0.043419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6008-3_1_4_line_62 |  | 57 | 59 | 0.0037197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_6008-3_1_4_line_63 |  | 58 | 60 | 0.0090555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6008-3_1_4_line_64 |  | 59 | 61 | 0.026324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_6008-3_1_4_line_65 |  | 60 | 62 | 0.076784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6008-3_1_4_line_66 |  | 61 | 63 | 0.020386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_6008-3_1_4_line_67 |  | 62 | 64 | 0.037382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6008-3_1_4_line_68 |  | 63 | 67 | 0.023059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_6008-3_1_4_line_69 |  | 64 | 65 | 0.00023237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6008-3_1_4_line_70 |  | 65 | 66 | 0.016468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6008-3_1_4_line_71 |  | 68 | 69 | 0.027998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6008-3_1_4_line_72 |  | 68 | 70 | 0.0031253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6008-3_1_4_line_73 |  | 69 | 71 | 0.00045999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6008-3_1_4_line_74 |  | 70 | 72 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6008-3_1_4_line_75 |  | 71 | 73 | 0.038997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6008-3_1_4_line_76 |  | 73 | 74 | 0.014071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6008-3_1_4_line_77 |  | 74 | 75 | 0.010995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6008-3_1_4_line_78 |  | 75 | 76 | 0.0067076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6008-3_1_4_line_79 |  | 77 | 78 | 0.012478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6008-3_1_4_line_80 |  | 78 | 81 | 0.024193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6008-3_1_4_line_81 |  | 79 | 82 | 0.051991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6008-3_1_4_line_82 |  | 82 | 83 | 0.021963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6008-3_1_4_trafo_98 | 0.63 MVA 20/0.4 kV | 84 | 67 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2643881.0631 | 1128512.8569 | 2643906.1914 | 1128503.69 | 2643920.5876 | 1128501.4968
1 | 2643881.0631 | 1128512.8569 | 2643872.3679 | 1128500.7877 | 2643870.1407 | 1128496.3675
2 | 2643881.0631 | 1128512.8569 | 2643858.7136 | 1128517.0637 | 2643825.907 | 1128518.4379 | 2643803.6083 | 1128519.8884
3 | 2643920.5876 | 1128501.4968 | 2643926.4604 | 1128500.6022 | 2643959.7184 | 1128494.3849 | 2643966.8048 | 1128493.4682
4 | 2643860.0338 | 1128476.308 | 2643870.1407 | 1128496.3675
5 | 2643803.6083 | 1128519.8884 | 2643794.6018 | 1128539.0177
6 | 2645079.002 | 1127371.4738 | 2645075.0207 | 1127374.2344 | 2645070.7819 | 1127377.4379 | 2645063.8811 | 1127384.2122 | 2645051.3894 | 1127396.7368 | 2645019.8064 | 1127455.4542 | 2645006.9226 | 1127492.7554 | 2644986.7711 | 1127535.4609 | 2644955.8454 | 1127608.5576 | 2644948.1695 | 1127621.1848 | 2644924.8452 | 1127644.0457 | 2644898.1753 | 1127679.5994 | 2644894.4649 | 1127688.4653 | 2644894.1543 | 1127697.0897 | 2644898.8515 | 1127726.573 | 2644892.0768 | 1127754.8484
7 | 2644892.5749 | 1127768.7259 | 2644892.0768 | 1127754.8484
8 | 2645079.002 | 1127371.4738 | 2645084.1545 | 1127361.4848 | 2645060.9119 | 1127357.6431 | 2645066.3502 | 1127348.59 | 2645065.4063 | 1127334.6203 | 2645043.9071 | 1127335.6941 | 2645051.4532 | 1127320.9094 | 2645032.0373 | 1127319.5308 | 2645039.5849 | 1127305.5798 | 2645033.0182 | 1127298.5273 | 2645023.6524 | 1127280.3261 | 2645023.3037 | 1127271.2633 | 2645019.3023 | 1127251.868 | 2645016.1271 | 1127235.3581 | 2645008.3365 | 1127227.0626 | 2644998.7729 | 1127234.4064 | 2644992.587 | 1127233.1264 | 2644983.8968 | 1127233.8844 | 2644981.9237 | 1127221.5079 | 2644982.4685 | 1127204.203 | 2644981.7147 | 1127194.6814 | 2644981.3351 | 1127189.7761 | 2644979.7305 | 1127182.7605 | 2644973.5643 | 1127177.7677 | 2644971.1521 | 1127169.5122 | 2644967.696 | 1127162.772
9 | 2644892.5749 | 1127768.7259 | 2644897.2811 | 1127778.2879 | 2644928.0806 | 1127818.4704 | 2645028.2596 | 1127905.7819 | 2645037.3432 | 1127917.2443 | 2645041.8132 | 1127929.5061 | 2645047.7805 | 1127959.0212
10 | 2644967.696 | 1127162.772 | 2644975.9732 | 1127156.408 | 2644981.7263 | 1127152.6932 | 2644986.874 | 1127149.5743 | 2644991.8577 | 1127146.7321 | 2644997.0932 | 1127144.2364 | 2645000.4932 | 1127142.9722 | 2645002.8941 | 1127142.3897 | 2645005.1926 | 1127142.1066 | 2645008.0052 | 1127142.1164 | 2645010.7084 | 1127142.3255 | 2645012.9928 | 1127142.9095 | 2645015.6894 | 1127144.0079 | 2645022.2893 | 1127147.6588 | 2645024.3343 | 1127148.3077 | 2645026.3826 | 1127148.5008 | 2645027.9698 | 1127148.5349 | 2645029.8299 | 1127148.1374 | 2645033.3054 | 1127147.0849 | 2645034.0472 | 1127146.7917
11 | 2645047.7805 | 1127959.0212 | 2645032.5283 | 1127928.5254 | 2645020.5296 | 1127912.25 | 2645010.7054 | 1127905.051 | 2644990.8314 | 1127896.1098 | 2644977.0148 | 1127885.9463 | 2644965.71 | 1127875.7904 | 2644939.3133 | 1127866.3673 | 2644903.1933 | 1127843.3764 | 2644862.6277 | 1127823.432 | 2644849.2362 | 1127789.1373
12 | 2644503.8048 | 1128409.6175 | 2645047.7805 | 1127959.0212
13 | 2644503.8048 | 1128409.6175 | 2644507.883 | 1128417.6405 | 2644509.6679 | 1128426.3581 | 2644508.4171 | 1128437.1878 | 2644504.5085 | 1128454.2901 | 2644498.0874 | 1128469.4284 | 2644496.3669 | 1128479.1874 | 2644489.9472 | 1128494.1368 | 2644486.6641 | 1128504.7626 | 2644488.3037 | 1128512.8228
14 | 2644222.6967 | 1128343.2786 | 2644235.3754 | 1128345.7725 | 2644270.8355 | 1128365.164 | 2644277.8449 | 1128367.4831 | 2644296.658 | 1128371.823 | 2644306.8798 | 1128376.289 | 2644312.7491 | 1128380.7009 | 2644316.0513 | 1128387.4063 | 2644321.1394 | 1128410.1107 | 2644324.0374 | 1128414.1563 | 2644328.8564 | 1128417.8379 | 2644364.1831 | 1128434.3163 | 2644372.1258 | 1128434.3745 | 2644387.087 | 1128430.2488 | 2644414.5098 | 1128415.12 | 2644440.2543 | 1128409.2837 | 2644464.2078 | 1128407.0807 | 2644483.6668 | 1128406.3233 | 2644497.364 | 1128407.5135 | 2644503.8048 | 1128409.6175
15 | 2644488.3037 | 1128512.8228 | 2644488.6344 | 1128514.4487 | 2644490.2992 | 1128525.8779 | 2644485.9445 | 1128532.5117
16 | 2644222.6967 | 1128343.2786 | 2644220.137 | 1128345.6389 | 2644219.8515 | 1128348.8718 | 2644221.3664 | 1128358.7435 | 2644234.8877 | 1128375.5843 | 2644245.856 | 1128392.8177 | 2644254.9471 | 1128403.3452 | 2644266.8625 | 1128417.4729 | 2644261.7203 | 1128424.261 | 2644250.6432 | 1128427.1926 | 2644242.4347 | 1128433.9805 | 2644235.8853 | 1128434.0771 | 2644228.1063 | 1128439.0339 | 2644220.6922 | 1128442.5482 | 2644209.5266 | 1128443.8896 | 2644202.8114 | 1128448.7541 | 2644183.1198 | 1128461.3502 | 2644161.5184 | 1128469.6079 | 2644154.9172 | 1128474.3897
17 | 2645060.0829 | 1127137.8572 | 2645057.8956 | 1127137.6964 | 2645055.4742 | 1127137.9341 | 2645052.3389 | 1127138.8223 | 2645039.8207 | 1127144.5099 | 2645034.0472 | 1127146.7917
18 | 2645060.0829 | 1127137.8572 | 2645062.4831 | 1127138.3976 | 2645065.8795 | 1127139.7013 | 2645070.5089 | 1127142.0148 | 2645076.4395 | 1127145.5274 | 2645082.5586 | 1127149.5861 | 2645083.0805 | 1127145.7214 | 2645082.1704 | 1127143.7692 | 2645075.0789 | 1127135.7567 | 2645067.9484 | 1127129.8895 | 2645059.9242 | 1127121.9145 | 2645057.7534 | 1127120.5754 | 2645047.9296 | 1127116.2557 | 2645041.4091 | 1127114.3506 | 2645040.3096 | 1127112.9862 | 2645040.3211 | 1127111.441 | 2645040.2427 | 1127103.3363
19 | 2645040.2427 | 1127103.3363 | 2645034.7088 | 1127102.4391 | 2645027.8723 | 1127101.5767 | 2645020.3377 | 1127101.3205 | 2645014.7279 | 1127101.301 | 2645012.3539 | 1127101.5002
20 | 2644956.1585 | 1127124.6222 | 2644962.0655 | 1127119.9081 | 2644969.2752 | 1127115.137 | 2644977.2839 | 1127110.7053 | 2644985.639 | 1127107.3546 | 2644995.2323 | 1127104.3354 | 2645002.0794 | 1127102.741 | 2645008.6441 | 1127101.8116 | 2645012.3539 | 1127101.5002
21 | 2644956.1585 | 1127124.6222 | 2644958.2693 | 1127115.3776 | 2644958.8675 | 1127113.6923 | 2644954.3829 | 1127114.6928 | 2644951.9064 | 1127116.1196 | 2644937.3856 | 1127127.8956 | 2644918.0785 | 1127159.5242 | 2644894.6458 | 1127171.8567 | 2644893.2991 | 1127150.8359 | 2644889.9951 | 1127156.8144 | 2644880.7538 | 1127162.2598
22 | 2644880.7538 | 1127162.2598 | 2644876.1201 | 1127165.7162 | 2644864.466 | 1127180.6374 | 2644853.9648 | 1127207.3956 | 2644846.2036 | 1127206.5488 | 2644841.381 | 1127179.3435 | 2644840.4696 | 1127149.4659 | 2644842.8342 | 1127123.6256 | 2644844.5335 | 1127103.3389 | 2644844.5904 | 1127081.0946 | 2644845.6609 | 1127048.9526 | 2644854.9435 | 1127019.2395 | 2644860.3451 | 1127002.6599 | 2644850.8908 | 1126983.8023 | 2644897.7379 | 1126949.3319 | 2644903.4642 | 1126937.8351 | 2644904.8372 | 1126923.1266 | 2644902.2562 | 1126916.8153 | 2644894.0572 | 1126937.5318 | 2644890.8096 | 1126943.1662 | 2644887.7959 | 1126946.3566 | 2644883.2775 | 1126949.8249 | 2644877.7371 | 1126952.8854 | 2644872.2025 | 1126955.1789 | 2644844.6387 | 1126963.3233 | 2644837.0813 | 1126966.1243 | 2644829.8272 | 1126969.5946 | 2644825.1204 | 1126972.4945
23 | 2644880.7538 | 1127162.2598 | 2644896.6502 | 1127101.1241 | 2644909.145 | 1127071.5904 | 2644924.8285 | 1127052.6749 | 2644945.348 | 1127043.578 | 2645015.719 | 1127029.6388
24 | 2644801.375 | 1126987.4264 | 2644809.8478 | 1126976.5169 | 2644811.8872 | 1126974.8089 | 2644814.7953 | 1126973.3852 | 2644817.9842 | 1126972.5417 | 2644821.0545 | 1126972.0976 | 2644825.1204 | 1126972.4945
25 | 2643861.968 | 1128447.5517 | 2643866.3571 | 1128466.9935 | 2643865.2576 | 1128470.9431 | 2643860.0338 | 1128476.308
26 | 2643861.968 | 1128447.5517 | 2643887.5139 | 1128456.2525 | 2643908.6467 | 1128460.4857 | 2643939.1816 | 1128492.9684 | 2643948.3782 | 1128491.3255
27 | 2643861.968 | 1128447.5517 | 2643844.289 | 1128432.3603 | 2643838.0809 | 1128430.0141 | 2643823.0834 | 1128428.3647
28 | 2643963.0416 | 1128488.7061 | 2643948.3782 | 1128491.3255
29 | 2643798.2537 | 1128423.9105 | 2643801.8303 | 1128426.0274 | 2643823.0834 | 1128428.3647
30 | 2644020.9676 | 1128486.8706 | 2643999.7649 | 1128489.0843 | 2643980.3851 | 1128491.7114 | 2643966.8048 | 1128493.4682
31 | 2643782.8236 | 1128409.1758 | 2643785.7509 | 1128411.1923 | 2643793.3303 | 1128420.9966 | 2643798.2537 | 1128423.9105
32 | 2643777.4332 | 1128405.4626 | 2643782.8236 | 1128409.1758
33 | 2644020.9676 | 1128486.8706 | 2644009.4524 | 1128508.7537 | 2644006.7409 | 1128526.6987 | 2644007.8778 | 1128548.3403
34 | 2644020.9676 | 1128486.8706 | 2644032.4994 | 1128473.3031 | 2644036.9573 | 1128464.1753 | 2644037.6837 | 1128458.5101
35 | 2644020.9676 | 1128486.8706 | 2644046.0494 | 1128484.1184 | 2644047.5999 | 1128484.4416
36 | 2644020.9676 | 1128486.8706 | 2644020.2826 | 1128509.0103 | 2644021.1004 | 1128514.21
37 | 2644073.6978 | 1128505.5528 | 2644067.7027 | 1128507.8437 | 2644063.636 | 1128526.7238 | 2644067.9504 | 1128556.3259 | 2644068.2479 | 1128558.365
38 | 2644073.6978 | 1128505.5528 | 2644085.8541 | 1128525.774 | 2644093.0299 | 1128529.5504 | 2644099.3503 | 1128528.0846 | 2644131.0044 | 1128504.1141 | 2644136.5093 | 1128505.6662 | 2644146.6831 | 1128512.4772 | 2644159.9761 | 1128527.8487 | 2644167.37 | 1128532.3605 | 2644188.2251 | 1128539.9298
39 | 2644073.6978 | 1128505.5528 | 2644069.9441 | 1128500.5118 | 2644055.9959 | 1128486.1918
40 | 2644073.6978 | 1128505.5528 | 2644075.2742 | 1128504.8973 | 2644078.9965 | 1128502.6344 | 2644084.9235 | 1128499.1202 | 2644101.681 | 1128491.6051 | 2644116.3589 | 1128488.2436 | 2644131.2997 | 1128482.6386 | 2644142.1167 | 1128483.6624 | 2644154.9172 | 1128474.3897
41 | 2644016.6277 | 1128595.2057 | 2643994.3203 | 1128577.7568 | 2643993.3854 | 1128576.6878
42 | 2644016.6277 | 1128595.2057 | 2644009.4545 | 1128558.2346 | 2644008.4918 | 1128552.1937
43 | 2643993.3854 | 1128576.6878 | 2643982.1488 | 1128563.839 | 2643980.6188 | 1128562.1881
44 | 2644007.8778 | 1128548.3403 | 2644008.4918 | 1128552.1937
45 | 2644007.8778 | 1128548.3403 | 2644004.1209 | 1128546.9011 | 2643997.3507 | 1128537.1358 | 2643990.0398 | 1128522.2528 | 2643985.8266 | 1128511.5167
46 | 2644037.6837 | 1128458.5101 | 2644038.1906 | 1128454.5571 | 2644038.1906 | 1128454.5571
47 | 2644047.5999 | 1128484.4416 | 2644055.9959 | 1128486.1918
48 | 2644021.1004 | 1128514.21 | 2644022.4548 | 1128522.8221 | 2644027.6855 | 1128536.6931
49 | 2644034.7215 | 1128445.3271 | 2644034.7215 | 1128445.3271 | 2644038.1906 | 1128454.5571
50 | 2643962.1525 | 1128539.0192 | 2643965.0335 | 1128545.3718 | 2643980.6188 | 1128562.1881
51 | 2644007.5851 | 1128432.9014 | 2644031.2422 | 1128441.7444 | 2644034.7215 | 1128445.3271
52 | 2643964.8449 | 1128345.7751 | 2643976.5088 | 1128345.6083 | 2643983.9054 | 1128347.6743 | 2643989.6904 | 1128350.384
53 | 2643964.8449 | 1128345.7751 | 2643950.7349 | 1128345.9769 | 2643944.4077 | 1128345.175 | 2643938.1006 | 1128340.549 | 2643935.2029 | 1128334.3026 | 2643933.7589 | 1128324.8075
54 | 2644009.686 | 1128359.7499 | 2643989.6904 | 1128350.384
55 | 2643916.0262 | 1128307.8165 | 2643925.9167 | 1128304.909 | 2643928.646 | 1128305.707 | 2643931.3644 | 1128309.0618 | 2643933.7589 | 1128324.8075
56 | 2644031.7445 | 1128366.0322 | 2644012.883 | 1128361.2474 | 2644009.686 | 1128359.7499
57 | 2643916.0262 | 1128307.8165 | 2643919.7586 | 1128313.7133 | 2643921.662 | 1128320.0192 | 2643922.2965 | 1128346.1705 | 2643925.6262 | 1128358.7234 | 2643930.1616 | 1128366.4825 | 2643942.7256 | 1128379.6292
58 | 2644031.7445 | 1128366.0322 | 2644050.3696 | 1128370.757
59 | 2643950.6918 | 1128387.9648 | 2643942.7256 | 1128379.6292
60 | 2644064.8505 | 1128376.8822 | 2644058.2704 | 1128372.7613 | 2644050.3696 | 1128370.757
61 | 2643950.6918 | 1128387.9648 | 2643960.5573 | 1128382.1223 | 2643967.0171 | 1128381.6356 | 2643991.1513 | 1128389.7916
62 | 2643950.6918 | 1128387.9648 | 2643953.3426 | 1128390.5743
63 | 2643991.1513 | 1128389.7916 | 2643999.7302 | 1128392.6907
64 | 2643953.3426 | 1128390.5743 | 2643972.1018 | 1128409.042
65 | 2643999.7302 | 1128392.6907 | 2644008.2342 | 1128395.5645 | 2644015.227 | 1128395.9378 | 2644029.6365 | 1128394.5419 | 2644042.078 | 1128396.8002 | 2644051.0521 | 1128400.1784 | 2644069.4473 | 1128415.739
66 | 2643972.1018 | 1128409.042 | 2643986.6295 | 1128423.344
67 | 2644069.4473 | 1128415.739 | 2644085.0803 | 1128428.9631 | 2644088.4761 | 1128434.5018 | 2644092.4201 | 1128444.1346
68 | 2643986.6295 | 1128423.344 | 2643986.6295 | 1128423.344 | 2644000.6085 | 1128430.2936 | 2644007.5851 | 1128432.9014
69 | 2644092.5082 | 1128444.3496 | 2644092.4201 | 1128444.1346
70 | 2644098.7479 | 1128459.5895 | 2644092.5082 | 1128444.3496
71 | 2644082.2249 | 1128389.9831 | 2644090.0271 | 1128396.1045 | 2644103.7439 | 1128407.8844
72 | 2644082.2249 | 1128389.9831 | 2644079.7661 | 1128388.0539
73 | 2644104.0928 | 1128408.1841 | 2644103.7439 | 1128407.8844
74 | 2644079.7661 | 1128388.0539 | 2644068.2022 | 1128378.9812 | 2644064.8505 | 1128376.8822
75 | 2644104.0928 | 1128408.1841 | 2644108.4484 | 1128411.9246 | 2644116.506 | 1128415.2517 | 2644124.642 | 1128415.2221 | 2644139.2247 | 1128411.2042 | 2644140.4873 | 1128411.389
76 | 2644152.7604 | 1128417.5806 | 2644144.8198 | 1128412.0232 | 2644140.4873 | 1128411.389
77 | 2644160.3302 | 1128425.4827 | 2644154.5469 | 1128418.8309 | 2644152.7604 | 1128417.5806
78 | 2644164.7312 | 1128430.5446 | 2644160.3302 | 1128425.4827
79 | 2644198.7016 | 1128546.4119 | 2644192.6266 | 1128541.5274 | 2644188.2251 | 1128539.9298
80 | 2644212.4832 | 1128565.3624 | 2644207.6539 | 1128553.61 | 2644198.7016 | 1128546.4119
81 | 2644464.1031 | 1128577.9601 | 2644462.8786 | 1128571.1441 | 2644467.1215 | 1128561.9928 | 2644481.9546 | 1128538.5898 | 2644485.9445 | 1128532.5117
82 | 2644464.1031 | 1128577.9601 | 2644467.7339 | 1128598.1714 | 2644467.9204 | 1128599.587

## bus_geodata
| x | y | coords
0 | 2643881.0631 | 1128512.8569
1 | 2643920.5876 | 1128501.4968
2 | 2643870.1407 | 1128496.3675
3 | 2643803.6083 | 1128519.8884
4 | 2644892.0768 | 1127754.8484
5 | 2645079.002 | 1127371.4738
6 | 2644892.5749 | 1127768.7259
7 | 2644967.696 | 1127162.772
8 | 2645047.7805 | 1127959.0212
9 | 2644503.8048 | 1128409.6175
10 | 2644488.3037 | 1128512.8228
11 | 2644222.6967 | 1128343.2786
12 | 2645034.0472 | 1127146.7917
13 | 2645060.0829 | 1127137.8572
14 | 2645040.2427 | 1127103.3363
15 | 2645012.3539 | 1127101.5002
16 | 2644849.2362 | 1127789.1373
17 | 2644956.1585 | 1127124.6222
18 | 2644880.7538 | 1127162.2598
19 | 2644825.1204 | 1126972.4945
20 | 2645015.719 | 1127029.6388
21 | 2643794.6018 | 1128539.0177
22 | 2643860.0338 | 1128476.308
23 | 2643861.968 | 1128447.5517
24 | 2643948.3782 | 1128491.3255
25 | 2643823.0834 | 1128428.3647
26 | 2643966.8048 | 1128493.4682
27 | 2643782.8236 | 1128409.1758
28 | 2643798.2537 | 1128423.9105
29 | 2643777.4332 | 1128405.4626
30 | 2643963.0416 | 1128488.7061
31 | 2644020.9676 | 1128486.8706
32 | 2644068.2479 | 1128558.365
33 | 2644073.6978 | 1128505.5528
34 | 2644016.6277 | 1128595.2057
35 | 2643993.3854 | 1128576.6878
36 | 2644008.4918 | 1128552.1937
37 | 2644007.8778 | 1128548.3403
38 | 2644037.6837 | 1128458.5101
39 | 2644047.5999 | 1128484.4416
40 | 2644021.1004 | 1128514.21
41 | 2643985.8266 | 1128511.5167
42 | 2644038.1906 | 1128454.5571
43 | 2644055.9959 | 1128486.1918
44 | 2644027.6855 | 1128536.6931
45 | 2643962.1525 | 1128539.0192
46 | 2643980.6188 | 1128562.1881
47 | 2644034.7215 | 1128445.3271
48 | 2643964.8449 | 1128345.7751
49 | 2643989.6904 | 1128350.384
50 | 2643933.7589 | 1128324.8075
51 | 2644009.686 | 1128359.7499
52 | 2643916.0262 | 1128307.8165
53 | 2644031.7445 | 1128366.0322
54 | 2643942.7257 | 1128379.6292
55 | 2644050.3696 | 1128370.757
56 | 2644154.9172 | 1128474.3897
57 | 2643950.6918 | 1128387.9648
58 | 2643991.1513 | 1128389.7916
59 | 2643953.3426 | 1128390.5743
60 | 2643999.7302 | 1128392.6907
61 | 2643972.1018 | 1128409.042
62 | 2644069.4473 | 1128415.739
63 | 2643986.6295 | 1128423.344
64 | 2644092.4201 | 1128444.1346
65 | 2644092.5082 | 1128444.3496
66 | 2644098.7479 | 1128459.5895
67 | 2644007.5851 | 1128432.9014
68 | 2644082.2249 | 1128389.9831
69 | 2644103.7439 | 1128407.8844
70 | 2644079.7661 | 1128388.0539
71 | 2644104.0928 | 1128408.1841
72 | 2644064.8505 | 1128376.8822
73 | 2644140.4873 | 1128411.389
74 | 2644152.7604 | 1128417.5807
75 | 2644160.3302 | 1128425.4827
76 | 2644164.7312 | 1128430.5446
77 | 2644188.2251 | 1128539.9298
78 | 2644198.7016 | 1128546.4119
79 | 2644485.9445 | 1128532.5117
80 | 2644801.3751 | 1126987.4264
81 | 2644212.4832 | 1128565.3624
82 | 2644464.1031 | 1128577.9601
83 | 2644467.9204 | 1128599.587
84 | 2643950.6918 | 1128387.9648

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1