## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6089-18_1_3_node_10 | 0.4 | n |  | TRUE
1 | bus_LV_6089-18_1_3_node_12 | 0.4 | n |  | TRUE
2 | bus_LV_6089-18_1_3_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_6089-18_1_3_node_14 | 0.4 | n |  | TRUE
4 | bus_LV_6089-18_1_3_node_99 | 0.4 | n |  | TRUE
5 | bus_LV_6089-18_1_3_node_72 | 0.4 | n |  | TRUE
6 | bus_LV_6089-18_1_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_6089-18_1_3_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_6089-18_1_3_node_71 | 0.4 | n |  | TRUE
9 | bus_LV_6089-18_1_3_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_6089-18_1_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_6089-18_1_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_6089-18_1_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_6089-18_1_3_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_6089-18_1_3_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_6089-18_1_3_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_6089-18_1_3_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_6089-18_1_3_node_68 | 0.4 | n |  | TRUE
18 | bus_LV_6089-18_1_3_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_6089-18_1_3_node_67 | 0.4 | n |  | TRUE
20 | bus_LV_6089-18_1_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_6089-18_1_3_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_6089-18_1_3_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_6089-18_1_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_6089-18_1_3_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_6089-18_1_3_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_6089-18_1_3_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_6089-18_1_3_node_46 | 0.4 | n |  | TRUE
28 | bus_LV_6089-18_1_3_node_52 | 0.4 | n |  | TRUE
29 | bus_LV_6089-18_1_3_node_53 | 0.4 | n |  | TRUE
30 | bus_LV_6089-18_1_3_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_6089-18_1_3_node_55 | 0.4 | n |  | TRUE
32 | bus_LV_6089-18_1_3_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_6089-18_1_3_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_6089-18_1_3_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_6089-18_1_3_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_6089-18_1_3_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_6089-18_1_3_node_59 | 0.4 | n |  | TRUE
38 | bus_LV_6089-18_1_3_node_57 | 0.4 | n |  | TRUE
39 | bus_LV_6089-18_1_3_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_6089-18_1_3_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_6089-18_1_3_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_6089-18_1_3_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_6089-18_1_3_node_66 | 0.4 | n |  | TRUE
44 | bus_LV_6089-18_1_3_node_77 | 0.4 | n |  | TRUE
45 | bus_LV_6089-18_1_3_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_6089-18_1_3_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_6089-18_1_3_node_70 | 0.4 | n |  | TRUE
48 | bus_LV_6089-18_1_3_node_73 | 0.4 | n |  | TRUE
49 | bus_LV_6089-18_1_3_node_74 | 0.4 | n |  | TRUE
50 | bus_LV_6089-18_1_3_node_81 | 0.4 | n |  | TRUE
51 | bus_LV_6089-18_1_3_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_6089-18_1_3_node_76 | 0.4 | n |  | TRUE
53 | bus_LV_6089-18_1_3_node_79 | 0.4 | n |  | TRUE
54 | bus_LV_6089-18_1_3_node_82 | 0.4 | n |  | TRUE
55 | bus_MV_90_2_node_104 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6089-18_1_3_load_10 | 0 | 0.0017704 | 0.0004437 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6089-18_1_3_load_14 | 3 | 0.0074205 | 0.0018597 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6089-18_1_3_load_99 | 4 | 0.010596 | 0.0026556 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6089-18_1_3_load_16 | 6 | 0.014047 | 0.0035206 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6089-18_1_3_load_80 | 7 | 0.0075621 | 0.0018953 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6089-18_1_3_load_17 | 9 | 0.0073158 | 0.0018335 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6089-18_1_3_load_18 | 10 | 0.0058339 | 0.0014621 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6089-18_1_3_load_23 | 11 | 0.0034942 | 0.00087573 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6089-18_1_3_load_24 | 12 | 0.0042468 | 0.0010644 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6089-18_1_3_load_25 | 13 | 0.0038185 | 0.000957 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6089-18_1_3_load_26 | 14 | 0.0028713 | 0.00071963 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6089-18_1_3_load_27 | 15 | 0.0049128 | 0.0012313 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6089-18_1_3_load_30 | 16 | 0.004379 | 0.0010975 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6089-18_1_3_load_68 | 17 | 0.0060192 | 0.0015085 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6089-18_1_3_load_28 | 18 | 0.0033555 | 0.00084096 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6089-18_1_3_load_67 | 19 | 0.0055969 | 0.0014027 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6089-18_1_3_load_29 | 20 | 0.0036107 | 0.00090493 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6089-18_1_3_load_31 | 21 | 0.0032792 | 0.00082183 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6089-18_1_3_load_35 | 22 | 0.0046335 | 0.0011613 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6089-18_1_3_load_36 | 23 | 0.0044401 | 0.0011128 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6089-18_1_3_load_44 | 24 | 0.0078817 | 0.0019753 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6089-18_1_3_load_45 | 25 | 0.0092671 | 0.0023226 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6089-18_1_3_load_47 | 26 | 0.0046183 | 0.0011575 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6089-18_1_3_load_46 | 27 | 0.0033896 | 0.00084952 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6089-18_1_3_load_52 | 28 | 0.0038332 | 0.00096069 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6089-18_1_3_load_53 | 29 | 0.0043616 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6089-18_1_3_load_48 | 30 | 0.0029838 | 0.00074781 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6089-18_1_3_load_55 | 31 | 0.004571 | 0.0011456 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6089-18_1_3_load_54 | 33 | 0.0029281 | 0.00073385 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6089-18_1_3_load_61 | 34 | 0.0099436 | 0.0024921 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6089-18_1_3_load_60 | 35 | 0.0044779 | 0.0011223 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6089-18_1_3_load_62 | 36 | 0.0072576 | 0.0018189 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6089-18_1_3_load_59 | 37 | 0.0036692 | 0.00091959 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6089-18_1_3_load_57 | 38 | 0.011791 | 0.0029552 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6089-18_1_3_load_58 | 39 | 0.0068498 | 0.0017167 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6089-18_1_3_load_63 | 40 | 0.008647 | 0.0021671 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6089-18_1_3_load_64 | 41 | 0.0069761 | 0.0017484 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6089-18_1_3_load_65 | 42 | 0.01061 | 0.0026591 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6089-18_1_3_load_66 | 43 | 0.0039102 | 0.00097998 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6089-18_1_3_load_77 | 44 | 0.0060409 | 0.001514 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6089-18_1_3_load_78 | 45 | 0.0015141 | 0.00037947 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6089-18_1_3_load_69 | 46 | 0.0028043 | 0.00070281 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6089-18_1_3_load_70 | 47 | 0.0055621 | 0.001394 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6089-18_1_3_load_73 | 48 | 0.0048676 | 0.0012199 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6089-18_1_3_load_74 | 49 | 0.0056642 | 0.0014196 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6089-18_1_3_load_81 | 50 | 0.0047504 | 0.0011906 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6089-18_1_3_load_75 | 51 | 0.0061719 | 0.0015468 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6089-18_1_3_load_76 | 52 | 0.0032276 | 0.00080891 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6089-18_1_3_load_79 | 53 | 0.0019738 | 0.00049467 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6089-18_1_3_load_82 | 54 | 0.0024627 | 0.00061722 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6089-18_1_3_line_0 |  | 0 | 1 | 0.038134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6089-18_1_3_line_1 |  | 1 | 2 | 0.052639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6089-18_1_3_line_2 |  | 1 | 3 | 0.018468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6089-18_1_3_line_3 |  | 2 | 4 | 0.053423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6089-18_1_3_line_4 |  | 2 | 5 | 0.032626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6089-18_1_3_line_5 |  | 3 | 6 | 0.045024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6089-18_1_3_line_6 |  | 5 | 7 | 0.052751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6089-18_1_3_line_7 |  | 5 | 8 | 0.042172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6089-18_1_3_line_8 |  | 6 | 9 | 0.0076625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6089-18_1_3_line_9 |  | 7 | 50 | 0.056382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6089-18_1_3_line_10 |  | 8 | 48 | 0.011976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6089-18_1_3_line_11 |  | 8 | 47 | 0.024889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6089-18_1_3_line_12 |  | 9 | 10 | 0.003315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6089-18_1_3_line_13 |  | 11 | 12 | 0.015207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_6089-18_1_3_line_14 |  | 11 | 13 | 0.0087202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_6089-18_1_3_line_15 |  | 12 | 14 | 0.019832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_6089-18_1_3_line_16 |  | 13 | 15 | 0.0028517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_6089-18_1_3_line_17 |  | 14 | 16 | 0.0087175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_6089-18_1_3_line_18 |  | 15 | 17 | 0.0043395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_6089-18_1_3_line_19 |  | 16 | 18 | 0.0041028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_6089-18_1_3_line_20 |  | 17 | 19 | 0.055647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_6089-18_1_3_line_21 |  | 18 | 20 | 0.017522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_6089-18_1_3_line_22 |  | 19 | 46 | 0.031641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6089-18_1_3_line_23 |  | 20 | 21 | 0.0039231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_6089-18_1_3_line_24 |  | 21 | 22 | 0.050373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_6089-18_1_3_line_25 |  | 22 | 23 | 0.028146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_6089-18_1_3_line_26 |  | 23 | 24 | 0.021601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_6089-18_1_3_line_27 |  | 24 | 25 | 0.033131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_6089-18_1_3_line_28 |  | 24 | 26 | 0.069341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6089-18_1_3_line_29 |  | 25 | 27 | 0.0241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_6089-18_1_3_line_30 |  | 27 | 28 | 0.0075016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6089-18_1_3_line_31 |  | 28 | 29 | 0.018342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6089-18_1_3_line_32 |  | 29 | 33 | 0.00092412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6089-18_1_3_line_33 |  | 30 | 31 | 0.14309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6089-18_1_3_line_34 |  | 31 | 32 | 0.019734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6089-18_1_3_line_35 |  | 31 | 33 | 0.0046407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6089-18_1_3_line_36 |  | 32 | 34 | 0.041933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6089-18_1_3_line_37 |  | 32 | 35 | 0.0058199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6089-18_1_3_line_38 |  | 34 | 36 | 0.029647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6089-18_1_3_line_39 |  | 35 | 37 | 0.0099797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6089-18_1_3_line_40 |  | 36 | 40 | 0.0049268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6089-18_1_3_line_41 |  | 37 | 38 | 0.0078784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6089-18_1_3_line_42 |  | 38 | 39 | 0.043599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6089-18_1_3_line_43 |  | 40 | 41 | 0.021902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6089-18_1_3_line_44 |  | 41 | 42 | 0.012898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6089-18_1_3_line_45 |  | 42 | 43 | 0.023383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6089-18_1_3_line_46 |  | 43 | 44 | 0.018166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6089-18_1_3_line_47 |  | 44 | 45 | 0.013444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6089-18_1_3_line_48 |  | 45 | 53 | 0.017641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6089-18_1_3_line_49 |  | 46 | 47 | 0.0061578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6089-18_1_3_line_50 |  | 48 | 49 | 0.034111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6089-18_1_3_line_51 |  | 49 | 51 | 0.026691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6089-18_1_3_line_52 |  | 50 | 54 | 0.0058872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6089-18_1_3_line_53 |  | 51 | 52 | 0.014306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6089-18_1_3_trafo_67 | 0.63 MVA 20/0.4 kV | 55 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2596983.1093 | 1118347.1515 | 2596973.1873 | 1118335.4286 | 2596962.4993 | 1118315.3158
1 | 2596983.1093 | 1118347.1515 | 2596984.2984 | 1118348.5627 | 2597000.2705 | 1118360.5493 | 2597002.8403 | 1118391.2964
2 | 2596983.1093 | 1118347.1515 | 2596996.1904 | 1118334.1143
3 | 2597002.8403 | 1118391.2964 | 2597005.7782 | 1118387.0928 | 2597007.6353 | 1118381.9338 | 2597012.1824 | 1118370.4815 | 2597016.8391 | 1118362.1306 | 2597029.8721 | 1118345.716
4 | 2596988.27 | 1118419.2953 | 2596989.6559 | 1118413.1249 | 2596998.3558 | 1118404.3717 | 2597001.6707 | 1118397.9002 | 2597002.8403 | 1118391.2964
5 | 2596996.1904 | 1118334.1143 | 2597026.3863 | 1118304.0195 | 2597027.9838 | 1118302.2397
6 | 2596988.27 | 1118419.2953 | 2596971.3049 | 1118426.6409 | 2596938.8543 | 1118437.6408
7 | 2597022.3345 | 1118395.0106 | 2597009.9013 | 1118407.0227 | 2596997.2348 | 1118415.411 | 2596988.27 | 1118419.2953
8 | 2597033.102 | 1118296.5373 | 2597027.9838 | 1118302.2397
9 | 2596938.8543 | 1118437.6408 | 2596938.8543 | 1118437.6408 | 2596904.632 | 1118439.4261 | 2596882.5439 | 1118438.3701
10 | 2597022.3345 | 1118395.0106 | 2597017.9416 | 1118406.1516
11 | 2597022.3345 | 1118395.0106 | 2597032.6313 | 1118385.0561 | 2597041.5147 | 1118379.3325
12 | 2597033.102 | 1118296.5373 | 2597035.3164 | 1118294.0703
13 | 2597139.9451 | 1118333.8319 | 2597152.1575 | 1118324.7698
14 | 2597139.9451 | 1118333.8319 | 2597132.9423 | 1118339.0283
15 | 2597165.6042 | 1118310.9749 | 2597163.1187 | 1118316.6362 | 2597152.1575 | 1118324.7698
16 | 2597132.9423 | 1118339.0283 | 2597130.6522 | 1118340.7276
17 | 2597165.6042 | 1118310.9749 | 2597169.1086 | 1118302.9929
18 | 2597130.6522 | 1118340.7276 | 2597127.1673 | 1118343.3135
19 | 2597170.758 | 1118299.2362 | 2597169.1086 | 1118302.9929
20 | 2597075.4484 | 1118363.1426 | 2597102.854 | 1118355.151 | 2597124.757 | 1118345.1021 | 2597127.1673 | 1118343.3135
21 | 2597170.758 | 1118299.2362 | 2597176.9629 | 1118285.103 | 2597177.7304 | 1118283.1622
22 | 2597075.4484 | 1118363.1426 | 2597071.2354 | 1118364.3711 | 2597053.3517 | 1118371.7058 | 2597046.6911 | 1118375.9973
23 | 2597177.7304 | 1118283.1622 | 2597179.173 | 1118279.514
24 | 2597179.173 | 1118279.514 | 2597228.5877 | 1118289.2938
25 | 2597228.5877 | 1118289.2938 | 2597225.2595 | 1118295.0406 | 2597222.1735 | 1118316.3235
26 | 2597222.1735 | 1118316.3235 | 2597220.6444 | 1118326.8694 | 2597219.3118 | 1118337.7326
27 | 2597219.3118 | 1118337.7326 | 2597215.2776 | 1118370.6173
28 | 2597219.3118 | 1118337.7326 | 2597284.4485 | 1118361.5093
29 | 2597215.2776 | 1118370.6173 | 2597214.1949 | 1118379.4427 | 2597205.373 | 1118391.8304
30 | 2597201.0214 | 1118397.9409 | 2597205.373 | 1118391.8304
31 | 2597201.0214 | 1118397.9409 | 2597190.3816 | 1118412.8814
32 | 2597190.3816 | 1118412.8814 | 2597190.3816 | 1118412.8814 | 2597189.6637 | 1118413.4633
33 | 2597186.0583 | 1118416.3852 | 2597270.7698 | 1118531.7029
34 | 2597170.7272 | 1118428.8097 | 2597186.0583 | 1118416.3852
35 | 2597189.6637 | 1118413.4633 | 2597186.0583 | 1118416.3852
36 | 2597170.7272 | 1118428.8097 | 2597142.7451 | 1118441.4961 | 2597131.9762 | 1118444.6068
37 | 2597170.7272 | 1118428.8097 | 2597166.4457 | 1118432.7519
38 | 2597103.3882 | 1118452.3702 | 2597105.0466 | 1118451.6639 | 2597121.9285 | 1118447.5092 | 2597131.9762 | 1118444.6068
39 | 2597166.4457 | 1118432.7519 | 2597159.1041 | 1118439.5117
40 | 2597103.3882 | 1118452.3702 | 2597098.8554 | 1118454.3008
41 | 2597153.3083 | 1118444.8482 | 2597159.1041 | 1118439.5117
42 | 2597153.3083 | 1118444.8482 | 2597147.7033 | 1118450.009 | 2597129.839 | 1118481.2409
43 | 2597079.372 | 1118464.1313 | 2597086.0754 | 1118459.7438 | 2597098.8554 | 1118454.3008
44 | 2597079.372 | 1118464.1313 | 2597068.5796 | 1118471.195
45 | 2597051.2178 | 1118486.753 | 2597053.0145 | 1118484.6613 | 2597065.2705 | 1118473.3608 | 2597068.5796 | 1118471.195
46 | 2597039.8685 | 1118500.8304 | 2597040.5287 | 1118499.1969 | 2597051.2178 | 1118486.753
47 | 2597039.8685 | 1118500.8304 | 2597034.8309 | 1118513.2951
48 | 2597027.8609 | 1118529.4793 | 2597029.4383 | 1118526.6381 | 2597034.8309 | 1118513.2951
49 | 2597041.5147 | 1118379.3325 | 2597046.6911 | 1118375.9973
50 | 2597017.9416 | 1118406.1516 | 2597017.9416 | 1118406.1516 | 2597011.4343 | 1118417.138 | 2597003.8797 | 1118437.0987
51 | 2597003.8797 | 1118437.0987 | 2596997.0004 | 1118455.2751 | 2596993.6563 | 1118461.7152
52 | 2596882.5439 | 1118438.3701 | 2596876.6634 | 1118438.089
53 | 2596987.0635 | 1118474.4118 | 2596993.6563 | 1118461.7152

## bus_geodata
| x | y | coords
0 | 2596962.4993 | 1118315.3158
1 | 2596983.1093 | 1118347.1515
2 | 2597002.8403 | 1118391.2964
3 | 2596996.1904 | 1118334.1143
4 | 2597029.8721 | 1118345.716
5 | 2596988.27 | 1118419.2953
6 | 2597027.9838 | 1118302.2397
7 | 2596938.8543 | 1118437.6408
8 | 2597022.3345 | 1118395.0106
9 | 2597033.102 | 1118296.5373
10 | 2597035.3164 | 1118294.0703
11 | 2597139.9451 | 1118333.8319
12 | 2597152.1575 | 1118324.7698
13 | 2597132.9423 | 1118339.0283
14 | 2597165.6042 | 1118310.9749
15 | 2597130.6522 | 1118340.7276
16 | 2597169.1086 | 1118302.9929
17 | 2597127.1673 | 1118343.3135
18 | 2597170.758 | 1118299.2362
19 | 2597075.4484 | 1118363.1426
20 | 2597177.7304 | 1118283.1622
21 | 2597179.173 | 1118279.514
22 | 2597228.5877 | 1118289.2938
23 | 2597222.1735 | 1118316.3235
24 | 2597219.3118 | 1118337.7326
25 | 2597215.2776 | 1118370.6173
26 | 2597284.4485 | 1118361.5093
27 | 2597205.373 | 1118391.8304
28 | 2597201.0214 | 1118397.9409
29 | 2597190.3816 | 1118412.8814
30 | 2597270.7698 | 1118531.7029
31 | 2597186.0583 | 1118416.3852
32 | 2597170.7272 | 1118428.8097
33 | 2597189.6637 | 1118413.4633
34 | 2597131.9762 | 1118444.6068
35 | 2597166.4457 | 1118432.7519
36 | 2597103.3882 | 1118452.3702
37 | 2597159.1041 | 1118439.5117
38 | 2597153.3083 | 1118444.8482
39 | 2597129.839 | 1118481.2409
40 | 2597098.8554 | 1118454.3008
41 | 2597079.372 | 1118464.1313
42 | 2597068.5796 | 1118471.195
43 | 2597051.2178 | 1118486.753
44 | 2597039.8685 | 1118500.8304
45 | 2597034.8309 | 1118513.2951
46 | 2597046.6911 | 1118375.9973
47 | 2597041.5147 | 1118379.3325
48 | 2597017.9416 | 1118406.1516
49 | 2597003.8797 | 1118437.0987
50 | 2596882.5439 | 1118438.3701
51 | 2596993.6563 | 1118461.7152
52 | 2596987.0635 | 1118474.4118
53 | 2597027.8609 | 1118529.4793
54 | 2596876.6634 | 1118438.089
55 | 2597022.3345 | 1118395.0106

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1