## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6131-2_1_4_node_129 | 0.4 | n |  | TRUE
1 | bus_LV_6131-2_1_4_node_41 | 0.4 | n |  | TRUE
2 | bus_LV_6131-2_1_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_6131-2_1_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_6131-2_1_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_6131-2_1_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_6131-2_1_4_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_6131-2_1_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_6131-2_1_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_6131-2_1_4_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_6131-2_1_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_6131-2_1_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_6131-2_1_4_node_47 | 0.4 | n |  | TRUE
13 | bus_LV_6131-2_1_4_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_6131-2_1_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_6131-2_1_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_6131-2_1_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_6131-2_1_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_6131-2_1_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_6131-2_1_4_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_6131-2_1_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_6131-2_1_4_node_125 | 0.4 | n |  | TRUE
22 | bus_LV_6131-2_1_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_6131-2_1_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_6131-2_1_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_6131-2_1_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_6131-2_1_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_6131-2_1_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_6131-2_1_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_6131-2_1_4_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_6131-2_1_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_6131-2_1_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_6131-2_1_4_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_6131-2_1_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_6131-2_1_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_6131-2_1_4_node_109 | 0.4 | n |  | TRUE
36 | bus_LV_6131-2_1_4_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_6131-2_1_4_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_6131-2_1_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_6131-2_1_4_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_6131-2_1_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_6131-2_1_4_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_6131-2_1_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_6131-2_1_4_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_6131-2_1_4_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_6131-2_1_4_node_127 | 0.4 | n |  | TRUE
46 | bus_MV_101_0_node_246 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6131-2_1_4_load_129 | 0 | 0.0035391 | 0.00088699 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6131-2_1_4_load_5 | 2 | 0.0032168 | 0.00080619 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6131-2_1_4_load_6 | 3 | 0.0029175 | 0.00073119 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6131-2_1_4_load_7 | 4 | 0.0056398 | 0.0014135 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6131-2_1_4_load_8 | 5 | 0.011124 | 0.002788 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6131-2_1_4_load_9 | 7 | 0.0044953 | 0.0011266 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6131-2_1_4_load_47 | 12 | 0.056597 | 0.014184 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6131-2_1_4_load_39 | 13 | 0.0032965 | 0.00082618 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6131-2_1_4_load_14 | 14 | 0.0046159 | 0.0011569 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6131-2_1_4_load_16 | 16 | 0.0059205 | 0.0014838 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6131-2_1_4_load_17 | 17 | 0.007351 | 0.0018423 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6131-2_1_4_load_35 | 19 | 0.0052216 | 0.0013087 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6131-2_1_4_load_46 | 20 | 0.0048623 | 0.0012186 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6131-2_1_4_load_125 | 21 | 0.0024271 | 0.00060828 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6131-2_1_4_load_19 | 22 | 0.0026218 | 0.00065709 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6131-2_1_4_load_20 | 23 | 0.0049155 | 0.0012319 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6131-2_1_4_load_21 | 24 | 0.0058308 | 0.0014613 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6131-2_1_4_load_23 | 27 | 0.004089 | 0.0010248 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6131-2_1_4_load_34 | 29 | 0.010101 | 0.0025315 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6131-2_1_4_load_32 | 30 | 0.0056112 | 0.0014063 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6131-2_1_4_load_26 | 31 | 0.0034238 | 0.00085808 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6131-2_1_4_load_29 | 32 | 0.005556 | 0.0013925 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6131-2_1_4_load_30 | 33 | 0.0044339 | 0.0011112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6131-2_1_4_load_109 | 35 | 0.0022983 | 0.00057601 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6131-2_1_4_load_40 | 40 | 0.004691 | 0.0011757 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6131-2_1_4_load_42 | 41 | 0.0048169 | 0.0012072 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6131-2_1_4_load_110 | 44 | 0.009656 | 0.00242 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6131-2_1_4_load_127 | 45 | 0.0044861 | 0.0011243 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6131-2_1_4_line_0 |  | 0 | 1 | 0.023031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6131-2_1_4_line_1 |  | 1 | 36 | 0.00729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6131-2_1_4_line_2 |  | 1 | 11 | 0.014438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_6131-2_1_4_line_3 |  | 2 | 3 | 0.020556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6131-2_1_4_line_4 |  | 2 | 4 | 0.037365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6131-2_1_4_line_5 |  | 3 | 5 | 0.03697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6131-2_1_4_line_6 |  | 5 | 6 | 0.032486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6131-2_1_4_line_7 |  | 6 | 32 | 0.036884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6131-2_1_4_line_8 |  | 6 | 31 | 0.024934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6131-2_1_4_line_9 |  | 7 | 8 | 0.048758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_6131-2_1_4_line_10 |  | 7 | 9 | 0.080307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_6131-2_1_4_line_11 |  | 8 | 10 | 0.1023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_6131-2_1_4_line_12 |  | 9 | 11 | 0.00323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_6131-2_1_4_line_13 |  | 10 | 12 | 0.05448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6131-2_1_4_line_14 |  | 11 | 13 | 0.031913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6131-2_1_4_line_15 |  | 12 | 39 | 0.016046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6131-2_1_4_line_16 |  | 13 | 40 | 0.0085668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6131-2_1_4_line_17 |  | 14 | 15 | 0.058504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6131-2_1_4_line_18 |  | 15 | 16 | 0.011187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6131-2_1_4_line_19 |  | 15 | 17 | 0.023728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6131-2_1_4_line_20 |  | 15 | 18 | 0.060384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6131-2_1_4_line_21 |  | 16 | 19 | 0.012273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6131-2_1_4_line_22 |  | 17 | 20 | 0.007314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6131-2_1_4_line_23 |  | 18 | 21 | 0.058194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6131-2_1_4_line_24 |  | 20 | 39 | 0.044923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6131-2_1_4_line_25 |  | 22 | 23 | 0.018877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6131-2_1_4_line_26 |  | 23 | 24 | 0.019029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6131-2_1_4_line_27 |  | 24 | 25 | 0.027596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6131-2_1_4_line_28 |  | 25 | 29 | 0.013776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6131-2_1_4_line_29 |  | 25 | 30 | 0.035311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6131-2_1_4_line_30 |  | 26 | 27 | 0.042277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6131-2_1_4_line_31 |  | 26 | 28 | 0.13115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6131-2_1_4_line_32 |  | 28 | 33 | 0.022445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6131-2_1_4_line_33 |  | 28 | 34 | 0.064515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6131-2_1_4_line_34 |  | 28 | 31 | 0.073801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6131-2_1_4_line_35 |  | 29 | 37 | 0.10856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6131-2_1_4_line_36 |  | 32 | 35 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6131-2_1_4_line_37 |  | 34 | 36 | 0.072346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6131-2_1_4_line_38 |  | 35 | 44 | 0.011746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6131-2_1_4_line_39 |  | 36 | 45 | 0.032713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6131-2_1_4_line_40 |  | 37 | 38 | 0.031429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6131-2_1_4_line_41 |  | 38 | 39 | 0.076056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6131-2_1_4_line_42 |  | 41 | 42 | 0.009102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6131-2_1_4_line_43 |  | 42 | 43 | 0.12884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6131-2_1_4_line_44 |  | 43 | 44 | 0.12472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6131-2_1_4_trafo_41 | 0.63 MVA 20/0.4 kV | 46 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2572651.6304 | 1103172.0557 | 2572644.5843 | 1103177.5459 | 2572642.3092 | 1103179.1125 | 2572640.8726 | 1103183.0432 | 2572635.6031 | 1103187.9251
1 | 2572647.5724 | 1103165.9932 | 2572651.6304 | 1103172.0557
2 | 2572651.6304 | 1103172.0557 | 2572653.7256 | 1103175.1811 | 2572658.8353 | 1103184.5628
3 | 2572562.3113 | 1103189.5304 | 2572553.3643 | 1103183.951 | 2572543.9006 | 1103180.6831
4 | 2572594.017 | 1103209.3019 | 2572562.3113 | 1103189.5304
5 | 2572543.9006 | 1103180.6831 | 2572515.583 | 1103170.9047 | 2572508.8938 | 1103168.8039
6 | 2572477.9 | 1103159.07 | 2572508.8938 | 1103168.8039
7 | 2572477.9 | 1103159.07 | 2572442.6157 | 1103148.3266
8 | 2572477.9 | 1103159.07 | 2572484.2943 | 1103134.9695
9 | 2572694.4637 | 1103294.9026 | 2572672.8235 | 1103258.4484 | 2572672.13 | 1103255.6279 | 2572672.4911 | 1103253.3695 | 2572673.0267 | 1103252.3258
10 | 2572660.3799 | 1103187.4017 | 2572674.8974 | 1103214.0497 | 2572687.4386 | 1103236.4935 | 2572688.5932 | 1103240.3569 | 2572687.929 | 1103242.3053 | 2572686.396 | 1103243.7463 | 2572675.2839 | 1103249.9552 | 2572673.4574 | 1103251.4864 | 2572673.0267 | 1103252.3258
11 | 2572775.6614 | 1103275.9049 | 2572774.195 | 1103280.1136 | 2572769.3913 | 1103281.9362 | 2572764.3394 | 1103278.4571 | 2572743.9308 | 1103261.118 | 2572716.7748 | 1103277.8044 | 2572694.4637 | 1103294.9026
12 | 2572658.8353 | 1103184.5628 | 2572660.3799 | 1103187.4017
13 | 2572775.6614 | 1103275.9049 | 2572760.3271 | 1103268.748 | 2572745.1286 | 1103255.6765 | 2572755.5329 | 1103241.5911
14 | 2572658.8353 | 1103184.5628 | 2572656.4516 | 1103186.0744 | 2572645.7056 | 1103196.2615 | 2572635.635 | 1103206.3898
15 | 2572765.0669 | 1103228.6841 | 2572755.5329 | 1103241.5911
16 | 2572629.5947 | 1103212.4648 | 2572635.635 | 1103206.3898
17 | 2572724.2944 | 1103164.6017 | 2572722.5483 | 1103161.6637 | 2572706.3599 | 1103136.7462 | 2572693.8244 | 1103119.0159 | 2572691.3527 | 1103116.3191
18 | 2572724.2944 | 1103164.6017 | 2572728.3332 | 1103159.5476 | 2572731.6143 | 1103156.1587
19 | 2572724.2944 | 1103164.6017 | 2572736.5467 | 1103183.0448 | 2572737.375 | 1103184.3976
20 | 2572679.3815 | 1103132.8993 | 2572694.8328 | 1103140.1777 | 2572713.3803 | 1103164.9733 | 2572715.2981 | 1103166.5322 | 2572717.6847 | 1103167.3663 | 2572719.9584 | 1103167.2115 | 2572724.2944 | 1103164.6017
21 | 2572741.0567 | 1103148.6545 | 2572737.3273 | 1103150.2579 | 2572731.6143 | 1103156.1587
22 | 2572741.194 | 1103190.6354 | 2572737.375 | 1103184.3976
23 | 2572705.4659 | 1103183.8075 | 2572679.1746 | 1103140.1928 | 2572679.3815 | 1103132.8993
24 | 2572765.0669 | 1103228.6841 | 2572756.6308 | 1103215.8488 | 2572741.194 | 1103190.6354
25 | 2572707.269 | 1103078.7649 | 2572720.1127 | 1103092.5989
26 | 2572733.8593 | 1103105.7482 | 2572722.2161 | 1103094.8645 | 2572720.1127 | 1103092.5989
27 | 2572752.0263 | 1103126.2351 | 2572747.8478 | 1103119.1614 | 2572737.6377 | 1103109.2801 | 2572733.8593 | 1103105.7482
28 | 2572752.0263 | 1103126.2351 | 2572756.6221 | 1103133.1846 | 2572761.2595 | 1103136.0371
29 | 2572752.0263 | 1103126.2351 | 2572754.8974 | 1103117.8401 | 2572758.0871 | 1103108.0652 | 2572763.1708 | 1103092.7288
30 | 2572515.7753 | 1102969.7236 | 2572485.1333 | 1102948.1407 | 2572480.6169 | 1102946.523
31 | 2572538.9133 | 1103098.8177 | 2572515.7753 | 1102969.7236
32 | 2572538.9133 | 1103098.8177 | 2572540.068 | 1103100.9691 | 2572546.8295 | 1103104.3512 | 2572551.922 | 1103106.507 | 2572554.1186 | 1103109.7987 | 2572553.4046 | 1103112.7035
33 | 2572538.9133 | 1103098.8177 | 2572541.4033 | 1103098.584 | 2572547.3953 | 1103099.4795 | 2572585.2885 | 1103111.5361 | 2572593.7224 | 1103113.5434 | 2572597.7726 | 1103112.7246 | 2572600.9214 | 1103111.054
34 | 2572538.9133 | 1103098.8177 | 2572535.5958 | 1103099.1329 | 2572514.2802 | 1103102.109 | 2572499.5773 | 1103106.3668 | 2572492.8782 | 1103111.611 | 2572488.7612 | 1103118.1331 | 2572484.2943 | 1103134.9695
35 | 2572832.8886 | 1103211.1481 | 2572834.612 | 1103207.2939 | 2572829.5615 | 1103195.5217 | 2572814.8279 | 1103177.4676 | 2572795.3284 | 1103157.6229 | 2572783.6697 | 1103148.9931 | 2572780.3427 | 1103147.1738 | 2572771.6567 | 1103142.4327 | 2572761.2595 | 1103136.0371
36 | 2572442.6157 | 1103148.3266 | 2572421.99 | 1103142.0464
37 | 2572647.5724 | 1103165.9932 | 2572631.8544 | 1103142.5189 | 2572618.9961 | 1103130.4154 | 2572612.6562 | 1103124.441 | 2572605.4231 | 1103115.9917 | 2572600.9214 | 1103111.054
38 | 2572410.7532 | 1103138.625 | 2572421.99 | 1103142.0464
39 | 2572623.2817 | 1103147.4491 | 2572637.2481 | 1103161.6487 | 2572642.3536 | 1103166.6949 | 2572645.5746 | 1103167.3029 | 2572647.5724 | 1103165.9932
40 | 2572807.7062 | 1103193.6967 | 2572819.8517 | 1103202.2132 | 2572828.6794 | 1103210.978 | 2572832.8886 | 1103211.1481
41 | 2572765.0669 | 1103228.6841 | 2572774.2352 | 1103242.6499 | 2572784.8106 | 1103227.1723 | 2572795.0247 | 1103210.4956 | 2572807.7062 | 1103193.6967
42 | 2572410.2173 | 1103088.2754 | 2572419.3187 | 1103088.3796
43 | 2572291.9251 | 1103101.1112 | 2572290.8278 | 1103096.3249 | 2572291.1289 | 1103092.7995 | 2572292.9313 | 1103091.0682 | 2572296.9284 | 1103090.5052 | 2572300.9839 | 1103090.8646 | 2572319.3734 | 1103089.2018 | 2572334.7218 | 1103085.6965 | 2572341.7379 | 1103085.531 | 2572361.1495 | 1103085.7536 | 2572390.7608 | 1103086.6855 | 2572410.2173 | 1103088.2754
44 | 2572291.9251 | 1103101.1112 | 2572298.0437 | 1103104.296 | 2572360.9194 | 1103123.4516 | 2572410.7532 | 1103138.625

## bus_geodata
| x | y | coords
0 | 2572635.6031 | 1103187.9251
1 | 2572651.6304 | 1103172.0557
2 | 2572562.3113 | 1103189.5304
3 | 2572543.9006 | 1103180.6831
4 | 2572594.017 | 1103209.3019
5 | 2572508.8938 | 1103168.8039
6 | 2572477.9 | 1103159.07
7 | 2572673.0267 | 1103252.3258
8 | 2572694.4637 | 1103294.9026
9 | 2572660.3799 | 1103187.4017
10 | 2572775.6614 | 1103275.9049
11 | 2572658.8353 | 1103184.5628
12 | 2572755.5329 | 1103241.5911
13 | 2572635.635 | 1103206.3898
14 | 2572691.3527 | 1103116.3191
15 | 2572724.2945 | 1103164.6017
16 | 2572731.6143 | 1103156.1587
17 | 2572737.375 | 1103184.3976
18 | 2572679.3815 | 1103132.8993
19 | 2572741.0567 | 1103148.6545
20 | 2572741.194 | 1103190.6354
21 | 2572705.4659 | 1103183.8075
22 | 2572707.269 | 1103078.7649
23 | 2572720.1127 | 1103092.5989
24 | 2572733.8593 | 1103105.7482
25 | 2572752.0263 | 1103126.2351
26 | 2572515.7753 | 1102969.7236
27 | 2572480.6169 | 1102946.523
28 | 2572538.9133 | 1103098.8177
29 | 2572761.2595 | 1103136.0371
30 | 2572763.1708 | 1103092.7288
31 | 2572484.2943 | 1103134.9695
32 | 2572442.6157 | 1103148.3266
33 | 2572553.4046 | 1103112.7035
34 | 2572600.9214 | 1103111.054
35 | 2572421.99 | 1103142.0464
36 | 2572647.5724 | 1103165.9932
37 | 2572832.8886 | 1103211.1481
38 | 2572807.7062 | 1103193.6967
39 | 2572765.0669 | 1103228.6841
40 | 2572629.5947 | 1103212.4648
41 | 2572419.3187 | 1103088.3796
42 | 2572410.2173 | 1103088.2754
43 | 2572291.9251 | 1103101.1112
44 | 2572410.7532 | 1103138.625
45 | 2572623.2817 | 1103147.4491
46 | 2572647.5724 | 1103165.9932

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1