## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6133-32_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6133-32_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6133-32_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6133-32_0_3_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_6133-32_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6133-32_0_3_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_6133-32_0_3_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_6133-32_0_3_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_6133-32_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_6133-32_0_3_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_6133-32_0_3_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_6133-32_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_6133-32_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6133-32_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_6133-32_0_3_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_6133-32_0_3_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_6133-32_0_3_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_6133-32_0_3_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_6133-32_0_3_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_6133-32_0_3_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_6133-32_0_3_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_6133-32_0_3_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_6133-32_0_3_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_6133-32_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_6133-32_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_6133-32_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_6133-32_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6133-32_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_6133-32_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6133-32_0_3_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_6133-32_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_6133-32_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6133-32_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_6133-32_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_6133-32_0_3_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_6133-32_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_6133-32_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_6133-32_0_3_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6133-32_0_3_node_54 | 0.4 | n |  | TRUE
39 | bus_LV_6133-32_0_3_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_6133-32_0_3_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_6133-32_0_3_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_6133-32_0_3_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_6133-32_0_3_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_6133-32_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_6133-32_0_3_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_6133-32_0_3_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_6133-32_0_3_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_6133-32_0_3_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_6133-32_0_3_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_6133-32_0_3_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_6133-32_0_3_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_6133-32_0_3_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_6133-32_0_3_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_6133-32_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_6133-32_0_3_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_6133-32_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_MV_102_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6133-32_0_3_load_0 | 0 | 0.0056285 | 0.0014106 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6133-32_0_3_load_1 | 1 | 0.0078361 | 0.0019639 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6133-32_0_3_load_2 | 2 | 0.0033368 | 0.00083628 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6133-32_0_3_load_23 | 5 | 0.010391 | 0.0026042 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6133-32_0_3_load_24 | 6 | 0.0098887 | 0.0024784 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6133-32_0_3_load_58 | 9 | 0.0067199 | 0.0016842 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6133-32_0_3_load_4 | 10 | 0.025909 | 0.0064934 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6133-32_0_3_load_6 | 12 | 0.0016779 | 0.00042051 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6133-32_0_3_load_7 | 13 | 0.00229 | 0.00057394 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6133-32_0_3_load_52 | 15 | 0.0066816 | 0.0016746 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6133-32_0_3_load_45 | 17 | 0.0085846 | 0.0021515 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6133-32_0_3_load_38 | 18 | 0.0028749 | 0.00072052 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6133-32_0_3_load_36 | 19 | 0.0042144 | 0.0010562 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6133-32_0_3_load_8 | 21 | 0.0030292 | 0.0007592 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6133-32_0_3_load_9 | 22 | 0.0057534 | 0.0014419 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6133-32_0_3_load_11 | 24 | 0.0053154 | 0.0013322 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6133-32_0_3_load_14 | 26 | 0.013107 | 0.0032849 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6133-32_0_3_load_18 | 27 | 0.0046994 | 0.0011778 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6133-32_0_3_load_16 | 28 | 0.0051757 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6133-32_0_3_load_15 | 29 | 0.0041444 | 0.0010387 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6133-32_0_3_load_20 | 30 | 0.0083562 | 0.0020943 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6133-32_0_3_load_19 | 31 | 0.015154 | 0.003798 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6133-32_0_3_load_21 | 32 | 0.0065238 | 0.001635 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6133-32_0_3_load_51 | 34 | 0.01079 | 0.0027042 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6133-32_0_3_load_31 | 36 | 0.011884 | 0.0029784 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6133-32_0_3_load_27 | 37 | 0.0027207 | 0.00068187 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6133-32_0_3_load_54 | 38 | 0.0054134 | 0.0013567 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6133-32_0_3_load_48 | 39 | 0.017933 | 0.0044945 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6133-32_0_3_load_28 | 40 | 0.0039139 | 0.00098091 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6133-32_0_3_load_30 | 41 | 0.002292 | 0.00057442 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6133-32_0_3_load_56 | 42 | 0.0033534 | 0.00084044 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6133-32_0_3_load_55 | 43 | 0.0068301 | 0.0017118 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6133-32_0_3_load_32 | 44 | 0.0079141 | 0.0019835 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6133-32_0_3_load_33 | 45 | 0.0036476 | 0.00091418 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6133-32_0_3_load_35 | 46 | 0.012026 | 0.0030141 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6133-32_0_3_load_47 | 47 | 0.0045437 | 0.0011387 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6133-32_0_3_load_49 | 48 | 0.0020362 | 0.00051032 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6133-32_0_3_load_39 | 49 | 0.0024879 | 0.00062353 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6133-32_0_3_load_57 | 52 | 0.0030964 | 0.00077603 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6133-32_0_3_load_50 | 53 | 0.019 | 0.0047618 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6133-32_0_3_load_42 | 54 | 0.0041099 | 0.00103 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6133-32_0_3_load_44 | 56 | 0.0029288 | 0.00073403 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6133-32_0_3_line_0 |  | 0 | 1 | 0.029434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_6133-32_0_3_line_1 |  | 0 | 2 | 0.041834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6133-32_0_3_line_2 |  | 0 | 3 | 0.019081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_6133-32_0_3_line_3 |  | 2 | 4 | 0.041553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6133-32_0_3_line_4 |  | 3 | 7 | 0.062147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_6133-32_0_3_line_5 |  | 3 | 6 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6133-32_0_3_line_6 |  | 4 | 8 | 0.047799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6133-32_0_3_line_7 |  | 5 | 6 | 0.0022519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6133-32_0_3_line_8 |  | 7 | 14 | 0.046407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_6133-32_0_3_line_9 |  | 7 | 15 | 0.015649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6133-32_0_3_line_10 |  | 7 | 10 | 0.033151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6133-32_0_3_line_11 |  | 8 | 9 | 0.040403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6133-32_0_3_line_12 |  | 11 | 12 | 0.001829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6133-32_0_3_line_13 |  | 11 | 13 | 0.0021107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6133-32_0_3_line_14 |  | 12 | 16 | 0.032694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6133-32_0_3_line_15 |  | 13 | 17 | 0.024275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6133-32_0_3_line_16 |  | 14 | 38 | 0.044247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_6133-32_0_3_line_17 |  | 14 | 39 | 0.033422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6133-32_0_3_line_18 |  | 16 | 18 | 0.017061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6133-32_0_3_line_19 |  | 16 | 19 | 0.036238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6133-32_0_3_line_20 |  | 17 | 20 | 0.0080053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6133-32_0_3_line_21 |  | 18 | 47 | 0.032741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6133-32_0_3_line_22 |  | 19 | 46 | 0.05092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6133-32_0_3_line_23 |  | 20 | 39 | 0.050651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6133-32_0_3_line_24 |  | 21 | 22 | 0.024294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6133-32_0_3_line_25 |  | 21 | 23 | 0.023123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6133-32_0_3_line_26 |  | 22 | 24 | 0.017772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6133-32_0_3_line_27 |  | 23 | 25 | 0.076206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6133-32_0_3_line_28 |  | 24 | 26 | 0.016052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6133-32_0_3_line_29 |  | 25 | 27 | 0.017671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6133-32_0_3_line_30 |  | 25 | 28 | 0.01193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6133-32_0_3_line_31 |  | 26 | 29 | 0.025294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6133-32_0_3_line_32 |  | 29 | 30 | 0.010182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6133-32_0_3_line_33 |  | 30 | 31 | 0.0035135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6133-32_0_3_line_34 |  | 31 | 32 | 0.024869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6133-32_0_3_line_35 |  | 32 | 33 | 0.012707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6133-32_0_3_line_36 |  | 33 | 34 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6133-32_0_3_line_37 |  | 33 | 35 | 0.035354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6133-32_0_3_line_38 |  | 35 | 36 | 0.010591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6133-32_0_3_line_39 |  | 35 | 37 | 0.013421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6133-32_0_3_line_40 |  | 36 | 42 | 0.037143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6133-32_0_3_line_41 |  | 37 | 40 | 0.0027891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6133-32_0_3_line_42 |  | 38 | 43 | 0.024589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_6133-32_0_3_line_43 |  | 40 | 41 | 0.0063051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6133-32_0_3_line_44 |  | 42 | 43 | 0.0018813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_6133-32_0_3_line_45 |  | 44 | 45 | 0.00031947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6133-32_0_3_line_46 |  | 45 | 46 | 0.02334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6133-32_0_3_line_47 |  | 47 | 48 | 0.022864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6133-32_0_3_line_48 |  | 48 | 53 | 0.020417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6133-32_0_3_line_49 |  | 48 | 56 | 0.0247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6133-32_0_3_line_50 |  | 49 | 50 | 0.018629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6133-32_0_3_line_51 |  | 50 | 51 | 0.021826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6133-32_0_3_line_52 |  | 51 | 52 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6133-32_0_3_line_53 |  | 51 | 53 | 0.020939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6133-32_0_3_line_54 |  | 54 | 55 | 0.022823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6133-32_0_3_line_55 |  | 55 | 56 | 0.0073966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6133-32_0_3_trafo_1 | 0.63 MVA 20/0.4 kV | 57 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2573657.3419 | 1108750.1139 | 2573673.8604 | 1108753.1376 | 2573686.3171 | 1108755.2898
1 | 2573657.3419 | 1108750.1139 | 2573616.1916 | 1108742.5813
2 | 2573657.3419 | 1108750.1139 | 2573661.9015 | 1108768.642
3 | 2573575.3805 | 1108734.7691 | 2573599.8334 | 1108739.5869 | 2573616.1916 | 1108742.5813
4 | 2573723.2413 | 1108779.6806 | 2573683.9774 | 1108772.5589 | 2573661.9015 | 1108768.642
5 | 2573661.9015 | 1108768.642 | 2573657.2717 | 1108789.0566
6 | 2573575.3805 | 1108734.7691 | 2573573.6482 | 1108734.5321 | 2573572.2838 | 1108738.918 | 2573569.2808 | 1108748.5916 | 2573568.191 | 1108752.1204 | 2573558.914 | 1108778.1518
7 | 2573656.7737 | 1108791.2527 | 2573657.2717 | 1108789.0566
8 | 2573723.2413 | 1108779.6806 | 2573747.5784 | 1108784.5996 | 2573758.4724 | 1108787.2314 | 2573768.5104 | 1108790.3116
9 | 2573723.2413 | 1108779.6806 | 2573721.2631 | 1108795.2037
10 | 2573736.5442 | 1108749.3156 | 2573723.2413 | 1108779.6806
11 | 2573580.7661 | 1108799.8117 | 2573583.609 | 1108785.3364 | 2573558.914 | 1108778.1518
12 | 2573772.3274 | 1108718.8145 | 2573770.6037 | 1108718.203
13 | 2573772.3274 | 1108718.8145 | 2573774.3167 | 1108719.5203
14 | 2573739.7915 | 1108707.2722 | 2573770.6037 | 1108718.203
15 | 2573774.3167 | 1108719.5203 | 2573797.1947 | 1108727.6366
16 | 2573768.5104 | 1108790.3116 | 2573764.9651 | 1108801.5327 | 2573758.1368 | 1108802.5072 | 2573743.9703 | 1108804.4808 | 2573743.1647 | 1108815.7307
17 | 2573778.2921 | 1108758.3526 | 2573768.5104 | 1108790.3116
18 | 2573739.7915 | 1108707.2722 | 2573745.7299 | 1108691.2783
19 | 2573739.7915 | 1108707.2722 | 2573705.6615 | 1108695.0934
20 | 2573804.7393 | 1108730.3132 | 2573797.1947 | 1108727.6366
21 | 2573757.1263 | 1108660.5845 | 2573745.7299 | 1108691.2783
22 | 2573657.703 | 1108677.9802 | 2573705.6615 | 1108695.0934
23 | 2573804.7393 | 1108730.3132 | 2573792.2857 | 1108763.7284 | 2573778.2921 | 1108758.3526
24 | 2573564.199 | 1108845.1506 | 2573560.4846 | 1108845.6457 | 2573540.1119 | 1108848.314
25 | 2573517.3334 | 1108847.3799 | 2573521.4594 | 1108848.8514 | 2573525.0637 | 1108849.4248 | 2573538.2687 | 1108848.5555 | 2573540.1119 | 1108848.314
26 | 2573564.199 | 1108845.1506 | 2573581.1786 | 1108842.8872 | 2573581.8187 | 1108842.8402
27 | 2573517.3334 | 1108847.3799 | 2573511.4167 | 1108849.996 | 2573500.8789 | 1108856.3232 | 2573492.4534 | 1108861.396 | 2573479.4192 | 1108871.2581 | 2573482.3539 | 1108874.2579 | 2573492.1234 | 1108879.551 | 2573503.8724 | 1108890.3494
28 | 2573581.8187 | 1108842.8402 | 2573591.169 | 1108842.1543 | 2573597.82 | 1108842.7411
29 | 2573503.8724 | 1108890.3494 | 2573506.728 | 1108889.4142 | 2573510.6462 | 1108889.3192 | 2573521.3493 | 1108890.7397
30 | 2573503.8724 | 1108890.3494 | 2573512.2566 | 1108898.8364
31 | 2573622.5625 | 1108847.7794 | 2573616.653 | 1108846.0227 | 2573600.7722 | 1108843.0016 | 2573597.82 | 1108842.7411
32 | 2573632.3227 | 1108850.6809 | 2573622.5625 | 1108847.7794
33 | 2573632.3227 | 1108850.6809 | 2573635.6905 | 1108851.6821
34 | 2573659.6635 | 1108858.2959 | 2573637.8812 | 1108852.3333 | 2573635.6905 | 1108851.6821
35 | 2573671.9369 | 1108861.5785 | 2573670.9003 | 1108861.3718 | 2573659.6635 | 1108858.2959
36 | 2573668.0738 | 1108877.859 | 2573671.9369 | 1108861.5785
37 | 2573706.4946 | 1108869.0096 | 2573705.3882 | 1108868.7365 | 2573698.0067 | 1108866.901 | 2573692.1507 | 1108865.7037 | 2573671.9369 | 1108861.5785
38 | 2573706.4946 | 1108869.0096 | 2573707.9407 | 1108858.5202
39 | 2573706.4946 | 1108869.0096 | 2573714.5462 | 1108872.0984 | 2573718.8976 | 1108874.117
40 | 2573707.9407 | 1108858.5202 | 2573741.2742 | 1108842.1338
41 | 2573718.8976 | 1108874.117 | 2573721.4277 | 1108875.2908
42 | 2573743.1647 | 1108815.7307 | 2573741.4085 | 1108840.2573
43 | 2573727.1273 | 1108877.9862 | 2573724.7071 | 1108876.8121 | 2573721.4277 | 1108875.2908
44 | 2573741.2742 | 1108842.1338 | 2573741.4085 | 1108840.2573
45 | 2573635.4197 | 1108670.0288 | 2573635.7206 | 1108670.1361
46 | 2573657.703 | 1108677.9802 | 2573635.7206 | 1108670.1361
47 | 2573757.1263 | 1108660.5845 | 2573773.1587 | 1108644.2838
48 | 2573773.1587 | 1108644.2838 | 2573754.1937 | 1108636.7214
49 | 2573773.1587 | 1108644.2838 | 2573796.102 | 1108653.4326
50 | 2573714.4195 | 1108620.8611 | 2573707.8083 | 1108638.2775
51 | 2573714.4195 | 1108620.8611 | 2573734.7441 | 1108628.9657
52 | 2573726.805 | 1108651.8229 | 2573734.7441 | 1108628.9657
53 | 2573734.7441 | 1108628.9657 | 2573754.1937 | 1108636.7214
54 | 2573802.9725 | 1108656.1723 | 2573795.0896 | 1108677.591
55 | 2573802.9725 | 1108656.1723 | 2573796.102 | 1108653.4326

## bus_geodata
| x | y | coords
0 | 2573657.3419 | 1108750.1139
1 | 2573686.3171 | 1108755.2898
2 | 2573616.1916 | 1108742.5813
3 | 2573661.9015 | 1108768.642
4 | 2573575.3805 | 1108734.7691
5 | 2573656.7737 | 1108791.2527
6 | 2573657.2717 | 1108789.0566
7 | 2573723.2413 | 1108779.6806
8 | 2573558.914 | 1108778.1518
9 | 2573580.7661 | 1108799.8117
10 | 2573736.5442 | 1108749.3156
11 | 2573772.3274 | 1108718.8145
12 | 2573770.6037 | 1108718.203
13 | 2573774.3167 | 1108719.5203
14 | 2573768.5104 | 1108790.3116
15 | 2573721.2631 | 1108795.2037
16 | 2573739.7915 | 1108707.2722
17 | 2573797.1947 | 1108727.6366
18 | 2573745.7299 | 1108691.2783
19 | 2573705.6615 | 1108695.0934
20 | 2573804.7393 | 1108730.3132
21 | 2573540.1119 | 1108848.314
22 | 2573564.199 | 1108845.1506
23 | 2573517.3334 | 1108847.3799
24 | 2573581.8187 | 1108842.8402
25 | 2573503.8724 | 1108890.3494
26 | 2573597.82 | 1108842.7411
27 | 2573521.3493 | 1108890.7397
28 | 2573512.2566 | 1108898.8364
29 | 2573622.5625 | 1108847.7794
30 | 2573632.3227 | 1108850.6809
31 | 2573635.6905 | 1108851.6821
32 | 2573659.6635 | 1108858.2959
33 | 2573671.9369 | 1108861.5785
34 | 2573668.0738 | 1108877.859
35 | 2573706.4946 | 1108869.0096
36 | 2573707.9407 | 1108858.5202
37 | 2573718.8976 | 1108874.117
38 | 2573743.1647 | 1108815.7307
39 | 2573778.2921 | 1108758.3526
40 | 2573721.4277 | 1108875.2908
41 | 2573727.1273 | 1108877.9862
42 | 2573741.2742 | 1108842.1338
43 | 2573741.4085 | 1108840.2573
44 | 2573635.4197 | 1108670.0288
45 | 2573635.7206 | 1108670.1361
46 | 2573657.703 | 1108677.9802
47 | 2573757.1263 | 1108660.5845
48 | 2573773.1587 | 1108644.2838
49 | 2573707.8083 | 1108638.2775
50 | 2573714.4195 | 1108620.8611
51 | 2573734.7441 | 1108628.9657
52 | 2573726.805 | 1108651.8229
53 | 2573754.1937 | 1108636.7214
54 | 2573795.0896 | 1108677.591
55 | 2573802.9725 | 1108656.1723
56 | 2573796.102 | 1108653.4326
57 | 2573792.685 | 1108779.1567

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1