## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6141-13_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6141-13_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6141-13_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6141-13_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6141-13_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6141-13_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6141-13_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6141-13_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_6141-13_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_6141-13_0_2_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_6141-13_0_2_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_6141-13_0_2_node_83 | 0.4 | n |  | TRUE
12 | bus_LV_6141-13_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_6141-13_0_2_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_6141-13_0_2_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_6141-13_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_6141-13_0_2_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_6141-13_0_2_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_6141-13_0_2_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_6141-13_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_6141-13_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_6141-13_0_2_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_6141-13_0_2_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_6141-13_0_2_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_6141-13_0_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_6141-13_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_6141-13_0_2_node_154 | 0.4 | n |  | TRUE
27 | bus_LV_6141-13_0_2_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_6141-13_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_6141-13_0_2_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_6141-13_0_2_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_6141-13_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_6141-13_0_2_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_6141-13_0_2_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_6141-13_0_2_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_6141-13_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_6141-13_0_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_6141-13_0_2_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_6141-13_0_2_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_6141-13_0_2_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_6141-13_0_2_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_6141-13_0_2_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_6141-13_0_2_node_42 | 0.4 | n |  | TRUE
43 | bus_MV_102_0_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6141-13_0_2_load_0 | 0 | 0.0035786 | 0.00089687 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6141-13_0_2_load_3 | 3 | 0.0042308 | 0.0010603 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6141-13_0_2_load_6 | 6 | 0.0060341 | 0.0015123 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6141-13_0_2_load_8 | 8 | 0.0021645 | 0.00054247 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6141-13_0_2_load_9 | 9 | 0.0024528 | 0.00061474 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6141-13_0_2_load_13 | 10 | 0.0018232 | 0.00045695 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6141-13_0_2_load_83 | 11 | 0.0012807 | 0.00032098 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6141-13_0_2_load_10 | 12 | 0.0019978 | 0.00050069 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6141-13_0_2_load_14 | 13 | 0.0018702 | 0.00046872 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6141-13_0_2_load_11 | 14 | 0.0024339 | 0.00061 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6141-13_0_2_load_12 | 15 | 0.0035858 | 0.0008987 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6141-13_0_2_load_38 | 16 | 0.0054994 | 0.0013783 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6141-13_0_2_load_15 | 17 | 0.001364 | 0.00034185 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6141-13_0_2_load_16 | 18 | 0.0037963 | 0.00095145 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6141-13_0_2_load_17 | 19 | 0.0045417 | 0.0011383 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6141-13_0_2_load_20 | 21 | 0.0020675 | 0.00051816 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6141-13_0_2_load_19 | 22 | 0.0019299 | 0.00048369 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6141-13_0_2_load_21 | 23 | 0.0021424 | 0.00053694 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6141-13_0_2_load_24 | 25 | 0.0024205 | 0.00060663 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6141-13_0_2_load_154 | 26 | 0.0031802 | 0.00079703 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6141-13_0_2_load_25 | 27 | 0.0049252 | 0.0012344 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6141-13_0_2_load_26 | 28 | 0.001726 | 0.00043258 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6141-13_0_2_load_27 | 29 | 0.0037051 | 0.0009286 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6141-13_0_2_load_28 | 30 | 0.0031768 | 0.00079617 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6141-13_0_2_load_30 | 31 | 0.0027768 | 0.00069593 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6141-13_0_2_load_31 | 32 | 0.0021193 | 0.00053115 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6141-13_0_2_load_32 | 33 | 0.0019444 | 0.0004873 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6141-13_0_2_load_34 | 35 | 0.0043322 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6141-13_0_2_load_35 | 36 | 0.003578 | 0.00089672 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6141-13_0_2_load_36 | 37 | 0.0051488 | 0.0012904 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6141-13_0_2_load_39 | 39 | 0.0023321 | 0.00058448 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6141-13_0_2_load_40 | 40 | 0.0030433 | 0.00076272 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6141-13_0_2_load_41 | 41 | 0.0027432 | 0.00068752 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6141-13_0_2_load_42 | 42 | 0.0036404 | 0.00091236 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6141-13_0_2_line_0 |  | 0 | 1 | 0.0061267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6141-13_0_2_line_1 |  | 1 | 2 | 0.068129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6141-13_0_2_line_2 |  | 2 | 3 | 0.13395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6141-13_0_2_line_3 |  | 3 | 4 | 0.015609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6141-13_0_2_line_4 |  | 4 | 5 | 0.018145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6141-13_0_2_line_5 |  | 4 | 6 | 0.05235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6141-13_0_2_line_6 |  | 5 | 7 | 0.13358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6141-13_0_2_line_7 |  | 5 | 8 | 0.05119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6141-13_0_2_line_8 |  | 6 | 9 | 0.012639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6141-13_0_2_line_9 |  | 7 | 10 | 0.097842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6141-13_0_2_line_10 |  | 7 | 11 | 0.22935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6141-13_0_2_line_11 |  | 8 | 12 | 0.0012524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6141-13_0_2_line_12 |  | 9 | 13 | 0.018228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6141-13_0_2_line_13 |  | 10 | 16 | 0.011238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6141-13_0_2_line_14 |  | 12 | 14 | 0.02643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6141-13_0_2_line_15 |  | 13 | 17 | 0.032104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6141-13_0_2_line_16 |  | 14 | 15 | 0.02383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6141-13_0_2_line_17 |  | 16 | 38 | 0.034403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6141-13_0_2_line_18 |  | 17 | 18 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6141-13_0_2_line_19 |  | 19 | 20 | 0.072177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6141-13_0_2_line_20 |  | 19 | 21 | 0.10171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6141-13_0_2_line_21 |  | 20 | 22 | 0.11022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6141-13_0_2_line_22 |  | 21 | 23 | 0.067664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6141-13_0_2_line_23 |  | 23 | 24 | 0.0078738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6141-13_0_2_line_24 |  | 24 | 25 | 0.020202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6141-13_0_2_line_25 |  | 25 | 26 | 0.079245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6141-13_0_2_line_26 |  | 26 | 33 | 0.094919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6141-13_0_2_line_27 |  | 27 | 28 | 0.019792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6141-13_0_2_line_28 |  | 27 | 29 | 0.011633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6141-13_0_2_line_29 |  | 28 | 30 | 0.010034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6141-13_0_2_line_30 |  | 30 | 31 | 0.019938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6141-13_0_2_line_31 |  | 31 | 32 | 0.028511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6141-13_0_2_line_32 |  | 32 | 33 | 0.039693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6141-13_0_2_line_33 |  | 33 | 34 | 0.072336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6141-13_0_2_line_34 |  | 34 | 35 | 0.015919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6141-13_0_2_line_35 |  | 34 | 36 | 0.069189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6141-13_0_2_line_36 |  | 35 | 37 | 0.04091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6141-13_0_2_line_37 |  | 37 | 38 | 0.038031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6141-13_0_2_line_38 |  | 38 | 39 | 0.040342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6141-13_0_2_line_39 |  | 39 | 40 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6141-13_0_2_line_40 |  | 40 | 41 | 0.080382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6141-13_0_2_line_41 |  | 41 | 42 | 0.016792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6141-13_0_2_trafo_39 | 0.63 MVA 20/0.4 kV | 43 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2578958.9128 | 1108872.9656 | 2578957.4831 | 1108875.2273 | 2578954.9775 | 1108877.6004
1 | 2579016.4944 | 1108886.6388 | 2579003.3037 | 1108889.5973 | 2579000.1909 | 1108890.1417 | 2578975.2356 | 1108890.5176 | 2578972.0002 | 1108889.1726 | 2578970.91 | 1108886.8196 | 2578970.644 | 1108881.4846 | 2578964.4048 | 1108874.236 | 2578961.582 | 1108873.7456 | 2578958.9128 | 1108872.9656
2 | 2579016.4944 | 1108886.6388 | 2579029.5625 | 1108895.1199 | 2579061.0366 | 1108911.2966 | 2579077.6477 | 1108920.7216 | 2579109.9006 | 1108934.2279 | 2579124.2315 | 1108943.6497 | 2579132.1912 | 1108952.3154
3 | 2579141.4243 | 1108964.901 | 2579132.1912 | 1108952.3154
4 | 2579141.4243 | 1108964.901 | 2579157.5524 | 1108973.3051
5 | 2579141.4243 | 1108964.901 | 2579125.4727 | 1108967.3351 | 2579117.3029 | 1108967.2077 | 2579104.4882 | 1108964.8619 | 2579101.2659 | 1108965.0287 | 2579097.5826 | 1108966.0197 | 2579091.5207 | 1108971.2013
6 | 2579157.5524 | 1108973.3051 | 2579176.7617 | 1108985.456 | 2579196.2814 | 1108995.7272 | 2579217.3497 | 1109002.3914 | 2579259.1833 | 1109015.243 | 2579279.5561 | 1109026.4564
7 | 2579157.5524 | 1108973.3051 | 2579139.2952 | 1108992.9335 | 2579120.7829 | 1109008.803
8 | 2579081.7792 | 1108979.253 | 2579089.16 | 1108973.2191 | 2579091.5207 | 1108971.2013
9 | 2579279.5561 | 1109026.4564 | 2579242.7391 | 1109018.2565 | 2579221.0402 | 1109019.2427 | 2579211.9001 | 1109024.5879 | 2579205.4957 | 1109032.1137 | 2579196.133 | 1109047.4071
10 | 2579464.8405 | 1108891.2878 | 2579279.5561 | 1109026.4564
11 | 2579120.7829 | 1109008.803 | 2579119.832 | 1109009.6181
12 | 2579081.7792 | 1108979.253 | 2579080.8981 | 1108979.9733 | 2579067.2057 | 1108990.1996
13 | 2579196.133 | 1109047.4071 | 2579190.2652 | 1109056.9918
14 | 2579119.832 | 1109009.6181 | 2579114.9599 | 1109013.7947 | 2579108.0882 | 1109022.4783 | 2579104.1075 | 1109030.4823
15 | 2579067.2057 | 1108990.1996 | 2579058.7661 | 1108996.5027 | 2579041.6806 | 1109008.4569 | 2579041.0497 | 1109008.7998
16 | 2579104.1075 | 1109030.4823 | 2579101.4644 | 1109035.7968 | 2579094.721 | 1109048.0374 | 2579093.5469 | 1109051.7767
17 | 2579172.3024 | 1109086.333 | 2579190.2652 | 1109056.9918
18 | 2579024.4741 | 1109007.7718 | 2579028.729 | 1109011.1698 | 2579033.9202 | 1109012.6748 | 2579041.0497 | 1109008.7998
19 | 2578988.9762 | 1109427.6387 | 2578990.9298 | 1109424.9306 | 2579003.2962 | 1109420.8522 | 2579033.1509 | 1109414.3453 | 2579052.7885 | 1109412.1427 | 2579057.9967 | 1109413.9095
20 | 2579095.7001 | 1109319.4443 | 2579057.9967 | 1109413.9095
21 | 2578988.9762 | 1109427.6387 | 2578984.1086 | 1109423.5091 | 2578981.8519 | 1109421.2714 | 2578971.4101 | 1109416.5832 | 2578913.3487 | 1109403.5346 | 2578884.4983 | 1109396.4656
22 | 2579095.7001 | 1109319.4443 | 2579099.971 | 1109321.0781 | 2579129.6997 | 1109345.0318 | 2579152.9499 | 1109353.9813
23 | 2579160.2982 | 1109356.8098 | 2579152.9499 | 1109353.9813
24 | 2579160.2982 | 1109356.8098 | 2579180.4849 | 1109356.0164
25 | 2579180.4849 | 1109356.0164 | 2579213.7209 | 1109284.0782
26 | 2579219.8094 | 1109189.3543 | 2579213.7209 | 1109284.0782
27 | 2579313.1465 | 1109127.5922 | 2579304.4938 | 1109127.0991 | 2579293.4117 | 1109128.0782
28 | 2579313.1465 | 1109127.5922 | 2579324.7602 | 1109128.2541
29 | 2579293.4117 | 1109128.0782 | 2579283.4166 | 1109128.9612
30 | 2579267.2935 | 1109140.6908 | 2579283.4166 | 1109128.9612 | 2579283.4166 | 1109128.9612
31 | 2579267.2935 | 1109140.6908 | 2579263.5805 | 1109143.392 | 2579246.0503 | 1109159.6659
32 | 2579246.0503 | 1109159.6659 | 2579238.3037 | 1109166.8572 | 2579219.8094 | 1109189.3543
33 | 2579153.0937 | 1109177.2337 | 2579161.0928 | 1109183.9761 | 2579184.0927 | 1109190.6557 | 2579194.3452 | 1109194.1888 | 2579205.3025 | 1109195.9298 | 2579213.0292 | 1109193.1684 | 2579219.8094 | 1109189.3543
34 | 2579153.0937 | 1109177.2337 | 2579150.7899 | 1109165.8581 | 2579151.5958 | 1109161.6218
35 | 2579153.0937 | 1109177.2337 | 2579137.4819 | 1109183.902 | 2579110.4955 | 1109179.9155 | 2579086.4808 | 1109173.2108
36 | 2579159.2408 | 1109121.4327 | 2579151.5958 | 1109161.6218
37 | 2579172.3024 | 1109086.333 | 2579169.4511 | 1109090.9896 | 2579162.9277 | 1109102.051 | 2579159.2408 | 1109121.4327
38 | 2579172.3024 | 1109086.333 | 2579164.1194 | 1109086.8059 | 2579151.8627 | 1109096.0417 | 2579138.5536 | 1109106.291
39 | 2579128.0965 | 1109116.2696 | 2579137.2173 | 1109107.3201 | 2579138.5536 | 1109106.291
40 | 2579128.0965 | 1109116.2696 | 2579122.2436 | 1109122.0126 | 2579113.0635 | 1109133.6168 | 2579109.7218 | 1109141.6879 | 2579100.8294 | 1109149.3114 | 2579093.3362 | 1109154.7845 | 2579089.2365 | 1109153.776 | 2579088.8788 | 1109148.6746 | 2579090.9139 | 1109144.9213 | 2579093.9574 | 1109137.7627 | 2579092.5759 | 1109131.6422 | 2579092.5759 | 1109131.6422
41 | 2579092.5759 | 1109131.6422 | 2579080.4844 | 1109119.9906

## bus_geodata
| x | y | coords
0 | 2578954.9775 | 1108877.6004
1 | 2578958.9128 | 1108872.9656
2 | 2579016.4944 | 1108886.6388
3 | 2579132.1912 | 1108952.3154
4 | 2579141.4243 | 1108964.901
5 | 2579157.5524 | 1108973.3051
6 | 2579091.5207 | 1108971.2013
7 | 2579279.5561 | 1109026.4564
8 | 2579120.7829 | 1109008.803
9 | 2579081.7792 | 1108979.253
10 | 2579196.133 | 1109047.4071
11 | 2579464.8404 | 1108891.2878
12 | 2579119.832 | 1109009.6181
13 | 2579067.2057 | 1108990.1996
14 | 2579104.1075 | 1109030.4823
15 | 2579093.5469 | 1109051.7767
16 | 2579190.2652 | 1109056.9918
17 | 2579041.0497 | 1109008.7998
18 | 2579024.4741 | 1109007.7718
19 | 2579057.9967 | 1109413.9095
20 | 2578988.9762 | 1109427.6387
21 | 2579095.7001 | 1109319.4443
22 | 2578884.4983 | 1109396.4656
23 | 2579152.9499 | 1109353.9813
24 | 2579160.2982 | 1109356.8098
25 | 2579180.4849 | 1109356.0164
26 | 2579213.7209 | 1109284.0782
27 | 2579313.1465 | 1109127.5922
28 | 2579293.4117 | 1109128.0782
29 | 2579324.7602 | 1109128.2541
30 | 2579283.4166 | 1109128.9612
31 | 2579267.2935 | 1109140.6908
32 | 2579246.0503 | 1109159.6659
33 | 2579219.8094 | 1109189.3543
34 | 2579153.0937 | 1109177.2337
35 | 2579151.5958 | 1109161.6218
36 | 2579086.4808 | 1109173.2108
37 | 2579159.2408 | 1109121.4327
38 | 2579172.3024 | 1109086.333
39 | 2579138.5536 | 1109106.291
40 | 2579128.0965 | 1109116.2696
41 | 2579092.5759 | 1109131.6422
42 | 2579080.4844 | 1109119.9906
43 | 2579138.5536 | 1109106.291

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1