## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6158-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6158-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6158-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6158-3_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6158-3_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6158-3_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6158-3_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6158-3_0_6_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_6158-3_0_6_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_6158-3_0_6_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_6158-3_0_6_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_6158-3_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_6158-3_0_6_node_62 | 0.4 | n |  | TRUE
13 | bus_LV_6158-3_0_6_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_6158-3_0_6_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_6158-3_0_6_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_6158-3_0_6_node_61 | 0.4 | n |  | TRUE
17 | bus_LV_6158-3_0_6_node_53 | 0.4 | n |  | TRUE
18 | bus_LV_6158-3_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_6158-3_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_6158-3_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_6158-3_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_6158-3_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_6158-3_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_6158-3_0_6_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_6158-3_0_6_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_6158-3_0_6_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_6158-3_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6158-3_0_6_node_44 | 0.4 | n |  | TRUE
29 | bus_LV_6158-3_0_6_node_42 | 0.4 | n |  | TRUE
30 | bus_LV_6158-3_0_6_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_6158-3_0_6_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_6158-3_0_6_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_6158-3_0_6_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_6158-3_0_6_node_65 | 0.4 | n |  | TRUE
35 | bus_LV_6158-3_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_6158-3_0_6_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_6158-3_0_6_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_6158-3_0_6_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_6158-3_0_6_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_6158-3_0_6_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_6158-3_0_6_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_6158-3_0_6_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_6158-3_0_6_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_6158-3_0_6_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_6158-3_0_6_node_50 | 0.4 | n |  | TRUE
46 | bus_LV_6158-3_0_6_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_6158-3_0_6_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_6158-3_0_6_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_6158-3_0_6_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_6158-3_0_6_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_6158-3_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_6158-3_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_6158-3_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_6158-3_0_6_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_6158-3_0_6_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_6158-3_0_6_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_6158-3_0_6_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_6158-3_0_6_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_6158-3_0_6_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_6158-3_0_6_node_60 | 0.4 | n |  | TRUE
61 | bus_MV_105_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6158-3_0_6_load_0 | 0 | 0.022463 | 0.0056298 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6158-3_0_6_load_1 | 1 | 0.0035689 | 0.00089444 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6158-3_0_6_load_6 | 6 | 0.0087216 | 0.0021858 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6158-3_0_6_load_8 | 7 | 0.0057322 | 0.0014366 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6158-3_0_6_load_10 | 8 | 0.0066437 | 0.0016651 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6158-3_0_6_load_55 | 10 | 0.0068346 | 0.0017129 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6158-3_0_6_load_9 | 11 | 0.0033299 | 0.00083456 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6158-3_0_6_load_62 | 12 | 0.0029132 | 0.00073012 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6158-3_0_6_load_58 | 13 | 0.0063433 | 0.0015898 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6158-3_0_6_load_24 | 14 | 0.011487 | 0.0028789 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6158-3_0_6_load_61 | 16 | 0.0039671 | 0.00099424 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6158-3_0_6_load_11 | 18 | 0.0071622 | 0.001795 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6158-3_0_6_load_12 | 19 | 0.0072764 | 0.0018236 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6158-3_0_6_load_14 | 21 | 0.015942 | 0.0039955 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6158-3_0_6_load_16 | 23 | 0.0078724 | 0.001973 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6158-3_0_6_load_19 | 24 | 0.0065059 | 0.0016305 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6158-3_0_6_load_18 | 25 | 0.0036839 | 0.00092326 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6158-3_0_6_load_23 | 26 | 0.010095 | 0.0025301 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6158-3_0_6_load_17 | 27 | 0.034562 | 0.0086621 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6158-3_0_6_load_44 | 28 | 0.013252 | 0.0033214 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6158-3_0_6_load_25 | 31 | 0.014458 | 0.0036236 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6158-3_0_6_load_64 | 33 | 0.0061255 | 0.0015352 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6158-3_0_6_load_65 | 34 | 0.007656 | 0.0019188 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6158-3_0_6_load_26 | 35 | 0.0202 | 0.0050626 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6158-3_0_6_load_27 | 36 | 0.013042 | 0.0032687 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6158-3_0_6_load_31 | 38 | 0.02602 | 0.0065213 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6158-3_0_6_load_32 | 39 | 0.019271 | 0.0048297 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6158-3_0_6_load_36 | 40 | 0.028975 | 0.0072617 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6158-3_0_6_load_33 | 41 | 0.027379 | 0.0068618 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6158-3_0_6_load_46 | 42 | 0.054663 | 0.0137 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6158-3_0_6_load_50 | 45 | 0.0066402 | 0.0016642 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6158-3_0_6_load_47 | 46 | 0.018391 | 0.0046093 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6158-3_0_6_load_49 | 48 | 0.0101 | 0.0025313 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6158-3_0_6_load_38 | 50 | 0.018295 | 0.0045851 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6158-3_0_6_load_39 | 51 | 0.0048705 | 0.0012207 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6158-3_0_6_load_40 | 52 | 0.044118 | 0.011057 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6158-3_0_6_load_41 | 53 | 0.0099523 | 0.0024943 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6158-3_0_6_load_48 | 54 | 0.027312 | 0.0068451 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6158-3_0_6_load_45 | 55 | 0.0047263 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6158-3_0_6_load_51 | 56 | 0.0077249 | 0.001936 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6158-3_0_6_load_54 | 58 | 0.0020859 | 0.00052278 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6158-3_0_6_load_59 | 59 | 0.013621 | 0.0034137 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6158-3_0_6_load_60 | 60 | 0.0032406 | 0.00081216 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6158-3_0_6_line_0 |  | 0 | 1 | 0.027824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6158-3_0_6_line_1 |  | 0 | 2 | 0.002231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6158-3_0_6_line_2 |  | 1 | 3 | 0.0010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6158-3_0_6_line_3 |  | 2 | 4 | 0.01852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6158-3_0_6_line_4 |  | 2 | 5 | 0.004559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6158-3_0_6_line_5 |  | 3 | 6 | 0.015256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6158-3_0_6_line_6 |  | 4 | 7 | 0.030716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6158-3_0_6_line_7 |  | 5 | 8 | 0.016917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6158-3_0_6_line_8 |  | 6 | 9 | 0.042166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6158-3_0_6_line_9 |  | 7 | 10 | 0.00072621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6158-3_0_6_line_10 |  | 8 | 13 | 0.038682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6158-3_0_6_line_11 |  | 9 | 14 | 0.033876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6158-3_0_6_line_12 |  | 9 | 15 | 0.008722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6158-3_0_6_line_13 |  | 11 | 12 | 0.016375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6158-3_0_6_line_14 |  | 12 | 16 | 0.0080294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6158-3_0_6_line_15 |  | 13 | 17 | 0.024662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6158-3_0_6_line_16 |  | 14 | 33 | 0.046388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6158-3_0_6_line_17 |  | 15 | 26 | 0.020538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_6158-3_0_6_line_18 |  | 15 | 23 | 0.060931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6158-3_0_6_line_19 |  | 16 | 60 | 0.0093301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6158-3_0_6_line_20 |  | 17 | 59 | 0.082256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6158-3_0_6_line_21 |  | 17 | 57 | 0.031131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6158-3_0_6_line_22 |  | 18 | 19 | 0.022337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6158-3_0_6_line_23 |  | 18 | 20 | 0.064118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6158-3_0_6_line_24 |  | 19 | 21 | 0.028136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6158-3_0_6_line_25 |  | 20 | 22 | 0.097077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6158-3_0_6_line_26 |  | 21 | 23 | 0.0073119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6158-3_0_6_line_27 |  | 22 | 24 | 0.038261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6158-3_0_6_line_28 |  | 24 | 25 | 0.01213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6158-3_0_6_line_29 |  | 25 | 27 | 0.0021763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6158-3_0_6_line_30 |  | 26 | 31 | 0.018158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_6158-3_0_6_line_31 |  | 28 | 29 | 0.018948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6158-3_0_6_line_32 |  | 29 | 47 | 0.021837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6158-3_0_6_line_33 |  | 29 | 39 | 0.018036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6158-3_0_6_line_34 |  | 30 | 31 | 0.019059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_6158-3_0_6_line_35 |  | 30 | 32 | 0.009542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_6158-3_0_6_line_36 |  | 32 | 55 | 0.0040049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_6158-3_0_6_line_37 |  | 33 | 34 | 0.006241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6158-3_0_6_line_38 |  | 35 | 36 | 0.0015536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6158-3_0_6_line_39 |  | 36 | 37 | 0.015636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6158-3_0_6_line_40 |  | 37 | 38 | 0.013115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6158-3_0_6_line_41 |  | 37 | 39 | 0.0064771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6158-3_0_6_line_42 |  | 38 | 40 | 0.0013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6158-3_0_6_line_43 |  | 41 | 42 | 0.025898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6158-3_0_6_line_44 |  | 42 | 44 | 0.021922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6158-3_0_6_line_45 |  | 43 | 44 | 0.053426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6158-3_0_6_line_46 |  | 43 | 45 | 0.04849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6158-3_0_6_line_47 |  | 44 | 46 | 0.0051297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6158-3_0_6_line_48 |  | 46 | 48 | 0.0030831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6158-3_0_6_line_49 |  | 47 | 55 | 0.0075552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_6158-3_0_6_line_50 |  | 47 | 53 | 0.0050359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_6158-3_0_6_line_51 |  | 48 | 54 | 0.0088445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6158-3_0_6_line_52 |  | 49 | 50 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_6158-3_0_6_line_53 |  | 49 | 51 | 0.017263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_6158-3_0_6_line_54 |  | 50 | 52 | 0.013594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_6158-3_0_6_line_55 |  | 51 | 53 | 0.018071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_6158-3_0_6_line_56 |  | 52 | 54 | 0.0045443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_6158-3_0_6_line_57 |  | 56 | 57 | 0.070761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6158-3_0_6_line_58 |  | 57 | 58 | 0.017301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6158-3_0_6_line_59 |  | 58 | 60 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6158-3_0_6_trafo_39 | 0.63 MVA 20/0.4 kV | 61 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2558373.5558 | 1129086.8152 | 2558400.9288 | 1129091.8037
1 | 2558371.3609 | 1129086.4152 | 2558373.5558 | 1129086.8152
2 | 2558401.982 | 1129091.9957 | 2558400.9288 | 1129091.8037
3 | 2558371.3609 | 1129086.4152 | 2558373.5192 | 1129074.3274 | 2558379.7259 | 1129075.1184
4 | 2558366.8641 | 1129085.5902 | 2558371.3609 | 1129086.4152
5 | 2558401.982 | 1129091.9957 | 2558416.9945 | 1129094.7098
6 | 2558379.7259 | 1129075.1184 | 2558383.3902 | 1129044.622
7 | 2558366.8641 | 1129085.5902 | 2558350.2213 | 1129082.5561
8 | 2558458.4875 | 1129102.2114 | 2558416.9945 | 1129094.7098
9 | 2558383.3902 | 1129044.622 | 2558384.1138 | 1129044.683
10 | 2558312.1667 | 1129075.6183 | 2558350.2213 | 1129082.5561
11 | 2558458.4875 | 1129102.2114 | 2558453.8328 | 1129127.6454 | 2558452.842 | 1129135.604
12 | 2558459.7762 | 1129093.5871 | 2558458.4875 | 1129102.2114
13 | 2558342.0884 | 1129051.7809 | 2558358.0543 | 1129055.4189
14 | 2558334.2596 | 1129049.997 | 2558342.0884 | 1129051.7809
15 | 2558287.9047 | 1129071.1951 | 2558312.1667 | 1129075.6183
16 | 2558452.842 | 1129135.604 | 2558447.1116 | 1129181.6365
17 | 2558459.7762 | 1129093.5871 | 2558461.0207 | 1129085.2631 | 2558461.4036 | 1129082.6925 | 2558462.8838 | 1129073.2857
18 | 2558459.7762 | 1129093.5871 | 2558465.3607 | 1129101.3526 | 2558465.8695 | 1129120.4143 | 2558467.4763 | 1129134.4882 | 2558474.7222 | 1129132.9375 | 2558485.2097 | 1129130.7057
19 | 2558334.2596 | 1129049.997 | 2558325.1627 | 1129047.9241
20 | 2558287.9047 | 1129071.1951 | 2558293.2815 | 1129094.5476 | 2558295.4977 | 1129114.2534 | 2558293.3378 | 1129132.7556 | 2558291.5781 | 1129152.3111 | 2558291.5494 | 1129152.509
21 | 2558287.9047 | 1129071.1951 | 2558288.907 | 1129059.0708 | 2558294.2969 | 1129040.891
22 | 2558541.7284 | 1129118.6779 | 2558519.8811 | 1129123.3273
23 | 2558604.442 | 1129105.3318 | 2558541.7284 | 1129118.6779
24 | 2558492.3614 | 1129129.1837 | 2558519.8811 | 1129123.3273
25 | 2558544.3604 | 1129054.5074 | 2558560.8647 | 1129051.6481 | 2558578.5384 | 1129048.5807 | 2558589.4012 | 1129073.3854 | 2558604.442 | 1129105.3318
26 | 2558492.3614 | 1129129.1837 | 2558485.2097 | 1129130.7057
27 | 2558544.3604 | 1129054.5074 | 2558516.5603 | 1129068.1833 | 2558509.8315 | 1129065.4059
28 | 2558506.8667 | 1129053.6442 | 2558509.8315 | 1129065.4059
29 | 2558506.3348 | 1129051.534 | 2558506.8667 | 1129053.6442
30 | 2558465.7063 | 1129055.3489 | 2558462.8838 | 1129073.2857
31 | 2558480.5995 | 1129004.2425 | 2558498.3594 | 1128997.6375
32 | 2558466.5597 | 1129019.3247 | 2558471.8267 | 1129008.9387 | 2558473.538 | 1129006.8703 | 2558480.5995 | 1129004.2425
33 | 2558480.5995 | 1129004.2425 | 2558480.2712 | 1128986.2091
34 | 2558474.4673 | 1129038.8913 | 2558471.0774 | 1129042.1941 | 2558468.5781 | 1129046.1689 | 2558467.201 | 1129049.7914 | 2558465.7063 | 1129055.3489
35 | 2558470.8859 | 1129030.0448 | 2558474.4673 | 1129038.8913
36 | 2558470.8859 | 1129030.0448 | 2558469.3871 | 1129026.3309
37 | 2558447.1116 | 1129181.6365 | 2558446.3406 | 1129187.8297
38 | 2558494.3134 | 1128973.1814 | 2558495.6766 | 1128972.4362
39 | 2558480.1533 | 1128979.7331 | 2558487.6289 | 1128976.8357 | 2558494.3134 | 1128973.1814
40 | 2558480.1533 | 1128979.7331 | 2558467.3087 | 1128982.3844
41 | 2558480.1533 | 1128979.7331 | 2558480.2712 | 1128986.2091
42 | 2558467.3087 | 1128982.3844 | 2558465.9857 | 1128982.6575
43 | 2558468.7727 | 1128941.9999 | 2558464.2327 | 1128942.0902 | 2558442.9777 | 1128944.1732
44 | 2558421.1602 | 1128946.3113 | 2558442.9777 | 1128944.1732
45 | 2558421.1602 | 1128946.3113 | 2558420.2887 | 1128936.1121 | 2558419.6387 | 1128916.7067 | 2558418.9355 | 1128892.9439
46 | 2558418.9355 | 1128892.9439 | 2558373.362 | 1128909.5061
47 | 2558421.1602 | 1128946.3113 | 2558421.5977 | 1128951.4223
48 | 2558421.5977 | 1128951.4223 | 2558421.8606 | 1128954.4942
49 | 2558466.5597 | 1129019.3247 | 2558469.3871 | 1129026.3309
50 | 2558466.5597 | 1129019.3247 | 2558464.6375 | 1129014.67
51 | 2558423.1968 | 1128963.208 | 2558422.308 | 1128959.7214 | 2558421.8606 | 1128954.4942
52 | 2558442.7673 | 1128987.4501 | 2558433.4649 | 1128980.1327 | 2558432.0383 | 1128978.6254
53 | 2558442.7673 | 1128987.4501 | 2558452.3599 | 1128997.7559 | 2558454.5736 | 1129000.0435
54 | 2558432.0383 | 1128978.6254 | 2558427.381 | 1128973.7046 | 2558424.3192 | 1128967.6115
55 | 2558464.6375 | 1129014.67 | 2558461.5928 | 1129007.2972 | 2558454.5736 | 1129000.0435
56 | 2558423.1968 | 1128963.208 | 2558424.3192 | 1128967.6115 | 2558424.3192 | 1128967.6115
57 | 2558294.2969 | 1129040.891 | 2558300.4661 | 1129022.8836 | 2558327.6093 | 1128978.8513
58 | 2558294.2969 | 1129040.891 | 2558311.1653 | 1129044.7347
59 | 2558325.1627 | 1129047.9241 | 2558311.1653 | 1129044.7347

## bus_geodata
| x | y | coords
0 | 2558373.5558 | 1129086.8152
1 | 2558400.9288 | 1129091.8037
2 | 2558371.3609 | 1129086.4152
3 | 2558401.982 | 1129091.9957
4 | 2558379.7259 | 1129075.1184
5 | 2558366.8641 | 1129085.5902
6 | 2558416.9945 | 1129094.7098
7 | 2558383.3902 | 1129044.622
8 | 2558350.2213 | 1129082.5561
9 | 2558458.4875 | 1129102.2114
10 | 2558384.1138 | 1129044.683
11 | 2558358.0543 | 1129055.4189
12 | 2558342.0884 | 1129051.7809
13 | 2558312.1667 | 1129075.6183
14 | 2558452.842 | 1129135.604
15 | 2558459.7762 | 1129093.5871
16 | 2558334.2596 | 1129049.997
17 | 2558287.9047 | 1129071.1951
18 | 2558541.7284 | 1129118.6779
19 | 2558519.8811 | 1129123.3273
20 | 2558604.442 | 1129105.3318
21 | 2558492.3614 | 1129129.1837
22 | 2558544.3604 | 1129054.5074
23 | 2558485.2097 | 1129130.7057
24 | 2558509.8315 | 1129065.4059
25 | 2558506.8667 | 1129053.6442
26 | 2558462.8838 | 1129073.2857
27 | 2558506.3348 | 1129051.534
28 | 2558498.3594 | 1128997.6375
29 | 2558480.5995 | 1129004.2425
30 | 2558474.4673 | 1129038.8913
31 | 2558465.7063 | 1129055.3489
32 | 2558470.8859 | 1129030.0448
33 | 2558447.1116 | 1129181.6365
34 | 2558446.3406 | 1129187.8297
35 | 2558495.6766 | 1128972.4362
36 | 2558494.3134 | 1128973.1814
37 | 2558480.1533 | 1128979.7331
38 | 2558467.3087 | 1128982.3844
39 | 2558480.2712 | 1128986.2091
40 | 2558465.9857 | 1128982.6575
41 | 2558468.7727 | 1128941.9999
42 | 2558442.9777 | 1128944.1732
43 | 2558418.9355 | 1128892.9439
44 | 2558421.1602 | 1128946.3113
45 | 2558373.362 | 1128909.5061
46 | 2558421.5977 | 1128951.4223
47 | 2558466.5597 | 1129019.3247
48 | 2558421.8606 | 1128954.4942
49 | 2558442.7673 | 1128987.4501
50 | 2558432.0383 | 1128978.6254
51 | 2558454.5736 | 1129000.0435
52 | 2558424.3192 | 1128967.6115
53 | 2558464.6375 | 1129014.67
54 | 2558423.1968 | 1128963.208
55 | 2558469.3871 | 1129026.3309
56 | 2558327.6093 | 1128978.8513
57 | 2558294.2969 | 1129040.891
58 | 2558311.1653 | 1129044.7347
59 | 2558291.5494 | 1129152.509
60 | 2558325.1627 | 1129047.9241
61 | 2558442.7673 | 1128987.4501

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1