## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6201-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6201-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6201-4_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6201-4_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6201-4_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6201-4_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6201-4_0_5_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_6201-4_0_5_node_64 | 0.4 | n |  | TRUE
8 | bus_LV_6201-4_0_5_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_6201-4_0_5_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_6201-4_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_6201-4_0_5_node_65 | 0.4 | n |  | TRUE
12 | bus_LV_6201-4_0_5_node_47 | 0.4 | n |  | TRUE
13 | bus_LV_6201-4_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_6201-4_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_6201-4_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6201-4_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_6201-4_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_6201-4_0_5_node_90 | 0.4 | n |  | TRUE
19 | bus_LV_6201-4_0_5_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_6201-4_0_5_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_6201-4_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_6201-4_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_6201-4_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_6201-4_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_6201-4_0_5_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_6201-4_0_5_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_6201-4_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_6201-4_0_5_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_6201-4_0_5_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_6201-4_0_5_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_6201-4_0_5_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_6201-4_0_5_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_6201-4_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_6201-4_0_5_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_6201-4_0_5_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_6201-4_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_6201-4_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_6201-4_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_6201-4_0_5_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_6201-4_0_5_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_6201-4_0_5_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_6201-4_0_5_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_6201-4_0_5_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_6201-4_0_5_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_6201-4_0_5_node_89 | 0.4 | n |  | TRUE
46 | bus_LV_6201-4_0_5_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_6201-4_0_5_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_6201-4_0_5_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_6201-4_0_5_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_6201-4_0_5_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_6201-4_0_5_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_6201-4_0_5_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_6201-4_0_5_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_6201-4_0_5_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_6201-4_0_5_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_6201-4_0_5_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_6201-4_0_5_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_6201-4_0_5_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_6201-4_0_5_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_6201-4_0_5_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_6201-4_0_5_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_6201-4_0_5_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_6201-4_0_5_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_6201-4_0_5_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_6201-4_0_5_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_6201-4_0_5_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_6201-4_0_5_node_78 | 0.4 | n |  | TRUE
68 | bus_LV_6201-4_0_5_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_6201-4_0_5_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_6201-4_0_5_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_6201-4_0_5_node_79 | 0.4 | n |  | TRUE
72 | bus_LV_6201-4_0_5_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_6201-4_0_5_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_6201-4_0_5_node_85 | 0.4 | n |  | TRUE
75 | bus_LV_6201-4_0_5_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_6201-4_0_5_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_6201-4_0_5_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_6201-4_0_5_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_6201-4_0_5_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_6201-4_0_5_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_6201-4_0_5_node_87 | 0.4 | n |  | TRUE
82 | bus_LV_6201-4_0_5_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_6201-4_0_5_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_6201-4_0_5_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_6201-4_0_5_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_6201-4_0_5_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_6201-4_0_5_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_6201-4_0_5_node_83 | 0.4 | n |  | TRUE
89 | bus_MV_109_0_node_188 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6201-4_0_5_load_0 | 0 | 0.016039 | 0.0040198 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6201-4_0_5_load_1 | 1 | 0.014205 | 0.0035602 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6201-4_0_5_load_3 | 3 | 0.010255 | 0.0025701 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6201-4_0_5_load_4 | 4 | 0.0042032 | 0.0010534 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6201-4_0_5_load_5 | 5 | 0.0031482 | 0.00078902 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6201-4_0_5_load_64 | 7 | 0.0070703 | 0.001772 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6201-4_0_5_load_48 | 8 | 0.0046822 | 0.0011735 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6201-4_0_5_load_9 | 10 | 0.0067301 | 0.0016867 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6201-4_0_5_load_65 | 11 | 0.0042782 | 0.0010722 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6201-4_0_5_load_47 | 12 | 0.0049013 | 0.0012284 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6201-4_0_5_load_6 | 13 | 0.026076 | 0.0065353 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6201-4_0_5_load_10 | 16 | 0.032822 | 0.0082261 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6201-4_0_5_load_11 | 17 | 0.034132 | 0.0085544 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6201-4_0_5_load_90 | 18 | 0.012774 | 0.0032015 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6201-4_0_5_load_20 | 19 | 0.010893 | 0.0027301 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6201-4_0_5_load_21 | 20 | 0.0087163 | 0.0021845 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6201-4_0_5_load_12 | 21 | 0.0048847 | 0.0012242 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6201-4_0_5_load_13 | 22 | 0.01248 | 0.0031277 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6201-4_0_5_load_15 | 24 | 0.0060819 | 0.0015243 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6201-4_0_5_load_17 | 26 | 0.016506 | 0.0041367 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6201-4_0_5_load_22 | 27 | 0.0030729 | 0.00077014 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6201-4_0_5_load_28 | 28 | 0.0032737 | 0.00082048 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6201-4_0_5_load_36 | 30 | 0.0038283 | 0.00095947 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6201-4_0_5_load_24 | 31 | 0.0024356 | 0.00061041 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6201-4_0_5_load_40 | 32 | 0.0074278 | 0.0018616 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6201-4_0_5_load_23 | 33 | 0.0068206 | 0.0017094 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6201-4_0_5_load_41 | 34 | 0.0058936 | 0.0014771 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6201-4_0_5_load_26 | 37 | 0.0043094 | 0.00108 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6201-4_0_5_load_27 | 38 | 0.0047484 | 0.0011901 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6201-4_0_5_load_43 | 39 | 0.0092043 | 0.0023068 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6201-4_0_5_load_34 | 40 | 0.0024206 | 0.00060665 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6201-4_0_5_load_44 | 41 | 0.0055969 | 0.0014027 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6201-4_0_5_load_32 | 42 | 0.0091466 | 0.0022924 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6201-4_0_5_load_37 | 43 | 0.0075818 | 0.0019002 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6201-4_0_5_load_88 | 44 | 0.0060358 | 0.0015127 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6201-4_0_5_load_89 | 45 | 0.0093086 | 0.002333 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6201-4_0_5_load_31 | 46 | 0.0089648 | 0.0022468 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6201-4_0_5_load_33 | 47 | 0.0047286 | 0.0011851 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6201-4_0_5_load_38 | 48 | 0.0033453 | 0.00083841 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6201-4_0_5_load_39 | 49 | 0.0042223 | 0.0010582 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6201-4_0_5_load_42 | 52 | 0.011692 | 0.0029302 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6201-4_0_5_load_62 | 53 | 0.0055098 | 0.0013809 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6201-4_0_5_load_63 | 54 | 0.005846 | 0.0014651 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6201-4_0_5_load_61 | 55 | 0.0089388 | 0.0022403 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6201-4_0_5_load_60 | 56 | 0.0049749 | 0.0012468 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6201-4_0_5_load_69 | 58 | 0.0060393 | 0.0015136 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6201-4_0_5_load_46 | 59 | 0.0055042 | 0.0013795 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6201-4_0_5_load_49 | 60 | 0.0041424 | 0.0010382 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6201-4_0_5_load_50 | 61 | 0.01538 | 0.0038546 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6201-4_0_5_load_53 | 64 | 0.0076481 | 0.0019168 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6201-4_0_5_load_55 | 65 | 0.0063006 | 0.0015791 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6201-4_0_5_load_56 | 66 | 0.003568 | 0.00089423 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6201-4_0_5_load_78 | 67 | 0.012436 | 0.0031167 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6201-4_0_5_load_80 | 68 | 0.011176 | 0.0028009 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6201-4_0_5_load_59 | 69 | 0.0030268 | 0.0007586 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6201-4_0_5_load_57 | 70 | 0.0052708 | 0.001321 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6201-4_0_5_load_79 | 71 | 0.0059225 | 0.0014843 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6201-4_0_5_load_58 | 72 | 0.0052143 | 0.0013068 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6201-4_0_5_load_81 | 73 | 0.0036251 | 0.00090853 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6201-4_0_5_load_85 | 74 | 0.0053312 | 0.0013361 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6201-4_0_5_load_67 | 76 | 0.013026 | 0.0032647 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6201-4_0_5_load_68 | 77 | 0.0079695 | 0.0019974 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6201-4_0_5_load_70 | 78 | 0.0045604 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6201-4_0_5_load_72 | 79 | 0.0043318 | 0.0010857 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6201-4_0_5_load_86 | 80 | 0.0049721 | 0.0012461 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6201-4_0_5_load_87 | 81 | 0.004389 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6201-4_0_5_load_73 | 83 | 0.010369 | 0.0025986 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6201-4_0_5_load_74 | 84 | 0.0056413 | 0.0014138 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6201-4_0_5_load_75 | 85 | 0.0035739 | 0.00089571 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6201-4_0_5_load_77 | 86 | 0.0043102 | 0.0010802 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6201-4_0_5_load_82 | 87 | 0.0042848 | 0.0010739 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6201-4_0_5_load_83 | 88 | 0.0088668 | 0.0022222 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6201-4_0_5_line_0 |  | 0 | 1 | 0.064388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6201-4_0_5_line_1 |  | 0 | 2 | 0.027211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6201-4_0_5_line_2 |  | 2 | 3 | 0.013654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6201-4_0_5_line_3 |  | 2 | 4 | 0.020911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6201-4_0_5_line_4 |  | 2 | 5 | 0.0090108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6201-4_0_5_line_5 |  | 3 | 6 | 0.018401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6201-4_0_5_line_6 |  | 4 | 7 | 0.0215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6201-4_0_5_line_7 |  | 5 | 8 | 0.0010299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6201-4_0_5_line_8 |  | 6 | 9 | 0.014915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_6201-4_0_5_line_9 |  | 6 | 10 | 0.010812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_6201-4_0_5_line_10 |  | 7 | 11 | 0.00039855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6201-4_0_5_line_11 |  | 8 | 12 | 0.019248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6201-4_0_5_line_12 |  | 9 | 31 | 0.011498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6201-4_0_5_line_13 |  | 9 | 32 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_6201-4_0_5_line_14 |  | 10 | 14 | 0.016049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_6201-4_0_5_line_15 |  | 11 | 75 | 0.011518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6201-4_0_5_line_16 |  | 12 | 59 | 0.019882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6201-4_0_5_line_17 |  | 13 | 14 | 0.022279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_6201-4_0_5_line_18 |  | 13 | 15 | 0.017679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6201-4_0_5_line_19 |  | 14 | 16 | 0.020987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_6201-4_0_5_line_20 |  | 15 | 17 | 0.010348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6201-4_0_5_line_21 |  | 16 | 18 | 0.023195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6201-4_0_5_line_22 |  | 17 | 19 | 0.00080191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6201-4_0_5_line_23 |  | 19 | 20 | 0.011958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6201-4_0_5_line_24 |  | 20 | 25 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6201-4_0_5_line_25 |  | 21 | 22 | 0.00095666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6201-4_0_5_line_26 |  | 21 | 23 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6201-4_0_5_line_27 |  | 22 | 24 | 0.0092925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6201-4_0_5_line_28 |  | 23 | 25 | 0.004059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6201-4_0_5_line_29 |  | 23 | 26 | 0.017527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6201-4_0_5_line_30 |  | 24 | 27 | 0.00061128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6201-4_0_5_line_31 |  | 25 | 28 | 0.0224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6201-4_0_5_line_32 |  | 27 | 29 | 0.055131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6201-4_0_5_line_33 |  | 28 | 30 | 0.01274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6201-4_0_5_line_34 |  | 29 | 35 | 0.029078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6201-4_0_5_line_35 |  | 30 | 43 | 0.015551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6201-4_0_5_line_36 |  | 31 | 33 | 0.0048994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6201-4_0_5_line_37 |  | 32 | 34 | 0.026914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_6201-4_0_5_line_38 |  | 33 | 36 | 0.0085155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6201-4_0_5_line_39 |  | 34 | 52 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_6201-4_0_5_line_40 |  | 35 | 44 | 0.016116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6201-4_0_5_line_41 |  | 35 | 45 | 0.022633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6201-4_0_5_line_42 |  | 36 | 37 | 0.010676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6201-4_0_5_line_43 |  | 36 | 38 | 0.0062048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6201-4_0_5_line_44 |  | 37 | 39 | 0.0098343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6201-4_0_5_line_45 |  | 38 | 40 | 0.0048427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6201-4_0_5_line_46 |  | 39 | 41 | 0.0060157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6201-4_0_5_line_47 |  | 40 | 42 | 0.01678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6201-4_0_5_line_48 |  | 41 | 55 | 0.010403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6201-4_0_5_line_49 |  | 42 | 46 | 0.012819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6201-4_0_5_line_50 |  | 43 | 48 | 0.009444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6201-4_0_5_line_51 |  | 46 | 47 | 0.014959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6201-4_0_5_line_52 |  | 49 | 50 | 0.036922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6201-4_0_5_line_53 |  | 50 | 51 | 0.01496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6201-4_0_5_line_54 |  | 51 | 57 | 0.045784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6201-4_0_5_line_55 |  | 51 | 58 | 0.0151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_6201-4_0_5_line_56 |  | 52 | 53 | 0.039713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_6201-4_0_5_line_57 |  | 53 | 54 | 0.0065598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_6201-4_0_5_line_58 |  | 54 | 73 | 0.00065962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_6201-4_0_5_line_59 |  | 55 | 56 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6201-4_0_5_line_60 |  | 56 | 72 | 0.0061034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6201-4_0_5_line_61 |  | 57 | 81 | 0.051439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6201-4_0_5_line_62 |  | 57 | 82 | 0.061601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6201-4_0_5_line_63 |  | 58 | 77 | 0.013857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_6201-4_0_5_line_64 |  | 60 | 61 | 0.011303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6201-4_0_5_line_65 |  | 60 | 62 | 0.044111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6201-4_0_5_line_66 |  | 61 | 63 | 0.03289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6201-4_0_5_line_67 |  | 62 | 64 | 0.018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6201-4_0_5_line_68 |  | 63 | 65 | 0.0073618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6201-4_0_5_line_69 |  | 63 | 66 | 0.033631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6201-4_0_5_line_70 |  | 65 | 67 | 0.032167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6201-4_0_5_line_71 |  | 66 | 68 | 0.021042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6201-4_0_5_line_72 |  | 67 | 71 | 0.025243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6201-4_0_5_line_73 |  | 69 | 70 | 0.0037127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6201-4_0_5_line_74 |  | 70 | 72 | 0.012413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6201-4_0_5_line_75 |  | 71 | 81 | 0.034347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6201-4_0_5_line_76 |  | 73 | 74 | 0.018194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_6201-4_0_5_line_77 |  | 74 | 80 | 0.0086962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_6201-4_0_5_line_78 |  | 75 | 76 | 0.017605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6201-4_0_5_line_79 |  | 77 | 78 | 0.0088854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_6201-4_0_5_line_80 |  | 78 | 79 | 0.010092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_6201-4_0_5_line_81 |  | 79 | 80 | 0.015931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_6201-4_0_5_line_82 |  | 82 | 87 | 0.021994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6201-4_0_5_line_83 |  | 82 | 84 | 0.018367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6201-4_0_5_line_84 |  | 83 | 84 | 0.0056246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6201-4_0_5_line_85 |  | 83 | 85 | 0.0055435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6201-4_0_5_line_86 |  | 85 | 86 | 0.022074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6201-4_0_5_line_87 |  | 87 | 88 | 0.010054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6201-4_0_5_trafo_10 | 0.63 MVA 20/0.4 kV | 89 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2627810.8008 | 1126043.1032 | 2627822.7973 | 1126044.1884 | 2627844.7156 | 1126057.7403 | 2627845.5193 | 1126084.3007
1 | 2627783.7001 | 1126040.6517 | 2627810.8008 | 1126043.1032
2 | 2627783.7001 | 1126040.6517 | 2627783.3096 | 1126027.003
3 | 2627783.7001 | 1126040.6517 | 2627787.1975 | 1126061.268
4 | 2627783.7001 | 1126040.6517 | 2627779.2572 | 1126048.4911
5 | 2627782.7834 | 1126008.6094 | 2627783.3096 | 1126027.003
6 | 2627790.7935 | 1126082.4653 | 2627787.1975 | 1126061.268
7 | 2627778.7495 | 1126049.387 | 2627779.2572 | 1126048.4911
8 | 2627767.9162 | 1126006.9626 | 2627782.7834 | 1126008.6094
9 | 2627782.7834 | 1126008.6094 | 2627793.5675 | 1126007.831
10 | 2627790.8602 | 1126082.8583 | 2627790.7935 | 1126082.4653
11 | 2627778.7495 | 1126049.387 | 2627778.3776 | 1126050.0431 | 2627770.6368 | 1126060.7685 | 2627765.875 | 1126063.0199
12 | 2627767.9162 | 1126006.9626 | 2627762.0742 | 1126008.6367 | 2627757.2719 | 1126011.1508
13 | 2627767.9162 | 1126006.9626 | 2627767.8812 | 1126001.1596 | 2627767.4797 | 1125994.0827
14 | 2627809.5746 | 1126006.6757 | 2627793.5675 | 1126007.831
15 | 2627793.8908 | 1126093.9694 | 2627790.904 | 1126083.117 | 2627790.8602 | 1126082.8583
16 | 2627753.9815 | 1126075.9887 | 2627755.0811 | 1126068.1232 | 2627765.875 | 1126063.0199
17 | 2627809.5746 | 1126006.6757 | 2627831.0433 | 1126000.7211
18 | 2627848.0747 | 1125995.9805 | 2627831.6143 | 1126000.5627 | 2627831.0433 | 1126000.7211
19 | 2627808.3991 | 1125985.7266 | 2627809.5746 | 1126006.6757
20 | 2627848.0747 | 1125995.9805 | 2627857.991 | 1125993.024
21 | 2627808.3991 | 1125985.7266 | 2627817.176 | 1125964.2562
22 | 2627857.991 | 1125993.024 | 2627858.7595 | 1125992.7949
23 | 2627858.7595 | 1125992.7949 | 2627870.2185 | 1125989.3785
24 | 2627883.2521 | 1125985.4926 | 2627870.2185 | 1125989.3785
25 | 2627890.1107 | 1125999.4786 | 2627889.925 | 1125998.5401
26 | 2627887.0584 | 1125984.0538 | 2627889.925 | 1125998.5401
27 | 2627891.9146 | 1126008.5943 | 2627890.1107 | 1125999.4786
28 | 2627883.2521 | 1125985.4926 | 2627887.0584 | 1125984.0538
29 | 2627887.0584 | 1125984.0538 | 2627902.132 | 1125975.1113
30 | 2627892.0332 | 1126009.194 | 2627891.9146 | 1126008.5943
31 | 2627883.2521 | 1125985.4926 | 2627875.92 | 1125964.3271
32 | 2627892.4087 | 1126059.0491 | 2627884.2188 | 1126041.7028 | 2627885.2885 | 1126033.6815 | 2627891.9315 | 1126027.1088 | 2627894.2363 | 1126020.3271 | 2627892.0332 | 1126009.194
33 | 2627875.92 | 1125964.3271 | 2627871.7496 | 1125952.2886
34 | 2627892.4087 | 1126059.0491 | 2627894.8642 | 1126064.7299 | 2627894.7459 | 1126068.6535 | 2627897.502 | 1126074.3357 | 2627900.9604 | 1126086.5021
35 | 2627866.6591 | 1125937.594 | 2627871.7496 | 1125952.2886
36 | 2627757.2719 | 1126011.1508 | 2627755.1907 | 1126012.2403 | 2627753.0723 | 1126013.6602
37 | 2627767.4797 | 1125994.0827 | 2627766.7331 | 1125980.922 | 2627765.8382 | 1125967.2188
38 | 2627745.9987 | 1126018.4013 | 2627753.0723 | 1126013.6602
39 | 2627764.3758 | 1125947.0388 | 2627765.6888 | 1125964.9315 | 2627765.8382 | 1125967.2188
40 | 2627900.9604 | 1126086.5021 | 2627917.0956 | 1126085.5537
41 | 2627900.9604 | 1126086.5021 | 2627878.6223 | 1126090.5236
42 | 2627745.9987 | 1126018.4013 | 2627738.3738 | 1126012.2189 | 2627737.6593 | 1126011.7411
43 | 2627745.9987 | 1126018.4013 | 2627741.3259 | 1126022.4836
44 | 2627737.6593 | 1126011.7411 | 2627729.4839 | 1126006.2752
45 | 2627741.3259 | 1126022.4836 | 2627737.6789 | 1126025.6697
46 | 2627729.4839 | 1126006.2752 | 2627729.4839 | 1126006.2752 | 2627724.2228 | 1126003.358
47 | 2627724.0809 | 1126035.4623 | 2627730.0535 | 1126031.6905 | 2627737.3785 | 1126025.9322 | 2627737.6789 | 1126025.6697
48 | 2627714.9202 | 1125998.7339 | 2627718.9518 | 1126000.4352 | 2627724.2228 | 1126003.358
49 | 2627712.5625 | 1126041.0354 | 2627721.6825 | 1126036.977 | 2627724.0809 | 1126035.4623
50 | 2627866.6591 | 1125937.594 | 2627865.081 | 1125933.0385 | 2627864.8472 | 1125928.4215
51 | 2627712.5625 | 1126041.0354 | 2627698.8952 | 1126047.1174
52 | 2627844.7851 | 1125833.0399 | 2627853.3913 | 1125865.5178 | 2627854.029 | 1125868.7787
53 | 2627844.7851 | 1125833.0399 | 2627829.9828 | 1125830.5929
54 | 2627829.9828 | 1125830.5929 | 2627834.5069 | 1125812.16 | 2627837.4557 | 1125801.1014 | 2627822.6454 | 1125797.0314
55 | 2627829.9828 | 1125830.5929 | 2627823.9851 | 1125837.5911 | 2627822.1291 | 1125843.1736
56 | 2627764.3758 | 1125947.0388 | 2627764.3758 | 1125947.0388 | 2627765.37 | 1125933.5922 | 2627770.6399 | 1125918.8757 | 2627777.6462 | 1125910.9233
57 | 2627777.6462 | 1125910.9233 | 2627781.9827 | 1125906.0013
58 | 2627782.4187 | 1125905.5064 | 2627781.9827 | 1125906.0013
59 | 2627714.9202 | 1125998.7339 | 2627702.0981 | 1125993.323
60 | 2627696.4749 | 1125990.95 | 2627702.0981 | 1125993.323
61 | 2627822.6454 | 1125797.0314 | 2627814.7797 | 1125806.3221 | 2627809.1266 | 1125815.4896 | 2627798.2623 | 1125834.9828 | 2627794.2989 | 1125839.7232
62 | 2627793.8573 | 1125787.1499 | 2627794.8528 | 1125783.5305 | 2627797.9713 | 1125780.8101 | 2627800.6542 | 1125780.6668 | 2627817.5988 | 1125783.2236 | 2627833.7841 | 1125783.2757 | 2627822.6454 | 1125797.0314
63 | 2627817.7573 | 1125856.3227 | 2627822.1291 | 1125843.1736
64 | 2627679.3661 | 1125923.6152 | 2627683.1377 | 1125919.2645 | 2627687.1882 | 1125915.477
65 | 2627650.472 | 1125956.9453 | 2627679.3661 | 1125923.6152
66 | 2627711.212 | 1125893.0131 | 2627687.1882 | 1125915.477
67 | 2627650.472 | 1125956.9453 | 2627638.9789 | 1125948.8666 | 2627637.4149 | 1125944.4924
68 | 2627711.212 | 1125893.0131 | 2627717.5275 | 1125889.2301
69 | 2627711.212 | 1125893.0131 | 2627744.6929 | 1125889.8431
70 | 2627717.5275 | 1125889.2301 | 2627731.7852 | 1125880.6899 | 2627745.1913 | 1125872.8168
71 | 2627765.6413 | 1125887.8596 | 2627744.6929 | 1125889.8431
72 | 2627766.9582 | 1125860.0337 | 2627745.1913 | 1125872.8168
73 | 2627686.3718 | 1125983.7651 | 2627683.462 | 1125981.4592
74 | 2627686.3718 | 1125983.7651 | 2627691.0726 | 1125987.4903 | 2627696.4749 | 1125990.95 | 2627696.4749 | 1125990.95
75 | 2627794.2989 | 1125839.7232 | 2627789.4662 | 1125845.5033 | 2627778.0843 | 1125853.4995 | 2627766.9582 | 1125860.0337
76 | 2627794.8106 | 1125892.1887 | 2627785.7012 | 1125901.7807 | 2627782.4187 | 1125905.5064
77 | 2627794.8106 | 1125892.1887 | 2627800.7991 | 1125885.883
78 | 2627811.4064 | 1126096.1953 | 2627793.8908 | 1126093.9694
79 | 2627817.7573 | 1125856.3227 | 2627814.954 | 1125864.7543
80 | 2627811.7699 | 1125874.3311 | 2627814.954 | 1125864.7543
81 | 2627800.7991 | 1125885.883 | 2627811.7699 | 1125874.3311 | 2627811.7699 | 1125874.3311
82 | 2627793.8573 | 1125787.1499 | 2627784.8185 | 1125786.7083 | 2627781.7348 | 1125783.5037 | 2627778.1829 | 1125779.8856 | 2627774.9915 | 1125778.6362
83 | 2627793.8573 | 1125787.1499 | 2627793.7262 | 1125790.5177 | 2627790.7664 | 1125803.9997 | 2627790.4539 | 1125805.1517
84 | 2627788.6074 | 1125810.3878 | 2627789.2455 | 1125809.6066 | 2627790.4539 | 1125805.1517
85 | 2627788.6074 | 1125810.3878 | 2627785.1003 | 1125814.681
86 | 2627785.1003 | 1125814.681 | 2627783.8353 | 1125816.2296 | 2627778.5972 | 1125820.6411 | 2627771.9206 | 1125822.7671 | 2627765.9455 | 1125824.4932
87 | 2627765.2248 | 1125776.947 | 2627771.1432 | 1125777.1297 | 2627774.9915 | 1125778.6362

## bus_geodata
| x | y | coords
0 | 2627810.8008 | 1126043.1032
1 | 2627845.5193 | 1126084.3007
2 | 2627783.7001 | 1126040.6517
3 | 2627783.3096 | 1126027.003
4 | 2627787.1975 | 1126061.268
5 | 2627779.2572 | 1126048.4911
6 | 2627782.7834 | 1126008.6094
7 | 2627790.7935 | 1126082.4653
8 | 2627778.7495 | 1126049.387
9 | 2627767.9162 | 1126006.9626
10 | 2627793.5675 | 1126007.831
11 | 2627790.8602 | 1126082.8583
12 | 2627765.875 | 1126063.0199
13 | 2627831.0433 | 1126000.7211
14 | 2627809.5746 | 1126006.6757
15 | 2627848.0747 | 1125995.9805
16 | 2627808.3991 | 1125985.7266
17 | 2627857.991 | 1125993.024
18 | 2627817.176 | 1125964.2562
19 | 2627858.7595 | 1125992.7949
20 | 2627870.2185 | 1125989.3785
21 | 2627889.925 | 1125998.5401
22 | 2627890.1107 | 1125999.4786
23 | 2627887.0584 | 1125984.0538
24 | 2627891.9146 | 1126008.5943
25 | 2627883.2521 | 1125985.4926
26 | 2627902.132 | 1125975.1113
27 | 2627892.0332 | 1126009.194
28 | 2627875.92 | 1125964.3271
29 | 2627892.4087 | 1126059.0491
30 | 2627871.7496 | 1125952.2886
31 | 2627757.2719 | 1126011.1508
32 | 2627767.4797 | 1125994.0827
33 | 2627753.0723 | 1126013.6602
34 | 2627765.8382 | 1125967.2188
35 | 2627900.9604 | 1126086.5021
36 | 2627745.9987 | 1126018.4013
37 | 2627737.6593 | 1126011.7411
38 | 2627741.3259 | 1126022.4836
39 | 2627729.4839 | 1126006.2752
40 | 2627737.6789 | 1126025.6697
41 | 2627724.2228 | 1126003.358
42 | 2627724.0809 | 1126035.4623
43 | 2627866.6591 | 1125937.594
44 | 2627917.0956 | 1126085.5537
45 | 2627878.6223 | 1126090.5236
46 | 2627712.5625 | 1126041.0354
47 | 2627698.8952 | 1126047.1174
48 | 2627864.8472 | 1125928.4215
49 | 2627854.029 | 1125868.7787
50 | 2627844.7851 | 1125833.0399
51 | 2627829.9828 | 1125830.5929
52 | 2627764.3758 | 1125947.0388
53 | 2627777.6462 | 1125910.9233
54 | 2627781.9827 | 1125906.0013
55 | 2627714.9202 | 1125998.7339
56 | 2627702.0981 | 1125993.323
57 | 2627822.6454 | 1125797.0314
58 | 2627822.1291 | 1125843.1736
59 | 2627753.9815 | 1126075.9887
60 | 2627679.3661 | 1125923.6152
61 | 2627687.1882 | 1125915.477
62 | 2627650.472 | 1125956.9453
63 | 2627711.212 | 1125893.0131
64 | 2627637.4149 | 1125944.4924
65 | 2627717.5275 | 1125889.2301
66 | 2627744.6929 | 1125889.8431
67 | 2627745.1913 | 1125872.8168
68 | 2627765.6413 | 1125887.8596
69 | 2627683.462 | 1125981.4592
70 | 2627686.3718 | 1125983.7651
71 | 2627766.9582 | 1125860.0337
72 | 2627696.4749 | 1125990.95
73 | 2627782.4187 | 1125905.5064
74 | 2627794.8106 | 1125892.1887
75 | 2627793.8908 | 1126093.9694
76 | 2627811.4064 | 1126096.1953
77 | 2627817.7573 | 1125856.3227
78 | 2627814.954 | 1125864.7543
79 | 2627811.7699 | 1125874.3311
80 | 2627800.7991 | 1125885.883
81 | 2627794.2989 | 1125839.7232
82 | 2627793.8573 | 1125787.1499
83 | 2627788.6074 | 1125810.3878
84 | 2627790.4539 | 1125805.1517
85 | 2627785.1003 | 1125814.681
86 | 2627765.9455 | 1125824.4932
87 | 2627774.9915 | 1125778.6362
88 | 2627765.2248 | 1125776.947
89 | 2627809.5746 | 1126006.6757

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1