## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6293-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6293-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6293-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6293-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6293-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6293-5_0_4_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_6293-5_0_4_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_6293-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_6293-5_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_6293-5_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_6293-5_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_6293-5_0_4_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_6293-5_0_4_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_6293-5_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6293-5_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6293-5_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_6293-5_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6293-5_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_6293-5_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6293-5_0_4_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_6293-5_0_4_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_6293-5_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_6293-5_0_4_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_6293-5_0_4_node_52 | 0.4 | n |  | TRUE
24 | bus_LV_6293-5_0_4_node_53 | 0.4 | n |  | TRUE
25 | bus_LV_6293-5_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_6293-5_0_4_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_6293-5_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_6293-5_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6293-5_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_6293-5_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_6293-5_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6293-5_0_4_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_6293-5_0_4_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_6293-5_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_6293-5_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_6293-5_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_6293-5_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_6293-5_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_6293-5_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_6293-5_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_6293-5_0_4_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_6293-5_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_6293-5_0_4_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_6293-5_0_4_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_6293-5_0_4_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_6293-5_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_6293-5_0_4_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_6293-5_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_6293-5_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_6293-5_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_6293-5_0_4_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_6293-5_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_6293-5_0_4_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_6293-5_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_MV_108_1_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6293-5_0_4_load_0 | 0 | 0.016955 | 0.0042493 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6293-5_0_4_load_1 | 1 | 0.013096 | 0.0032823 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6293-5_0_4_load_2 | 2 | 0.0064477 | 0.001616 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6293-5_0_4_load_3 | 3 | 0.028133 | 0.0070507 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6293-5_0_4_load_4 | 4 | 0.019661 | 0.0049275 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6293-5_0_4_load_30 | 5 | 0.009013 | 0.0022589 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6293-5_0_4_load_31 | 6 | 0.012262 | 0.0030731 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6293-5_0_4_load_5 | 7 | 0.01034 | 0.0025914 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6293-5_0_4_load_6 | 8 | 0.0073572 | 0.0018439 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6293-5_0_4_load_9 | 9 | 0.0014841 | 0.00037194 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6293-5_0_4_load_7 | 10 | 0.0055102 | 0.001381 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6293-5_0_4_load_42 | 11 | 0.0058246 | 0.0014598 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6293-5_0_4_load_8 | 13 | 0.003519 | 0.00088195 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6293-5_0_4_load_11 | 15 | 0.0025555 | 0.00064046 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6293-5_0_4_load_12 | 16 | 0.0077346 | 0.0019385 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6293-5_0_4_load_13 | 17 | 0.0027867 | 0.00069841 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6293-5_0_4_load_45 | 19 | 0.0041624 | 0.0010432 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6293-5_0_4_load_51 | 20 | 0.009427 | 0.0023626 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6293-5_0_4_load_15 | 21 | 0.0030541 | 0.00076543 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6293-5_0_4_load_52 | 23 | 0.0041514 | 0.0010404 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6293-5_0_4_load_53 | 24 | 0.0066347 | 0.0016628 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6293-5_0_4_load_35 | 25 | 0.0033661 | 0.00084362 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6293-5_0_4_load_34 | 26 | 0.0065709 | 0.0016468 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6293-5_0_4_load_36 | 27 | 0.0081669 | 0.0020468 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6293-5_0_4_load_16 | 28 | 0.0052387 | 0.0013129 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6293-5_0_4_load_17 | 29 | 0.0070966 | 0.0017786 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6293-5_0_4_load_18 | 30 | 0.0122 | 0.0030577 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6293-5_0_4_load_19 | 31 | 0.009041 | 0.0022659 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6293-5_0_4_load_39 | 32 | 0.0073775 | 0.001849 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6293-5_0_4_load_40 | 33 | 0.014637 | 0.0036684 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6293-5_0_4_load_20 | 34 | 0.0076504 | 0.0019174 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6293-5_0_4_load_21 | 35 | 0.0069186 | 0.001734 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6293-5_0_4_load_22 | 36 | 0.013371 | 0.003351 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6293-5_0_4_load_23 | 37 | 0.0080984 | 0.0020297 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6293-5_0_4_load_24 | 38 | 0.0065203 | 0.0016341 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6293-5_0_4_load_25 | 39 | 0.0067811 | 0.0016995 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6293-5_0_4_load_27 | 40 | 0.014314 | 0.0035874 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6293-5_0_4_load_28 | 42 | 0.016964 | 0.0042515 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6293-5_0_4_load_54 | 43 | 0.0087605 | 0.0021956 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6293-5_0_4_load_55 | 44 | 0.0089797 | 0.0022505 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6293-5_0_4_load_32 | 46 | 0.010065 | 0.0025226 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6293-5_0_4_load_43 | 47 | 0.0047308 | 0.0011857 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6293-5_0_4_load_44 | 48 | 0.014912 | 0.0037374 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6293-5_0_4_load_37 | 49 | 0.01278 | 0.003203 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6293-5_0_4_load_38 | 50 | 0.0068838 | 0.0017252 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6293-5_0_4_load_46 | 51 | 0.009373 | 0.0023491 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6293-5_0_4_load_47 | 52 | 0.004204 | 0.0010536 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6293-5_0_4_load_50 | 54 | 0.0043588 | 0.0010924 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6293-5_0_4_line_0 |  | 0 | 1 | 0.053242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6293-5_0_4_line_1 |  | 0 | 2 | 0.028216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6293-5_0_4_line_2 |  | 1 | 3 | 0.045782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6293-5_0_4_line_3 |  | 3 | 4 | 0.0069651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6293-5_0_4_line_4 |  | 4 | 5 | 0.021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6293-5_0_4_line_5 |  | 5 | 6 | 0.00021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6293-5_0_4_line_6 |  | 6 | 46 | 0.00026333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6293-5_0_4_line_7 |  | 7 | 8 | 0.052958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6293-5_0_4_line_8 |  | 8 | 9 | 0.0024752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6293-5_0_4_line_9 |  | 8 | 10 | 0.051456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6293-5_0_4_line_10 |  | 9 | 11 | 0.052082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_6293-5_0_4_line_11 |  | 10 | 13 | 0.031959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6293-5_0_4_line_12 |  | 11 | 12 | 0.018888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_6293-5_0_4_line_13 |  | 12 | 41 | 0.033702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_6293-5_0_4_line_14 |  | 12 | 38 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_6293-5_0_4_line_15 |  | 13 | 14 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6293-5_0_4_line_16 |  | 14 | 15 | 0.032078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6293-5_0_4_line_17 |  | 14 | 16 | 0.04495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6293-5_0_4_line_18 |  | 14 | 17 | 0.018769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6293-5_0_4_line_19 |  | 15 | 18 | 0.030934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6293-5_0_4_line_20 |  | 15 | 19 | 0.047185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6293-5_0_4_line_21 |  | 16 | 20 | 0.092898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6293-5_0_4_line_22 |  | 17 | 21 | 0.046043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6293-5_0_4_line_23 |  | 18 | 22 | 0.048866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6293-5_0_4_line_24 |  | 20 | 23 | 0.026106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6293-5_0_4_line_25 |  | 21 | 25 | 0.034963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6293-5_0_4_line_26 |  | 22 | 26 | 0.032783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6293-5_0_4_line_27 |  | 23 | 24 | 0.056842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6293-5_0_4_line_28 |  | 25 | 27 | 0.030477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6293-5_0_4_line_29 |  | 27 | 49 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6293-5_0_4_line_30 |  | 28 | 29 | 0.016014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6293-5_0_4_line_31 |  | 29 | 30 | 0.016009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6293-5_0_4_line_32 |  | 30 | 31 | 0.016815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6293-5_0_4_line_33 |  | 31 | 32 | 0.015755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6293-5_0_4_line_34 |  | 32 | 33 | 0.025105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6293-5_0_4_line_35 |  | 33 | 45 | 0.010654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6293-5_0_4_line_36 |  | 34 | 35 | 0.015434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_6293-5_0_4_line_37 |  | 34 | 36 | 0.00059319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_6293-5_0_4_line_38 |  | 35 | 37 | 0.013044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_6293-5_0_4_line_39 |  | 36 | 38 | 0.01581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_6293-5_0_4_line_40 |  | 37 | 39 | 0.020673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_6293-5_0_4_line_41 |  | 39 | 40 | 0.032858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6293-5_0_4_line_42 |  | 40 | 42 | 0.013155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6293-5_0_4_line_43 |  | 41 | 43 | 0.025532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_6293-5_0_4_line_44 |  | 41 | 44 | 0.0078317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6293-5_0_4_line_45 |  | 42 | 45 | 0.0033505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6293-5_0_4_line_46 |  | 43 | 53 | 0.045537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6293-5_0_4_line_47 |  | 46 | 47 | 0.017773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6293-5_0_4_line_48 |  | 47 | 48 | 0.029214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6293-5_0_4_line_49 |  | 48 | 53 | 0.012683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6293-5_0_4_line_50 |  | 49 | 50 | 0.0077914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6293-5_0_4_line_51 |  | 50 | 51 | 0.031367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6293-5_0_4_line_52 |  | 51 | 52 | 0.028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6293-5_0_4_line_53 |  | 52 | 54 | 0.03179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6293-5_0_4_trafo_25 | 0.63 MVA 20/0.4 kV | 55 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2633119.3718 | 1119981.0041 | 2633118.199 | 1119978.8567 | 2633113.046 | 1119973.1146 | 2633108.9658 | 1119970.1019 | 2633100.7847 | 1119967.8784 | 2633094.229 | 1119968.932 | 2633084.9257 | 1119971.6048 | 2633078.0804 | 1119974.8246 | 2633073.5828 | 1119978.2375
1 | 2633119.3718 | 1119981.0041 | 2633122.5224 | 1119986.7732 | 2633125.2132 | 1119994.1361 | 2633127.3518 | 1120002.3186 | 2633128.689 | 1120007.4951
2 | 2633062.0169 | 1120017.4696 | 2633062.0169 | 1120017.4696 | 2633059.5945 | 1120010.3862 | 2633058.8272 | 1120001.1218 | 2633058.8569 | 1119995.6859 | 2633060.2476 | 1119991.0578 | 2633064.3767 | 1119985.0995 | 2633070.9532 | 1119980.2329 | 2633073.5828 | 1119978.2375
3 | 2633062.0169 | 1120017.4696 | 2633065.6834 | 1120023.3916
4 | 2633078.0082 | 1120040.5499 | 2633074.7467 | 1120035.7816 | 2633070.4115 | 1120030.0328 | 2633066.0777 | 1120024.0284 | 2633065.6834 | 1120023.3916
5 | 2633078.0082 | 1120040.5499 | 2633078.1324 | 1120040.7315
6 | 2633078.1324 | 1120040.7315 | 2633078.281 | 1120040.9488
7 | 2633054.3629 | 1120198.762 | 2633040.6245 | 1120182.8808 | 2633015.6451 | 1120162.9458
8 | 2633015.6451 | 1120162.9458 | 2633015.6451 | 1120162.9458 | 2633017.3854 | 1120161.1857
9 | 2632995.4862 | 1120210.289 | 2633015.6451 | 1120162.9458
10 | 2633065.6293 | 1120141.5629 | 2633017.3854 | 1120161.1857
11 | 2632995.4862 | 1120210.289 | 2632993.8162 | 1120210.4732 | 2632983.3632 | 1120210.4163 | 2632974.934 | 1120201.3992 | 2632968.5169 | 1120197.5513
12 | 2633077.0947 | 1120127.1849 | 2633070.304 | 1120138.8093 | 2633065.6293 | 1120141.5629
13 | 2633077.0947 | 1120127.1849 | 2633086.602 | 1120132.3171 | 2633105.0425 | 1120146.0024
14 | 2633077.0947 | 1120127.1849 | 2633062.8046 | 1120119.4753
15 | 2632955.2104 | 1120190.9756 | 2632963.4843 | 1120194.5335 | 2632968.5169 | 1120197.5513
16 | 2632955.2104 | 1120190.9756 | 2632948.6409 | 1120186.1042 | 2632941.2056 | 1120182.9622 | 2632926.2664 | 1120177.7351
17 | 2632955.2104 | 1120190.9756 | 2632962.5003 | 1120203.8106 | 2632972.3186 | 1120225.5194 | 2632976.0166 | 1120230.6976
18 | 2632955.2104 | 1120190.9756 | 2632947.848 | 1120173.7108
19 | 2632897.9481 | 1120166.2078 | 2632908.0751 | 1120168.0415 | 2632924.1655 | 1120177 | 2632926.2664 | 1120177.7351
20 | 2632926.2664 | 1120177.7351 | 2632911.3713 | 1120222.5069
21 | 2632976.0166 | 1120230.6976 | 2632986.8546 | 1120322.9614
22 | 2632947.848 | 1120173.7108 | 2632947.4558 | 1120172.791 | 2632936.5816 | 1120156.5349 | 2632925.929 | 1120137.8231 | 2632925.204 | 1120133.9369
23 | 2632897.9481 | 1120166.2078 | 2632854.5593 | 1120143.7279
24 | 2632986.8546 | 1120322.9614 | 2632998.0143 | 1120332.0906 | 2633005.1194 | 1120341.3713
25 | 2632925.204 | 1120133.9369 | 2632918.7917 | 1120099.5669
26 | 2632854.5593 | 1120143.7279 | 2632842.0807 | 1120140.1919 | 2632832.5884 | 1120129.3795 | 2632828.2758 | 1120126.0878
27 | 2633005.1194 | 1120341.3713 | 2633005.6206 | 1120342.0259 | 2633004.7324 | 1120352.1261 | 2632988.7578 | 1120360.2878 | 2632975.5507 | 1120353.2012 | 2632965.9569 | 1120344.5008
28 | 2632908.5949 | 1120070.8954 | 2632908.5949 | 1120070.8954 | 2632918.1851 | 1120096.3158 | 2632918.7917 | 1120099.5669
29 | 2632897.121 | 1120057.9785 | 2632908.5949 | 1120070.8954
30 | 2632911.8991 | 1119990.8731 | 2632900.2233 | 1119979.9128
31 | 2632911.8991 | 1119990.8731 | 2632923.5716 | 1120001.8302
32 | 2632935.8312 | 1120013.3385 | 2632923.5716 | 1120001.8302
33 | 2632947.0132 | 1120024.4364 | 2632936.2697 | 1120013.7502 | 2632935.8312 | 1120013.3385
34 | 2632947.0132 | 1120024.4364 | 2632960.9702 | 1120038.319 | 2632964.8382 | 1120042.1143
35 | 2632972.4426 | 1120049.5759 | 2632964.8382 | 1120042.1143
36 | 2633034.7856 | 1120104.3589 | 2633048.3686 | 1120111.687
37 | 2633048.3686 | 1120111.687 | 2633048.8907 | 1120111.9687
38 | 2633034.7856 | 1120104.3589 | 2633031.9037 | 1120102.8041 | 2633024.625 | 1120096.2884
39 | 2633048.8907 | 1120111.9687 | 2633062.8046 | 1120119.4753
40 | 2633024.625 | 1120096.2884 | 2633009.2221 | 1120082.5
41 | 2632984.7404 | 1120060.5846 | 2633009.2221 | 1120082.5
42 | 2632974.939 | 1120051.8106 | 2632984.7404 | 1120060.5846
43 | 2633105.0425 | 1120146.0024 | 2633102.312 | 1120137.4388 | 2633100.6988 | 1120133.3501 | 2633099.6319 | 1120129.5424 | 2633099.9153 | 1120127.0871 | 2633102.3967 | 1120121.9314
44 | 2633105.0425 | 1120146.0024 | 2633108.956 | 1120152.7863
45 | 2632972.4426 | 1120049.5759 | 2632974.939 | 1120051.8106
46 | 2633116.8028 | 1120084.7247 | 2633119.2218 | 1120090.9966 | 2633119.7383 | 1120096.7134 | 2633120.2578 | 1120101.8855 | 2633117.7612 | 1120108.4085 | 2633114.732 | 1120113.5612 | 2633106.7857 | 1120119.2318 | 2633102.3967 | 1120121.9314
47 | 2633087.8176 | 1120055.9197 | 2633083.6876 | 1120048.6146 | 2633080.1656 | 1120043.704 | 2633078.281 | 1120040.9488
48 | 2633087.8176 | 1120055.9197 | 2633088.0124 | 1120056.2643 | 2633092.0702 | 1120063.3567 | 2633095.3192 | 1120068.8216 | 2633100.4766 | 1120073.7522 | 2633106.0487 | 1120078.2386
49 | 2633116.8028 | 1120084.7247 | 2633112.178 | 1120081.1643 | 2633107.2742 | 1120079.2254 | 2633106.0487 | 1120078.2386
50 | 2632897.121 | 1120057.9785 | 2632891.9467 | 1120052.1535
51 | 2632872.8801 | 1120027.7675 | 2632877.7752 | 1120030.9192 | 2632890.9126 | 1120050.9894 | 2632891.9467 | 1120052.1535
52 | 2632872.8801 | 1120027.7675 | 2632865.8127 | 1120023.2171 | 2632845.8434 | 1120018.3869
53 | 2632845.8434 | 1120018.3869 | 2632867.9225 | 1119995.5146

## bus_geodata
| x | y | coords
0 | 2633119.3718 | 1119981.0041
1 | 2633073.5828 | 1119978.2375
2 | 2633128.689 | 1120007.4951
3 | 2633062.0169 | 1120017.4696
4 | 2633065.6834 | 1120023.3916
5 | 2633078.0082 | 1120040.5499
6 | 2633078.1324 | 1120040.7315
7 | 2633054.3629 | 1120198.762
8 | 2633015.6451 | 1120162.9458
9 | 2633017.3854 | 1120161.1857
10 | 2632995.4862 | 1120210.289
11 | 2633065.6293 | 1120141.5629
12 | 2633077.0947 | 1120127.1849
13 | 2632968.5169 | 1120197.5513
14 | 2632955.2104 | 1120190.9756
15 | 2632926.2664 | 1120177.7351
16 | 2632976.0166 | 1120230.6976
17 | 2632947.848 | 1120173.7108
18 | 2632897.9481 | 1120166.2078
19 | 2632911.3713 | 1120222.5069
20 | 2632986.8546 | 1120322.9614
21 | 2632925.204 | 1120133.9369
22 | 2632854.5593 | 1120143.7279
23 | 2633005.1194 | 1120341.3713
24 | 2632965.9569 | 1120344.5008
25 | 2632918.7917 | 1120099.5669
26 | 2632828.2758 | 1120126.0878
27 | 2632908.5949 | 1120070.8954
28 | 2632900.2233 | 1119979.9128
29 | 2632911.8991 | 1119990.8731
30 | 2632923.5716 | 1120001.8302
31 | 2632935.8312 | 1120013.3385
32 | 2632947.0132 | 1120024.4364
33 | 2632964.8382 | 1120042.1143
34 | 2633048.3686 | 1120111.687
35 | 2633034.7856 | 1120104.3589
36 | 2633048.8907 | 1120111.9687
37 | 2633024.625 | 1120096.2884
38 | 2633062.8046 | 1120119.4753
39 | 2633009.2221 | 1120082.5
40 | 2632984.7404 | 1120060.5846
41 | 2633105.0425 | 1120146.0024
42 | 2632974.939 | 1120051.8106
43 | 2633102.3967 | 1120121.9314
44 | 2633108.956 | 1120152.7863
45 | 2632972.4426 | 1120049.5759
46 | 2633078.281 | 1120040.9488
47 | 2633087.8176 | 1120055.9197
48 | 2633106.0487 | 1120078.2386
49 | 2632897.121 | 1120057.9785
50 | 2632891.9467 | 1120052.1535
51 | 2632872.8801 | 1120027.7675
52 | 2632845.8434 | 1120018.3869
53 | 2633116.8028 | 1120084.7247
54 | 2632867.9225 | 1119995.5146
55 | 2632972.4426 | 1120049.5759

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1