## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1001-1_2_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_1001-1_2_2_node_129 | 0.4 | n |  | TRUE
2 | bus_LV_1001-1_2_2_node_127 | 0.4 | n |  | TRUE
3 | bus_LV_1001-1_2_2_node_133 | 0.4 | n |  | TRUE
4 | bus_LV_1001-1_2_2_node_134 | 0.4 | n |  | TRUE
5 | bus_LV_1001-1_2_2_node_135 | 0.4 | n |  | TRUE
6 | bus_LV_1001-1_2_2_node_101 | 0.4 | n |  | TRUE
7 | bus_LV_1001-1_2_2_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1001-1_2_2_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1001-1_2_2_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_1001-1_2_2_node_103 | 0.4 | n |  | TRUE
11 | bus_LV_1001-1_2_2_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_1001-1_2_2_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1001-1_2_2_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_1001-1_2_2_node_123 | 0.4 | n |  | TRUE
15 | bus_LV_1001-1_2_2_node_69 | 0.4 | n |  | TRUE
16 | bus_LV_1001-1_2_2_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_1001-1_2_2_node_48 | 0.4 | n |  | TRUE
18 | bus_LV_1001-1_2_2_node_119 | 0.4 | n |  | TRUE
19 | bus_LV_1001-1_2_2_node_71 | 0.4 | n |  | TRUE
20 | bus_LV_1001-1_2_2_node_122 | 0.4 | n |  | TRUE
21 | bus_LV_1001-1_2_2_node_126 | 0.4 | n |  | TRUE
22 | bus_LV_1001-1_2_2_node_105 | 0.4 | n |  | TRUE
23 | bus_LV_1001-1_2_2_node_106 | 0.4 | n |  | TRUE
24 | bus_LV_1001-1_2_2_node_107 | 0.4 | n |  | TRUE
25 | bus_LV_1001-1_2_2_node_108 | 0.4 | n |  | TRUE
26 | bus_LV_1001-1_2_2_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_1001-1_2_2_node_110 | 0.4 | n |  | TRUE
28 | bus_LV_1001-1_2_2_node_116 | 0.4 | n |  | TRUE
29 | bus_LV_1001-1_2_2_node_111 | 0.4 | n |  | TRUE
30 | bus_LV_1001-1_2_2_node_112 | 0.4 | n |  | TRUE
31 | bus_LV_1001-1_2_2_node_113 | 0.4 | n |  | TRUE
32 | bus_LV_1001-1_2_2_node_121 | 0.4 | n |  | TRUE
33 | bus_LV_1001-1_2_2_node_114 | 0.4 | n |  | TRUE
34 | bus_LV_1001-1_2_2_node_117 | 0.4 | n |  | TRUE
35 | bus_LV_1001-1_2_2_node_118 | 0.4 | n |  | TRUE
36 | bus_LV_1001-1_2_2_node_120 | 0.4 | n |  | TRUE
37 | bus_LV_1001-1_2_2_node_124 | 0.4 | n |  | TRUE
38 | bus_LV_1001-1_2_2_node_125 | 0.4 | n |  | TRUE
39 | bus_MV_0_node_46 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1001-1_2_2_load_128 | 0 | 0.0010376 | 0.00026005 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1001-1_2_2_load_129 | 1 | 0.00023986 | 6.0115e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1001-1_2_2_load_133 | 3 | 0.0007708 | 0.00019318 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1001-1_2_2_load_134 | 4 | 0.00029156 | 7.3073e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1001-1_2_2_load_135 | 5 | 0.00032587 | 8.1672e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1001-1_2_2_load_27 | 7 | 0.00023008 | 5.7663e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1001-1_2_2_load_28 | 8 | 0.0011352 | 0.00028451 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1001-1_2_2_load_30 | 11 | 0.00023841 | 5.9752e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1001-1_2_2_load_31 | 12 | 0.00026725 | 6.698e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1001-1_2_2_load_46 | 13 | 0.00040088 | 0.00010047 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1001-1_2_2_load_69 | 15 | 0.00012973 | 3.2512e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1001-1_2_2_load_47 | 16 | 0.00075993 | 0.00019046 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1001-1_2_2_load_119 | 18 | 0.00021989 | 5.5109e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1001-1_2_2_load_122 | 20 | 0.00022821 | 5.7194e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1001-1_2_2_load_126 | 21 | 0.00089851 | 0.00022519 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1001-1_2_2_load_105 | 22 | 0.0018998 | 0.00047615 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1001-1_2_2_load_106 | 23 | 0.00020306 | 5.0893e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1001-1_2_2_load_108 | 25 | 0.00022725 | 5.6953e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1001-1_2_2_load_110 | 27 | 0.00013713 | 3.4367e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1001-1_2_2_load_116 | 28 | 0.00028306 | 7.0941e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1001-1_2_2_load_111 | 29 | 0.00033564 | 8.412e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1001-1_2_2_load_112 | 30 | 0.00059901 | 0.00015013 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1001-1_2_2_load_113 | 31 | 0.001266 | 0.00031728 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1001-1_2_2_load_114 | 33 | 0.00019275 | 4.8307e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1001-1_2_2_load_117 | 34 | 0.00058433 | 0.00014645 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1001-1_2_2_load_118 | 35 | 0.00023323 | 5.8453e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1001-1_2_2_load_120 | 36 | 0.00075201 | 0.00018847 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1001-1_2_2_load_124 | 37 | 0.00023726 | 5.9463e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1001-1_2_2_load_125 | 38 | 0.0013312 | 0.00033362 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1001-1_2_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.080721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1001-1_2_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.020561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1001-1_2_2_line_2 | NAYY 4x150 SE | 2 | 38 | 0.0090955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1001-1_2_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.08923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1001-1_2_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.19845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1001-1_2_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.085067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1001-1_2_2_line_6 | NAYY 4x150 SE | 6 | 10 | 0.13823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1001-1_2_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.050287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1001-1_2_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.036964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1001-1_2_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.37135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1001-1_2_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.043657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1001-1_2_2_line_11 | NAYY 4x150 SE | 9 | 12 | 0.01419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1001-1_2_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.017192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1001-1_2_2_line_13 | NAYY 4x150 SE | 11 | 14 | 0.2762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1001-1_2_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.023337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1001-1_2_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.013352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1001-1_2_2_line_16 | NAYY 4x150 SE | 14 | 20 | 0.14657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1001-1_2_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.13022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1001-1_2_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.18158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1001-1_2_2_line_19 | NAYY 4x150 SE | 18 | 35 | 0.0032127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1001-1_2_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.054197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1001-1_2_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.15296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1001-1_2_2_line_22 | NAYY 4x150 SE | 21 | 37 | 0.016045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1001-1_2_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.011638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1001-1_2_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.028531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1001-1_2_2_line_25 | NAYY 4x150 SE | 23 | 25 | 0.025872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1001-1_2_2_line_26 | NAYY 4x150 SE | 24 | 26 | 0.04393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1001-1_2_2_line_27 | NAYY 4x150 SE | 25 | 27 | 0.030616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1001-1_2_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.029745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1001-1_2_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.00012286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1001-1_2_2_line_30 | NAYY 4x150 SE | 28 | 34 | 0.022557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1001-1_2_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.035745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1001-1_2_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.013713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1001-1_2_2_line_33 | NAYY 4x150 SE | 30 | 32 | 0.25865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1001-1_2_2_line_34 | NAYY 4x150 SE | 31 | 33 | 0.009505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1001-1_2_2_line_35 | NAYY 4x150 SE | 32 | 36 | 0.032179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1001-1_2_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.011984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1001-1_2_2_line_37 | NAYY 4x150 SE | 37 | 38 | 0.043162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1001-1_2_2_trafo_46 | 0.25 MVA 20/0.4 kV | 39 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2647052.2725 | 1206633.3523 | 2647052.9776 | 1206648.076 | 2647054.3671 | 1206653.1677 | 2647062.2601 | 1206660.9566 | 2647067.9067 | 1206669.1392 | 2647070.2959 | 1206676.6734 | 2647069.022 | 1206682.967 | 2647065.5048 | 1206689.243 | 2647059.5536 | 1206693.6764 | 2647048.9331 | 1206695.2159 | 2647048.9331 | 1206695.2159
1 | 2647030.051 | 1206688.4633 | 2647039.1547 | 1206694.1272 | 2647048.9331 | 1206695.2159
2 | 2647030.051 | 1206688.4633 | 2647031.4717 | 1206685.7396 | 2647029.7605 | 1206679.9642
3 | 2646241.2694 | 1206741.4828 | 2646242.4791 | 1206743.6031 | 2646252.6027 | 1206760.0243 | 2646255.5066 | 1206766.0391 | 2646257.0209 | 1206769.8308 | 2646258.469 | 1206774.3224 | 2646261.3904 | 1206782.9833 | 2646264.8829 | 1206790.5703 | 2646267.5905 | 1206795.4163 | 2646271.7243 | 1206801.6964 | 2646279.6015 | 1206810.6515 | 2646286.0203 | 1206817.6931
4 | 2646396.1578 | 1206982.7705 | 2646286.0203 | 1206817.6931
5 | 2646477.2525 | 1207008.2111 | 2646459.2178 | 1207004.0128 | 2646440.9814 | 1206998.3677 | 2646396.1578 | 1206982.7705
6 | 2646605.4293 | 1206972.9114 | 2646605.4044 | 1206976.1019 | 2646604.1953 | 1206979.0386 | 2646596.0937 | 1206985.2902 | 2646584.9144 | 1206991.2842 | 2646577.8912 | 1206993.8198 | 2646572.5357 | 1206995.0788 | 2646545.633 | 1206997.9152 | 2646528.6796 | 1207001.3185 | 2646503.7921 | 1207006.0941 | 2646490.6552 | 1207007.6595 | 2646477.2525 | 1207008.2111
7 | 2646650.2785 | 1206604.2818 | 2646643.7143 | 1206595.4587 | 2646642.2106 | 1206592.2785 | 2646641.5806 | 1206589.2051 | 2646642.163 | 1206585.7188 | 2646643.8328 | 1206580.2953 | 2646644.7614 | 1206575.3219 | 2646644.8307 | 1206567.4179 | 2646644.6473 | 1206565.5821 | 2646643.882 | 1206563.2859 | 2646640.5922 | 1206558.035
8 | 2646650.3505 | 1206527.6603 | 2646640.002 | 1206536.2289 | 2646637.7491 | 1206539.3909 | 2646636.5959 | 1206543.9178 | 2646636.432 | 1206547.3741 | 2646636.8681 | 1206549.9568 | 2646640.5922 | 1206558.035
9 | 2646650.2785 | 1206604.2818 | 2646605.4293 | 1206972.9114
10 | 2646650.3505 | 1206527.6603 | 2646651.4867 | 1206525.3234 | 2646653.2207 | 1206523.358 | 2646656.9666 | 1206520.8525 | 2646675.335 | 1206512.6912 | 2646678.7992 | 1206510.228 | 2646679.8529 | 1206508.7131 | 2646680.7326 | 1206506.1074 | 2646681.1669 | 1206501.1412
11 | 2646650.3505 | 1206527.6603 | 2646650.7399 | 1206530.3871 | 2646651.8259 | 1206532.5191 | 2646653.2221 | 1206533.8863 | 2646655.3762 | 1206535.5819 | 2646659.1992 | 1206537.6513
12 | 2646668.123 | 1206492.351 | 2646674.4945 | 1206493.7404 | 2646677.4124 | 1206495.0195 | 2646679.8291 | 1206497.1729 | 2646680.8261 | 1206499.0151 | 2646681.1669 | 1206501.1412
13 | 2646681.1669 | 1206501.1412 | 2646919.8173 | 1206362.0969
14 | 2646680.7873 | 1206546.4867 | 2646660.7528 | 1206538.4922 | 2646659.1992 | 1206537.6513
15 | 2646668.123 | 1206492.351 | 2646655.0771 | 1206489.5061
16 | 2646919.8173 | 1206362.0969 | 2646891.0682 | 1206423.4178 | 2646877.4567 | 1206465.8799 | 2646870.636 | 1206499.4519
17 | 2646529.0452 | 1206501.5993 | 2646530.7731 | 1206502.3688 | 2646532.641 | 1206502.728 | 2646535.2196 | 1206502.6591 | 2646537.9089 | 1206502.0353 | 2646578.4148 | 1206487.0423 | 2646588.4988 | 1206484.1081 | 2646598.0176 | 1206482.4703 | 2646607.617 | 1206482.1894 | 2646621.0488 | 1206482.9391 | 2646630.7655 | 1206484.2045 | 2646655.0771 | 1206489.5061
18 | 2646529.0452 | 1206501.5993 | 2646543.2742 | 1206320.5816
19 | 2646542.0701 | 1206317.6031 | 2646543.2742 | 1206320.5816
20 | 2646869.1539 | 1206552.8762 | 2646865.5081 | 1206533.8921 | 2646867.2365 | 1206516.1844 | 2646870.636 | 1206499.4519
21 | 2647001.9351 | 1206628.8187 | 2646869.1539 | 1206552.8762
22 | 2647001.9351 | 1206628.8187 | 2647012.1896 | 1206641.1594
23 | 2646688.1631 | 1206040.689 | 2646698.8051 | 1206045.4004
24 | 2646670.9276 | 1206021.8402 | 2646670.7914 | 1206025.6414 | 2646671.2192 | 1206029.2913 | 2646672.4321 | 1206031.7466 | 2646674.279 | 1206033.8511 | 2646677.6236 | 1206036.0229 | 2646688.1631 | 1206040.689
25 | 2646698.8051 | 1206045.4004 | 2646700.2472 | 1206046.0388 | 2646706.5525 | 1206049.8792 | 2646715.4502 | 1206057.72 | 2646719.0656 | 1206061.2503
26 | 2646710.2358 | 1206005.827 | 2646699.1054 | 1206015.0454 | 2646691.8718 | 1206019.0578 | 2646685.2766 | 1206021.163 | 2646677.909 | 1206021.8837 | 2646670.9276 | 1206021.8402
27 | 2646721.0439 | 1206090.5616 | 2646721.2643 | 1206087.3936 | 2646722.7744 | 1206078.1001 | 2646723.5271 | 1206073.2699 | 2646723.4561 | 1206070.6789 | 2646722.7939 | 1206067.8388 | 2646722.1314 | 1206065.9992 | 2646720.8649 | 1206063.599 | 2646719.0656 | 1206061.2503 | 2646719.0656 | 1206061.2503
28 | 2646710.2358 | 1206005.827 | 2646730.9786 | 1206027.1463
29 | 2646721.0439 | 1206090.5616 | 2646721.0354 | 1206090.6842
30 | 2646730.9786 | 1206027.1463 | 2646746.709 | 1206043.3139
31 | 2646721.0354 | 1206090.6842 | 2646720.6559 | 1206096.1384 | 2646721.559 | 1206102.2156 | 2646723.3501 | 1206110.4677 | 2646724.13 | 1206117.7224 | 2646725.161 | 1206120.0874 | 2646726.3976 | 1206121.4534 | 2646728.2855 | 1206122.1908 | 2646730.2257 | 1206122.0837
32 | 2646743.3826 | 1206118.2346 | 2646735.179 | 1206120.8217 | 2646730.2257 | 1206122.0837 | 2646730.2257 | 1206122.0837
33 | 2646525.8542 | 1206280.6136 | 2646730.2257 | 1206122.0837
34 | 2646752.4475 | 1206115.3759 | 2646752.4475 | 1206115.3759 | 2646743.3826 | 1206118.2346
35 | 2646525.8542 | 1206280.6136 | 2646530.2014 | 1206281.9594 | 2646534.7103 | 1206285.0074 | 2646538.263 | 1206289.7378 | 2646539.9002 | 1206297.2771 | 2646540.142 | 1206305.8283
36 | 2646542.0701 | 1206317.6031 | 2646541.5392 | 1206316.2897 | 2646540.1983 | 1206307.8188 | 2646540.142 | 1206305.8283
37 | 2647012.1896 | 1206641.1594 | 2647018.3198 | 1206648.5368 | 2647023.4122 | 1206658.5382 | 2647029.7605 | 1206679.9642

## bus_geodata
| x | y | coords
0 | 2647052.2725 | 1206633.3523
1 | 2647048.9331 | 1206695.2159
2 | 2647030.051 | 1206688.4633
3 | 2646241.2694 | 1206741.4828
4 | 2646286.0203 | 1206817.6931
5 | 2646396.1578 | 1206982.7705
6 | 2646477.2525 | 1207008.2111
7 | 2646640.5922 | 1206558.035
8 | 2646650.2785 | 1206604.2818
9 | 2646650.3505 | 1206527.6603
10 | 2646605.4293 | 1206972.9114
11 | 2646681.1669 | 1206501.1412
12 | 2646659.1992 | 1206537.6513
13 | 2646668.123 | 1206492.351
14 | 2646919.8173 | 1206362.0969
15 | 2646680.7873 | 1206546.4867
16 | 2646655.0771 | 1206489.5061
17 | 2646529.0452 | 1206501.5993
18 | 2646543.2742 | 1206320.5816
19 | 2646869.1539 | 1206552.8762
20 | 2646870.636 | 1206499.4519
21 | 2647001.9351 | 1206628.8187
22 | 2646688.1631 | 1206040.689
23 | 2646698.8051 | 1206045.4004
24 | 2646670.9276 | 1206021.8402
25 | 2646719.0656 | 1206061.2503
26 | 2646710.2358 | 1206005.827
27 | 2646721.0439 | 1206090.5616
28 | 2646730.9786 | 1206027.1463
29 | 2646721.0354 | 1206090.6842
30 | 2646730.2257 | 1206122.0837
31 | 2646743.3826 | 1206118.2346
32 | 2646525.8542 | 1206280.6136
33 | 2646752.4475 | 1206115.3759
34 | 2646746.709 | 1206043.3139
35 | 2646542.0701 | 1206317.6031
36 | 2646540.142 | 1206305.8283
37 | 2647012.1896 | 1206641.1594
38 | 2647029.7605 | 1206679.9642
39 | 2646668.123 | 1206492.351

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99591 | -0.02902 | 0.0010376 | 0.00026005
1 | 0.99603 | -0.028175 | 0.00023986 | 6.0115e-05
2 | 0.99607 | -0.027909 | 0 | 0
3 | 0.99772 | -0.016517 | 0.0007708 | 0.00019318
4 | 0.99782 | -0.015824 | 0.00029156 | 7.3073e-05
5 | 0.99812 | -0.013675 | 0.00032587 | 8.1672e-05
6 | 0.99829 | -0.012465 | 0 | 0
7 | 0.99948 | -0.0037627 | 0.00023008 | 5.7663e-05
8 | 0.9993 | -0.0050753 | 0.0011352 | 0.00028451
9 | 0.99962 | -0.0027117 | 0 | 0
10 | 0.99856 | -0.010484 | 0 | 0
11 | 0.99982 | -0.0012945 | 0.00023841 | 5.9752e-05
12 | 0.99962 | -0.0027684 | 0.00026725 | 6.698e-05
13 | 1 | 0 | -0.015911 | -0.0037591
14 | 0.99825 | -0.012444 | 0 | 0
15 | 0.99961 | -0.0027989 | 0.00012973 | 3.2512e-05
16 | 0.99985 | -0.0010367 | 0.00075993 | 0.00019046
17 | 0.99856 | -0.010164 | 0 | 0
18 | 0.99676 | -0.022901 | 0.00021989 | 5.5109e-05
19 | 0.99713 | -0.0204 | 0 | 0
20 | 0.99742 | -0.018345 | 0.00022821 | 5.7194e-05
21 | 0.99631 | -0.026191 | 0.00089851 | 0.00022519
22 | 0.99374 | -0.044236 | 0.0018998 | 0.00047615
23 | 0.99379 | -0.043909 | 0.00020306 | 5.0893e-05
24 | 0.9937 | -0.044489 | 0 | 0
25 | 0.9939 | -0.043129 | 0.00022725 | 5.6953e-05
26 | 0.99365 | -0.044878 | 0 | 0
27 | 0.99404 | -0.042135 | 0.00013713 | 3.4367e-05
28 | 0.99361 | -0.04514 | 0.00028306 | 7.0941e-05
29 | 0.99404 | -0.042131 | 0.00033564 | 8.412e-05
30 | 0.99423 | -0.040798 | 0.00059901 | 0.00015013
31 | 0.9942 | -0.041001 | 0.001266 | 0.00031728
32 | 0.99635 | -0.025776 | 0 | 0
33 | 0.99419 | -0.041019 | 0.00019275 | 4.8307e-05
34 | 0.99359 | -0.045273 | 0.00058433 | 0.00014645
35 | 0.99672 | -0.02312 | 0.00023323 | 5.8453e-05
36 | 0.99661 | -0.023906 | 0.00075201 | 0.00018847
37 | 0.99624 | -0.026653 | 0.00023726 | 5.9463e-05
38 | 0.99608 | -0.027791 | 0.0013312 | 0.00033362
39 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010376 | -0.00026005 | 0.0010377 | 0.00025905 | 1.2104e-07 | -1.0039e-06 | 0.0015503 | 0.00155 | 0.0015503 | 0.99591 | -0.02902 | 0.99603 | -0.028175 | 0.5742
1 | -0.0012776 | -0.00031916 | 0.0012777 | 0.00031892 | 4.672e-08 | -2.4964e-07 | 0.0019083 | 0.0019082 | 0.0019083 | 0.99603 | -0.028175 | 0.99607 | -0.027909 | 0.70679
2 | -0.0012777 | -0.00031892 | 0.0012777 | 0.0003188 | 2.0666e-08 | -1.1044e-07 | 0.0019082 | 0.0019082 | 0.0019082 | 0.99607 | -0.027909 | 0.99608 | -0.027791 | 0.70675
3 | -0.0007708 | -0.00019318 | 0.00077088 | 0.00019204 | 7.3557e-08 | -1.1371e-06 | 0.0011496 | 0.0011492 | 0.0011496 | 0.99772 | -0.016517 | 0.99782 | -0.015824 | 0.42577
4 | -0.0010624 | -0.00026512 | 0.0010628 | 0.00026264 | 3.1051e-07 | -2.4735e-06 | 0.001584 | 0.0015831 | 0.001584 | 0.99782 | -0.015824 | 0.99812 | -0.013675 | 0.58666
5 | -0.0013886 | -0.00034432 | 0.0013889 | 0.00034329 | 2.2716e-07 | -1.0246e-06 | 0.0020689 | 0.0020685 | 0.0020689 | 0.99812 | -0.013675 | 0.99829 | -0.012465 | 0.76626
6 | -0.0013889 | -0.00034329 | 0.0013892 | 0.00034162 | 3.6894e-07 | -1.6658e-06 | 0.0020685 | 0.0020679 | 0.0020685 | 0.99829 | -0.012465 | 0.99856 | -0.010484 | 0.76611
7 | 0.0025259 | 0.00062116 | -0.0025254 | -0.00062165 | 4.4279e-07 | -4.8862e-07 | 0.0037563 | 0.0037566 | 0.0037566 | 0.99948 | -0.0037627 | 0.9993 | -0.0050753 | 1.3913
8 | -0.0027559 | -0.00067883 | 0.0027563 | 0.00067849 | 3.8751e-07 | -3.3547e-07 | 0.0040989 | 0.0040987 | 0.0040989 | 0.99948 | -0.0037627 | 0.99962 | -0.0027117 | 1.5181
9 | 0.0013902 | 0.00033714 | -0.0013892 | -0.00034162 | 9.9007e-07 | -4.4806e-06 | 0.0020662 | 0.0020679 | 0.0020679 | 0.9993 | -0.0050753 | 0.99856 | -0.010484 | 0.76588
10 | -0.0031533 | -0.00077749 | 0.0031539 | 0.00077715 | 5.9906e-07 | -3.4202e-07 | 0.0046895 | 0.0046893 | 0.0046895 | 0.99962 | -0.0027117 | 0.99982 | -0.0012945 | 1.7368
11 | 0.00039698 | 9.9002e-05 | -0.00039698 | -9.9187e-05 | 3.0906e-09 | -1.8483e-07 | 0.00059077 | 0.00059083 | 0.00059083 | 0.99962 | -0.0027117 | 0.99962 | -0.0027684 | 0.21883
12 | -0.007379 | -0.0018275 | 0.0073803 | 0.0018278 | 1.292e-06 | 2.7143e-07 | 0.010975 | 0.010974 | 0.010975 | 0.99982 | -0.0012945 | 1 | 0 | 4.0646
13 | 0.0039867 | 0.00099062 | -0.0039807 | -0.0009919 | 6.0628e-06 | -1.2847e-06 | 0.0059304 | 0.0059317 | 0.0059317 | 0.99982 | -0.0012945 | 0.99825 | -0.012444 | 2.1969
14 | 0.00012973 | 3.2207e-05 | -0.00012973 | -3.2512e-05 | 5.4275e-10 | -3.0572e-07 | 0.000193 | 0.00019311 | 0.00019311 | 0.99962 | -0.0027684 | 0.99961 | -0.0027989 | 0.071522
15 | 0.0077311 | 0.0019312 | -0.00773 | -0.0019309 | 1.1022e-06 | 2.4879e-07 | 0.011502 | 0.011502 | 0.011502 | 1 | 0 | 0.99985 | -0.0010367 | 4.2599
16 | 0.0039807 | 0.0009919 | -0.0039775 | -0.00099258 | 3.2184e-06 | -6.7677e-07 | 0.0059317 | 0.0059323 | 0.0059323 | 0.99825 | -0.012444 | 0.99742 | -0.018345 | 2.1972
17 | 0.00697 | 0.0017405 | -0.0069613 | -0.0017388 | 8.7404e-06 | 1.6559e-06 | 0.010371 | 0.010371 | 0.010371 | 0.99985 | -0.0010367 | 0.99856 | -0.010164 | 3.8413
18 | 0.0069613 | 0.0017388 | -0.0069491 | -0.0017365 | 1.2189e-05 | 2.3169e-06 | 0.010371 | 0.010372 | 0.010372 | 0.99856 | -0.010164 | 0.99676 | -0.022901 | 3.8416
19 | 0.0067292 | 0.0016814 | -0.006729 | -0.0016814 | 2.0224e-07 | 3.5911e-08 | 0.010044 | 0.010044 | 0.010044 | 0.99676 | -0.022901 | 0.99672 | -0.02312 | 3.72
20 | -0.0037482 | -0.00093569 | 0.0037492 | 0.00093539 | 1.0575e-06 | -3.0041e-07 | 0.0055921 | 0.0055919 | 0.0055921 | 0.99713 | -0.0204 | 0.99742 | -0.018345 | 2.0712
21 | 0.0037482 | 0.00093569 | -0.0037452 | -0.00093653 | 2.9853e-06 | -8.4545e-07 | 0.0055921 | 0.0055928 | 0.0055928 | 0.99713 | -0.0204 | 0.99631 | -0.026191 | 2.0714
22 | 0.0028467 | 0.00071135 | -0.0028465 | -0.00071148 | 1.8092e-07 | -1.3935e-07 | 0.0042509 | 0.004251 | 0.004251 | 0.99631 | -0.026191 | 0.99624 | -0.026653 | 1.5744
23 | -0.0027674 | -0.00069196 | 0.0027675 | 0.00069186 | 1.2467e-07 | -1.0284e-07 | 0.0041432 | 0.0041432 | 0.0041432 | 0.99374 | -0.044236 | 0.99379 | -0.043909 | 1.5345
24 | 0.00086751 | 0.00021582 | -0.00086748 | -0.00021618 | 3.0019e-08 | -3.5808e-07 | 0.0012984 | 0.0012986 | 0.0012986 | 0.99374 | -0.044236 | 0.9937 | -0.044489 | 0.48095
25 | -0.0029705 | -0.00074275 | 0.0029709 | 0.00074254 | 3.1929e-07 | -2.1245e-07 | 0.0044472 | 0.0044471 | 0.0044472 | 0.99379 | -0.043909 | 0.9939 | -0.043129 | 1.6471
26 | 0.00086748 | 0.00021618 | -0.00086743 | -0.00021673 | 4.6232e-08 | -5.5128e-07 | 0.0012986 | 0.0012988 | 0.0012988 | 0.9937 | -0.044489 | 0.99365 | -0.044878 | 0.48103
27 | -0.0031981 | -0.00079949 | 0.0031985 | 0.00079927 | 4.3783e-07 | -2.2843e-07 | 0.0047873 | 0.0047872 | 0.0047873 | 0.9939 | -0.043129 | 0.99404 | -0.042135 | 1.7731
28 | 0.00086743 | 0.00021673 | -0.0008674 | -0.0002171 | 3.1312e-08 | -3.7324e-07 | 0.0012988 | 0.0012989 | 0.0012989 | 0.99365 | -0.044878 | 0.99361 | -0.04514 | 0.48108
29 | -0.0033357 | -0.00083363 | 0.0033357 | 0.00083363 | 1.9115e-09 | -8.5758e-10 | 0.0049925 | 0.0049925 | 0.0049925 | 0.99404 | -0.042135 | 0.99404 | -0.042131 | 1.8491
30 | 0.00058435 | 0.00014616 | -0.00058433 | -0.00014645 | 1.0778e-08 | -2.8802e-07 | 0.000875 | 0.00087511 | 0.00087511 | 0.99361 | -0.04514 | 0.99359 | -0.045273 | 0.32411
31 | -0.0036713 | -0.00091775 | 0.003672 | 0.00091755 | 6.7345e-07 | -2.0444e-07 | 0.0054949 | 0.0054947 | 0.0054949 | 0.99404 | -0.042131 | 0.99423 | -0.040798 | 2.0352
32 | 0.0014587 | 0.0003653 | -0.0014587 | -0.00036546 | 4.0785e-08 | -1.6215e-07 | 0.0021831 | 0.0021832 | 0.0021832 | 0.99423 | -0.040798 | 0.9942 | -0.041001 | 0.80859
33 | -0.0057297 | -0.001433 | 0.0057416 | 0.0014342 | 1.1864e-05 | 1.2018e-06 | 0.0085744 | 0.0085732 | 0.0085744 | 0.99423 | -0.040798 | 0.99635 | -0.025776 | 3.1757
34 | 0.00019275 | 4.8184e-05 | -0.00019275 | -4.8307e-05 | 4.9354e-10 | -1.2307e-07 | 0.00028844 | 0.00028848 | 0.00028848 | 0.9942 | -0.041001 | 0.99419 | -0.041019 | 0.10685
35 | -0.0057416 | -0.0014342 | 0.0057431 | 0.0014343 | 1.4758e-06 | 1.4843e-07 | 0.0085732 | 0.0085731 | 0.0085732 | 0.99635 | -0.025776 | 0.99661 | -0.023906 | 3.1753
36 | 0.0064958 | 0.0016229 | -0.0064951 | -0.0016228 | 7.0302e-07 | 1.1421e-07 | 0.0096958 | 0.0096959 | 0.0096959 | 0.99672 | -0.02312 | 0.99661 | -0.023906 | 3.5911
37 | 0.0026093 | 0.00065202 | -0.0026088 | -0.00065243 | 4.0895e-07 | -4.0463e-07 | 0.0038966 | 0.0038968 | 0.0038968 | 0.99624 | -0.026653 | 0.99608 | -0.027791 | 1.4432

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.016312 | 0.0038595

## res_load
| p_mw | q_mvar
0 | 0.0010376 | 0.00026005
1 | 0.00023986 | 6.0115e-05
2 | 0.0007708 | 0.00019318
3 | 0.00029156 | 7.3073e-05
4 | 0.00032587 | 8.1672e-05
5 | 0.00023008 | 5.7663e-05
6 | 0.0011352 | 0.00028451
7 | 0.00023841 | 5.9752e-05
8 | 0.00026725 | 6.698e-05
9 | 0.00040088 | 0.00010047
10 | 0.00012973 | 3.2512e-05
11 | 0.00075993 | 0.00019046
12 | 0.00021989 | 5.5109e-05
13 | 0.00022821 | 5.7194e-05
14 | 0.00089851 | 0.00022519
15 | 0.0018998 | 0.00047615
16 | 0.00020306 | 5.0893e-05
17 | 0.00022725 | 5.6953e-05
18 | 0.00013713 | 3.4367e-05
19 | 0.00028306 | 7.0941e-05
20 | 0.00033564 | 8.412e-05
21 | 0.00059901 | 0.00015013
22 | 0.001266 | 0.00031728
23 | 0.00019275 | 4.8307e-05
24 | 0.00058433 | 0.00014645
25 | 0.00023323 | 5.8453e-05
26 | 0.00075201 | 0.00018847
27 | 0.00023726 | 5.9463e-05
28 | 0.0013312 | 0.00033362

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1