## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1002-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1002-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1002-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1002-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1002-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1002-2_0_4_node_219 | 0.4 | n |  | TRUE
6 | bus_LV_1002-2_0_4_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1002-2_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1002-2_0_4_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1002-2_0_4_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_1002-2_0_4_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1002-2_0_4_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1002-2_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1002-2_0_4_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1002-2_0_4_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1002-2_0_4_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_1002-2_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1002-2_0_4_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_1002-2_0_4_node_148 | 0.4 | n |  | TRUE
19 | bus_LV_1002-2_0_4_node_140 | 0.4 | n |  | TRUE
20 | bus_LV_1002-2_0_4_node_141 | 0.4 | n |  | TRUE
21 | bus_LV_1002-2_0_4_node_142 | 0.4 | n |  | TRUE
22 | bus_LV_1002-2_0_4_node_143 | 0.4 | n |  | TRUE
23 | bus_LV_1002-2_0_4_node_70 | 0.4 | n |  | TRUE
24 | bus_LV_1002-2_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1002-2_0_4_node_144 | 0.4 | n |  | TRUE
26 | bus_LV_1002-2_0_4_node_145 | 0.4 | n |  | TRUE
27 | bus_LV_1002-2_0_4_node_146 | 0.4 | n |  | TRUE
28 | bus_LV_1002-2_0_4_node_147 | 0.4 | n |  | TRUE
29 | bus_LV_1002-2_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_1002-2_0_4_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1002-2_0_4_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_1002-2_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1002-2_0_4_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_1002-2_0_4_node_149 | 0.4 | n |  | TRUE
35 | bus_LV_1002-2_0_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_1002-2_0_4_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_1002-2_0_4_node_65 | 0.4 | n |  | TRUE
38 | bus_LV_1002-2_0_4_node_66 | 0.4 | n |  | TRUE
39 | bus_LV_1002-2_0_4_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_1002-2_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1002-2_0_4_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_1002-2_0_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_1002-2_0_4_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_1002-2_0_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1002-2_0_4_node_69 | 0.4 | n |  | TRUE
46 | bus_LV_1002-2_0_4_node_68 | 0.4 | n |  | TRUE
47 | bus_LV_1002-2_0_4_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_1002-2_0_4_node_49 | 0.4 | n |  | TRUE
49 | bus_LV_1002-2_0_4_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_1002-2_0_4_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_1002-2_0_4_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_1002-2_0_4_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_1002-2_0_4_node_93 | 0.4 | n |  | TRUE
54 | bus_LV_1002-2_0_4_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_1002-2_0_4_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_1002-2_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_1002-2_0_4_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_1002-2_0_4_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_1002-2_0_4_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_1002-2_0_4_node_215 | 0.4 | n |  | TRUE
61 | bus_LV_1002-2_0_4_node_63 | 0.4 | n |  | TRUE
62 | bus_LV_1002-2_0_4_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_1002-2_0_4_node_216 | 0.4 | n |  | TRUE
64 | bus_LV_1002-2_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1002-2_0_4_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_1002-2_0_4_node_71 | 0.4 | n |  | TRUE
67 | bus_LV_1002-2_0_4_node_217 | 0.4 | n |  | TRUE
68 | bus_LV_1002-2_0_4_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_1002-2_0_4_node_112 | 0.4 | n |  | TRUE
70 | bus_LV_1002-2_0_4_node_218 | 0.4 | n |  | TRUE
71 | bus_LV_1002-2_0_4_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_1002-2_0_4_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_1002-2_0_4_node_222 | 0.4 | n |  | TRUE
74 | bus_LV_1002-2_0_4_node_100 | 0.4 | n |  | TRUE
75 | bus_LV_1002-2_0_4_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_1002-2_0_4_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_1002-2_0_4_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_1002-2_0_4_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_1002-2_0_4_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_1002-2_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_1002-2_0_4_node_131 | 0.4 | n |  | TRUE
82 | bus_LV_1002-2_0_4_node_135 | 0.4 | n |  | TRUE
83 | bus_LV_1002-2_0_4_node_132 | 0.4 | n |  | TRUE
84 | bus_LV_1002-2_0_4_node_129 | 0.4 | n |  | TRUE
85 | bus_LV_1002-2_0_4_node_133 | 0.4 | n |  | TRUE
86 | bus_LV_1002-2_0_4_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_1002-2_0_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_1002-2_0_4_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_1002-2_0_4_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_1002-2_0_4_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_1002-2_0_4_node_86 | 0.4 | n |  | TRUE
92 | bus_LV_1002-2_0_4_node_87 | 0.4 | n |  | TRUE
93 | bus_LV_1002-2_0_4_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_1002-2_0_4_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_1002-2_0_4_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_1002-2_0_4_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_1002-2_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1002-2_0_4_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_1002-2_0_4_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_1002-2_0_4_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_1002-2_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_1002-2_0_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_1002-2_0_4_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_1002-2_0_4_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_1002-2_0_4_node_106 | 0.4 | n |  | TRUE
106 | bus_LV_1002-2_0_4_node_116 | 0.4 | n |  | TRUE
107 | bus_LV_1002-2_0_4_node_110 | 0.4 | n |  | TRUE
108 | bus_LV_1002-2_0_4_node_115 | 0.4 | n |  | TRUE
109 | bus_LV_1002-2_0_4_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_1002-2_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_1002-2_0_4_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_1002-2_0_4_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_1002-2_0_4_node_120 | 0.4 | n |  | TRUE
114 | bus_LV_1002-2_0_4_node_118 | 0.4 | n |  | TRUE
115 | bus_LV_1002-2_0_4_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_1002-2_0_4_node_117 | 0.4 | n |  | TRUE
117 | bus_LV_1002-2_0_4_node_119 | 0.4 | n |  | TRUE
118 | bus_LV_1002-2_0_4_node_121 | 0.4 | n |  | TRUE
119 | bus_LV_1002-2_0_4_node_130 | 0.4 | n |  | TRUE
120 | bus_LV_1002-2_0_4_node_125 | 0.4 | n |  | TRUE
121 | bus_LV_1002-2_0_4_node_122 | 0.4 | n |  | TRUE
122 | bus_LV_1002-2_0_4_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_1002-2_0_4_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_1002-2_0_4_node_126 | 0.4 | n |  | TRUE
125 | bus_LV_1002-2_0_4_node_127 | 0.4 | n |  | TRUE
126 | bus_LV_1002-2_0_4_node_128 | 0.4 | n |  | TRUE
127 | bus_LV_1002-2_0_4_node_136 | 0.4 | n |  | TRUE
128 | bus_LV_1002-2_0_4_node_134 | 0.4 | n |  | TRUE
129 | bus_LV_1002-2_0_4_node_138 | 0.4 | n |  | TRUE
130 | bus_LV_1002-2_0_4_node_137 | 0.4 | n |  | TRUE
131 | bus_LV_1002-2_0_4_node_139 | 0.4 | n |  | TRUE
132 | bus_MV_0_node_116 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1002-2_0_4_load_0 | 0 | 0.00023132 | 5.7974e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1002-2_0_4_load_219 | 5 | 0.00034811 | 8.7245e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1002-2_0_4_load_35 | 6 | 0.00012739 | 3.1928e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1002-2_0_4_load_32 | 7 | 7.7714e-05 | 1.9477e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1002-2_0_4_load_31 | 8 | 0.00034444 | 8.6325e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1002-2_0_4_load_25 | 9 | 0.00042137 | 0.00010561 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1002-2_0_4_load_27 | 11 | 0.00060976 | 0.00015282 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1002-2_0_4_load_28 | 12 | 4.624e-05 | 1.1589e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1002-2_0_4_load_34 | 15 | 0.00033984 | 8.5173e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1002-2_0_4_load_33 | 16 | 9.0318e-05 | 2.2636e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1002-2_0_4_load_42 | 17 | 0.00014312 | 3.587e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1002-2_0_4_load_148 | 18 | 6.2381e-05 | 1.5634e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1002-2_0_4_load_140 | 19 | 9.2049e-05 | 2.307e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1002-2_0_4_load_142 | 21 | 6.089e-05 | 1.5261e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1002-2_0_4_load_143 | 22 | 7.0267e-05 | 1.761e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1002-2_0_4_load_70 | 23 | 0.00066609 | 0.00016694 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1002-2_0_4_load_40 | 24 | 0.0017793 | 0.00044593 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1002-2_0_4_load_144 | 25 | 4.0372e-05 | 1.0118e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1002-2_0_4_load_145 | 26 | 0.00013445 | 3.3697e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1002-2_0_4_load_146 | 27 | 5.7413e-05 | 1.4389e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1002-2_0_4_load_147 | 28 | 0.00032086 | 8.0415e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1002-2_0_4_load_36 | 29 | 0.00047468 | 0.00011897 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1002-2_0_4_load_37 | 30 | 0.00016411 | 4.1129e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1002-2_0_4_load_43 | 32 | 0.00010154 | 2.5448e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1002-2_0_4_load_48 | 33 | 0.00052656 | 0.00013197 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1002-2_0_4_load_149 | 34 | 0.00013348 | 3.3453e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1002-2_0_4_load_64 | 36 | 0.00025276 | 6.3347e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1002-2_0_4_load_66 | 38 | 0.0021836 | 0.00054727 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1002-2_0_4_load_41 | 40 | 0.00011896 | 2.9813e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1002-2_0_4_load_44 | 41 | 0.00075605 | 0.00018948 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1002-2_0_4_load_45 | 43 | 0.0011387 | 0.00028539 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1002-2_0_4_load_39 | 44 | 0.00058262 | 0.00014602 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1002-2_0_4_load_69 | 45 | 0.0013766 | 0.000345 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1002-2_0_4_load_68 | 46 | 0.00036186 | 9.069e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1002-2_0_4_load_49 | 48 | 0.00015308 | 3.8364e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1002-2_0_4_load_50 | 49 | 0.00015971 | 4.0026e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1002-2_0_4_load_53 | 52 | 0.0011716 | 0.00029363 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1002-2_0_4_load_54 | 54 | 0.00019379 | 4.8568e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1002-2_0_4_load_57 | 58 | 0.0023981 | 0.00060103 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1002-2_0_4_load_215 | 60 | 0.00013067 | 3.275e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1002-2_0_4_load_63 | 61 | 0.00046678 | 0.00011699 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1002-2_0_4_load_59 | 62 | 0.00098491 | 0.00024684 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1002-2_0_4_load_216 | 63 | 0.0001306 | 3.2731e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1002-2_0_4_load_60 | 64 | 0.00077455 | 0.00019412 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1002-2_0_4_load_62 | 65 | 0.0053959 | 0.0013523 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1002-2_0_4_load_71 | 66 | 0.00013064 | 3.2743e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1002-2_0_4_load_217 | 67 | 0.00013066 | 3.2746e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1002-2_0_4_load_114 | 68 | 0.00035428 | 8.8792e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1002-2_0_4_load_112 | 69 | 0.0001096 | 2.7469e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1002-2_0_4_load_218 | 70 | 9.1355e-05 | 2.2896e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1002-2_0_4_load_72 | 71 | 0.0011491 | 0.00028799 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1002-2_0_4_load_73 | 72 | 0.00012352 | 3.0957e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1002-2_0_4_load_222 | 73 | 0.00034136 | 8.5554e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1002-2_0_4_load_100 | 74 | 0.00026876 | 6.7357e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1002-2_0_4_load_101 | 75 | 0.00065368 | 0.00016383 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1002-2_0_4_load_74 | 77 | 0.00032617 | 8.1745e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1002-2_0_4_load_78 | 79 | 0.0022108 | 0.00055409 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1002-2_0_4_load_131 | 81 | 0.0021745 | 0.00054499 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1002-2_0_4_load_135 | 82 | 0.0014726 | 0.00036908 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1002-2_0_4_load_132 | 83 | 0.002193 | 0.00054962 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1002-2_0_4_load_133 | 85 | 0.00099581 | 0.00024957 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1002-2_0_4_load_80 | 86 | 0.00018724 | 4.6927e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1002-2_0_4_load_82 | 88 | 0.00060492 | 0.00015161 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1002-2_0_4_load_85 | 89 | 0.00035301 | 8.8472e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1002-2_0_4_load_84 | 90 | 0.00022868 | 5.7313e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1002-2_0_4_load_95 | 93 | 6.7859e-05 | 1.7007e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1002-2_0_4_load_97 | 94 | 0.0006108 | 0.00015308 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1002-2_0_4_load_94 | 95 | 5.3536e-05 | 1.3417e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1002-2_0_4_load_88 | 97 | 0.00044145 | 0.00011064 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1002-2_0_4_load_89 | 98 | 0.0001121 | 2.8096e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1002-2_0_4_load_91 | 100 | 5.9373e-05 | 1.488e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1002-2_0_4_load_102 | 101 | 0.00012808 | 3.21e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1002-2_0_4_load_103 | 102 | 0.0004938 | 0.00012376 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1002-2_0_4_load_104 | 103 | 0.00052491 | 0.00013155 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1002-2_0_4_load_105 | 104 | 0.00093708 | 0.00023485 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1002-2_0_4_load_106 | 105 | 0.0001893 | 4.7442e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1002-2_0_4_load_116 | 106 | 0.00018286 | 4.583e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1002-2_0_4_load_110 | 107 | 0.00054668 | 0.00013701 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1002-2_0_4_load_115 | 108 | 0.00016032 | 4.0179e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1002-2_0_4_load_108 | 109 | 0.00016511 | 4.138e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1002-2_0_4_load_107 | 110 | 0.00015432 | 3.8677e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1002-2_0_4_load_109 | 111 | 0.0013091 | 0.00032809 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1002-2_0_4_load_111 | 112 | 0.00067813 | 0.00016996 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1002-2_0_4_load_120 | 113 | 0.00063082 | 0.0001581 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1002-2_0_4_load_118 | 114 | 0.0011275 | 0.00028258 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1002-2_0_4_load_113 | 115 | 0.00019823 | 4.9681e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1002-2_0_4_load_117 | 116 | 0.0017019 | 0.00042654 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1002-2_0_4_load_119 | 117 | 0.00088247 | 0.00022117 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1002-2_0_4_load_121 | 118 | 0.00048881 | 0.00012251 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1002-2_0_4_load_130 | 119 | 0.0011572 | 0.00029001 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1002-2_0_4_load_122 | 121 | 0.0031724 | 0.00079508 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1002-2_0_4_load_123 | 122 | 0.00066632 | 0.000167 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1002-2_0_4_load_126 | 124 | 0.0030445 | 0.00076303 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1002-2_0_4_load_127 | 125 | 0.001149 | 0.00028798 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1002-2_0_4_load_128 | 126 | 0.00090674 | 0.00022725 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1002-2_0_4_load_136 | 127 | 0.00058252 | 0.00014599 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1002-2_0_4_load_134 | 128 | 0.00048977 | 0.00012275 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1002-2_0_4_load_138 | 129 | 0.00091927 | 0.00023039 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1002-2_0_4_load_137 | 130 | 0.001515 | 0.0003797 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1002-2_0_4_load_139 | 131 | 0.00084871 | 0.00021271 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 106 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1002-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1002-2_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.058972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1002-2_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.027616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1002-2_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.039228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1002-2_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.044665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1002-2_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.099629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1002-2_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.22704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1002-2_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.057366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1002-2_0_4_line_8 | NAYY 4x150 SE | 8 | 12 | 0.031128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1002-2_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.10457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1002-2_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0021439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1002-2_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0040221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1002-2_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.11075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1002-2_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.053469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1002-2_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.15763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1002-2_0_4_line_15 | NAYY 4x150 SE | 14 | 16 | 0.14004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1002-2_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.15891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1002-2_0_4_line_17 | NAYY 4x150 SE | 15 | 18 | 0.31485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1002-2_0_4_line_18 | NAYY 4x150 SE | 17 | 23 | 0.18637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1002-2_0_4_line_19 | NAYY 4x150 SE | 17 | 24 | 0.22332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1002-2_0_4_line_20 | NAYY 4x150 SE | 18 | 28 | 0.035973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1002-2_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.16912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1002-2_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.078456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1002-2_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.14193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1002-2_0_4_line_24 | NAYY 4x150 SE | 22 | 25 | 0.0017264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1002-2_0_4_line_25 | NAYY 4x150 SE | 23 | 45 | 0.069323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1002-2_0_4_line_26 | NAYY 4x150 SE | 24 | 44 | 0.0538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1002-2_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.02647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1002-2_0_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.022197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1002-2_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.021625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1002-2_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.020451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1002-2_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.041958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1002-2_0_4_line_32 | NAYY 4x150 SE | 30 | 32 | 0.2711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1002-2_0_4_line_33 | NAYY 4x150 SE | 31 | 39 | 0.013685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1002-2_0_4_line_34 | NAYY 4x150 SE | 31 | 40 | 0.042057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1002-2_0_4_line_35 | NAYY 4x150 SE | 32 | 41 | 0.0075894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1002-2_0_4_line_36 | NAYY 4x150 SE | 32 | 42 | 0.27459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1002-2_0_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.0067426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1002-2_0_4_line_38 | NAYY 4x150 SE | 33 | 35 | 0.1427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1002-2_0_4_line_39 | NAYY 4x150 SE | 35 | 42 | 0.045875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1002-2_0_4_line_40 | NAYY 4x150 SE | 36 | 37 | 0.035987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1002-2_0_4_line_41 | NAYY 4x150 SE | 36 | 38 | 0.041267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1002-2_0_4_line_42 | NAYY 4x150 SE | 36 | 39 | 0.24698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1002-2_0_4_line_43 | NAYY 4x150 SE | 37 | 47 | 0.10626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1002-2_0_4_line_44 | NAYY 4x150 SE | 40 | 44 | 0.003567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1002-2_0_4_line_45 | NAYY 4x150 SE | 41 | 43 | 0.0143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1002-2_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.034379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1002-2_0_4_line_47 | NAYY 4x150 SE | 46 | 68 | 0.25072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1002-2_0_4_line_48 | NAYY 4x150 SE | 47 | 66 | 0.048122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1002-2_0_4_line_49 | NAYY 4x150 SE | 47 | 61 | 0.031993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1002-2_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.0089906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1002-2_0_4_line_51 | NAYY 4x150 SE | 48 | 50 | 0.015393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1002-2_0_4_line_52 | NAYY 4x150 SE | 49 | 51 | 0.036771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1002-2_0_4_line_53 | NAYY 4x150 SE | 50 | 52 | 0.055152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1002-2_0_4_line_54 | NAYY 4x150 SE | 51 | 53 | 0.16705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1002-2_0_4_line_55 | NAYY 4x150 SE | 52 | 54 | 0.029574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1002-2_0_4_line_56 | NAYY 4x150 SE | 53 | 55 | 0.12497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1002-2_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.014512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1002-2_0_4_line_58 | NAYY 4x150 SE | 55 | 73 | 0.14926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1002-2_0_4_line_59 | NAYY 4x150 SE | 55 | 99 | 0.097105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1002-2_0_4_line_60 | NAYY 4x150 SE | 56 | 57 | 0.16585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1002-2_0_4_line_61 | NAYY 4x150 SE | 56 | 58 | 0.01124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1002-2_0_4_line_62 | NAYY 4x150 SE | 57 | 59 | 0.032999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1002-2_0_4_line_63 | NAYY 4x150 SE | 57 | 60 | 0.04494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1002-2_0_4_line_64 | NAYY 4x150 SE | 59 | 61 | 0.0086235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1002-2_0_4_line_65 | NAYY 4x150 SE | 59 | 62 | 0.028777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1002-2_0_4_line_66 | NAYY 4x150 SE | 60 | 63 | 0.0025274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1002-2_0_4_line_67 | NAYY 4x150 SE | 62 | 64 | 0.027667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1002-2_0_4_line_68 | NAYY 4x150 SE | 64 | 65 | 0.014417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1002-2_0_4_line_69 | NAYY 4x150 SE | 66 | 67 | 0.0030217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1002-2_0_4_line_70 | NAYY 4x150 SE | 67 | 70 | 0.00047053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1002-2_0_4_line_71 | NAYY 4x150 SE | 68 | 69 | 0.043905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1002-2_0_4_line_72 | NAYY 4x150 SE | 69 | 115 | 0.023315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1002-2_0_4_line_73 | NAYY 4x150 SE | 71 | 72 | 0.1202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1002-2_0_4_line_74 | NAYY 4x150 SE | 72 | 73 | 0.035656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1002-2_0_4_line_75 | NAYY 4x150 SE | 74 | 75 | 0.018029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1002-2_0_4_line_76 | NAYY 4x150 SE | 75 | 76 | 0.25753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1002-2_0_4_line_77 | NAYY 4x150 SE | 76 | 87 | 0.099647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1002-2_0_4_line_78 | NAYY 4x150 SE | 77 | 78 | 0.41815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1002-2_0_4_line_79 | NAYY 4x150 SE | 78 | 79 | 0.017986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1002-2_0_4_line_80 | NAYY 4x150 SE | 78 | 80 | 0.059597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1002-2_0_4_line_81 | NAYY 4x150 SE | 79 | 81 | 0.004367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1002-2_0_4_line_82 | NAYY 4x150 SE | 80 | 82 | 0.012664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1002-2_0_4_line_83 | NAYY 4x150 SE | 80 | 83 | 0.0135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1002-2_0_4_line_84 | NAYY 4x150 SE | 82 | 84 | 0.018988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1002-2_0_4_line_85 | NAYY 4x150 SE | 83 | 85 | 0.02142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1002-2_0_4_line_86 | NAYY 4x150 SE | 84 | 127 | 0.031255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1002-2_0_4_line_87 | NAYY 4x150 SE | 84 | 120 | 0.002875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1002-2_0_4_line_88 | NAYY 4x150 SE | 85 | 128 | 0.001966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1002-2_0_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.024255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1002-2_0_4_line_90 | NAYY 4x150 SE | 86 | 88 | 0.0065908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1002-2_0_4_line_91 | NAYY 4x150 SE | 88 | 89 | 0.24626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1002-2_0_4_line_92 | NAYY 4x150 SE | 89 | 90 | 0.0076175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1002-2_0_4_line_93 | NAYY 4x150 SE | 90 | 91 | 0.052761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1002-2_0_4_line_94 | NAYY 4x150 SE | 91 | 92 | 0.14658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1002-2_0_4_line_95 | NAYY 4x150 SE | 91 | 93 | 0.14088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1002-2_0_4_line_96 | NAYY 4x150 SE | 92 | 94 | 0.069458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1002-2_0_4_line_97 | NAYY 4x150 SE | 93 | 95 | 0.039875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1002-2_0_4_line_98 | NAYY 4x150 SE | 95 | 96 | 0.052416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1002-2_0_4_line_99 | NAYY 4x150 SE | 96 | 97 | 0.13699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1002-2_0_4_line_100 | NAYY 4x150 SE | 97 | 98 | 0.020652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1002-2_0_4_line_101 | NAYY 4x150 SE | 97 | 99 | 0.08835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1002-2_0_4_line_102 | NAYY 4x150 SE | 98 | 100 | 0.028949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1002-2_0_4_line_103 | NAYY 4x150 SE | 101 | 102 | 0.0091129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1002-2_0_4_line_104 | NAYY 4x150 SE | 101 | 103 | 0.016978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1002-2_0_4_line_105 | NAYY 4x150 SE | 102 | 104 | 0.016433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1002-2_0_4_line_106 | NAYY 4x150 SE | 103 | 105 | 0.0061614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1002-2_0_4_line_107 | NAYY 4x150 SE | 104 | 106 | 0.0064305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1002-2_0_4_line_108 | NAYY 4x150 SE | 105 | 107 | 0.017653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1002-2_0_4_line_109 | NAYY 4x150 SE | 106 | 108 | 0.014551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_1002-2_0_4_line_110 | NAYY 4x150 SE | 107 | 109 | 0.0040833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1002-2_0_4_line_111 | NAYY 4x150 SE | 108 | 115 | 0.023921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_1002-2_0_4_line_112 | NAYY 4x150 SE | 109 | 110 | 0.0211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1002-2_0_4_line_113 | NAYY 4x150 SE | 110 | 111 | 0.00167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1002-2_0_4_line_114 | NAYY 4x150 SE | 111 | 112 | 0.048947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1002-2_0_4_line_115 | NAYY 4x150 SE | 112 | 113 | 0.029168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1002-2_0_4_line_116 | NAYY 4x150 SE | 113 | 114 | 0.024653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1002-2_0_4_line_117 | NAYY 4x150 SE | 114 | 116 | 0.006493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1002-2_0_4_line_118 | NAYY 4x150 SE | 116 | 117 | 0.029321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1002-2_0_4_line_119 | NAYY 4x150 SE | 117 | 118 | 0.041178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1002-2_0_4_line_120 | NAYY 4x150 SE | 118 | 119 | 0.024751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1002-2_0_4_line_121 | NAYY 4x150 SE | 119 | 120 | 0.009719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1002-2_0_4_line_122 | NAYY 4x150 SE | 120 | 122 | 0.036048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1002-2_0_4_line_123 | NAYY 4x150 SE | 121 | 122 | 0.0095125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1002-2_0_4_line_124 | NAYY 4x150 SE | 121 | 123 | 0.0073585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1002-2_0_4_line_125 | NAYY 4x150 SE | 123 | 124 | 0.03227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1002-2_0_4_line_126 | NAYY 4x150 SE | 123 | 125 | 0.010814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1002-2_0_4_line_127 | NAYY 4x150 SE | 125 | 126 | 0.019173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1002-2_0_4_line_128 | NAYY 4x150 SE | 128 | 129 | 0.01867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1002-2_0_4_line_129 | NAYY 4x150 SE | 129 | 130 | 0.0069135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1002-2_0_4_line_130 | NAYY 4x150 SE | 130 | 131 | 0.022053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1002-2_0_4_trafo_116 | 0.25 MVA 20/0.4 kV | 132 | 106 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2649612.0353 | 1206033.255 | 2649602.5236 | 1206046.6727 | 2649595.0549 | 1206062.2642 | 2649592.7551 | 1206068.0319
1 | 2649612.0353 | 1206033.255 | 2649613.3926 | 1206035.5788 | 2649614.8933 | 1206038.9487 | 2649615.6396 | 1206041.5787 | 2649616.3616 | 1206046.2207 | 2649616.6719 | 1206053.7277 | 2649615.9114 | 1206080.259 | 2649616.0336 | 1206086.6081 | 2649616.3212 | 1206091.3466
2 | 2649588.4853 | 1206019.9518 | 2649593.5879 | 1206020.9503 | 2649598.7661 | 1206022.9166 | 2649603.3911 | 1206025.5566 | 2649607.4954 | 1206028.6146 | 2649612.0353 | 1206033.255
3 | 2649621.879 | 1205996.382 | 2649621.2777 | 1206008.3284 | 2649619.4897 | 1206019.3978 | 2649618.0452 | 1206024.8334 | 2649616.0347 | 1206028.8079 | 2649612.0353 | 1206033.255
4 | 2649586.1311 | 1206112.0413 | 2649587.0327 | 1206104.2109 | 2649590.1371 | 1206096.7101 | 2649593.2077 | 1206093.2891 | 2649595.7422 | 1206091.2201 | 2649599.6311 | 1206089.9961 | 2649603.3052 | 1206089.9154 | 2649609.0618 | 1206090.9083 | 2649616.3212 | 1206091.3466
5 | 2649588.4853 | 1206019.9518 | 2649587.8287 | 1206017.5116 | 2649586.3526 | 1206015.765 | 2649583.8874 | 1206014.0547 | 2649581.2727 | 1206012.9434 | 2649562.4302 | 1206008.818 | 2649546.3592 | 1206005.2382 | 2649519.7187 | 1205997.7241 | 2649507.341 | 1205992.6631 | 2649496.4805 | 1205987.1769
6 | 2649703.3643 | 1205784.4642 | 2649621.879 | 1205996.382
7 | 2649703.3643 | 1205784.4642 | 2649728.9 | 1205733.0954
8 | 2649742.7562 | 1205705.2216 | 2649728.9 | 1205733.0954
9 | 2649744.5466 | 1205701.6199 | 2649747.818 | 1205701.5138 | 2649749.8986 | 1205700.0858 | 2649752.2829 | 1205696.9149 | 2649762.8333 | 1205682.1831 | 2649766.929 | 1205678.0815 | 2649769.8579 | 1205676.1826 | 2649773.4995 | 1205675.457 | 2649778.167 | 1205675.7627 | 2649788.0855 | 1205678.4469 | 2649793.8373 | 1205680.9741 | 2649801.805 | 1205685.9322 | 2649804.959 | 1205688.9492 | 2649805.7508 | 1205691.6017 | 2649805.6657 | 1205695.4144 | 2649798.82 | 1205716.4487
10 | 2649798.1565 | 1205718.4874 | 2649798.82 | 1205716.4487
11 | 2649744.5466 | 1205701.6199 | 2649742.7562 | 1205705.2216
12 | 2649744.5466 | 1205701.6199 | 2649774.2499 | 1205639.2756 | 2649784.6719 | 1205598.9056
13 | 2649784.6719 | 1205598.9056 | 2649788.699 | 1205605.7765 | 2649792.0114 | 1205608.9726 | 2649795.9993 | 1205610.5068 | 2649802.6046 | 1205611.9404 | 2649811.6033 | 1205605.4561 | 2649826.9887 | 1205594.6893
14 | 2649826.9887 | 1205594.6893 | 2649842.7459 | 1205583.1362 | 2649852.4593 | 1205574.868 | 2649862.6063 | 1205564.7801 | 2649872.936 | 1205552.8594 | 2649881.1371 | 1205541.7214 | 2649888.3357 | 1205530.4083 | 2649897.3777 | 1205515.1194 | 2649906.482 | 1205496.0288 | 2649914.084 | 1205477.4148 | 2649917.0031 | 1205468.9063
15 | 2649826.9887 | 1205594.6893 | 2649885.4619 | 1205597.6233 | 2649889.9353 | 1205599.3172 | 2649892.9935 | 1205602.8892 | 2649894.3027 | 1205606.4133 | 2649895.2662 | 1205611.2575 | 2649896.4161 | 1205671.1686 | 2649897.955 | 1205674.1812
16 | 2649917.0031 | 1205468.9063 | 2649825.3741 | 1205339.0704
17 | 2649917.0031 | 1205468.9063 | 2650230.6628 | 1205496.3007
18 | 2649825.3741 | 1205339.0704 | 2649641.4786 | 1205369.3629
19 | 2649825.3741 | 1205339.0704 | 2649837.8102 | 1205116.0942
20 | 2650230.717 | 1205532.2739 | 2650230.6628 | 1205496.3007
21 | 2650326.4735 | 1205715.7457 | 2650336.6717 | 1205711.3735 | 2650341.5265 | 1205708.4016 | 2650343.24 | 1205706.3371 | 2650344.9677 | 1205702.5939 | 2650345.1363 | 1205698.8376 | 2650340.9509 | 1205663.0037 | 2650336.9961 | 1205648.5287 | 2650330.1426 | 1205614.3066 | 2650329.228 | 1205601.8917 | 2650332.9358 | 1205597.8539 | 2650338.2401 | 1205597.4984 | 2650347.5858 | 1205602.2577 | 2650360.5476 | 1205612.9398 | 2650362.6926 | 1205617.7341
22 | 2650326.4735 | 1205715.7457 | 2650338.1854 | 1205723.9936 | 2650344.472 | 1205727.104 | 2650351.7034 | 1205729.1216 | 2650360.5798 | 1205730.8752 | 2650369.0055 | 1205731.0575 | 2650377.0325 | 1205731.6255 | 2650381.4568 | 1205732.7968 | 2650384.2344 | 1205734.4212 | 2650385.9736 | 1205736.5259 | 2650387.8922 | 1205740.8002 | 2650388.8729 | 1205745.3666 | 2650388.8754 | 1205749.5735
23 | 2650326.4735 | 1205715.7457 | 2650303.3769 | 1205687.4681 | 2650272.6591 | 1205650.1546 | 2650267.4995 | 1205642.3511 | 2650264.2709 | 1205636.465 | 2650252.6434 | 1205611.8195 | 2650247.1757 | 1205603.5687 | 2650244.7371 | 1205600.5577
24 | 2650243.6505 | 1205599.2161 | 2650244.7371 | 1205600.5577
25 | 2649641.4786 | 1205369.3629 | 2649632.4652 | 1205386.0716 | 2649619.6776 | 1205411.8915 | 2649617.2448 | 1205414.495 | 2649607.934 | 1205418.2532 | 2649600.6042 | 1205421.258
26 | 2649826.5904 | 1205063.5076 | 2649833.9161 | 1205093.5677 | 2649837.8102 | 1205116.0942
27 | 2650243.6505 | 1205599.2161 | 2650236.7045 | 1205590.6399 | 2650234.4409 | 1205586.6741 | 2650233.0738 | 1205581.9154 | 2650232.8317 | 1205576.0045
28 | 2650232.8317 | 1205576.0045 | 2650232.8151 | 1205575.5984 | 2650232.2946 | 1205553.8143
29 | 2650232.2946 | 1205553.8143 | 2650232.1963 | 1205549.7004 | 2650230.7236 | 1205536.6916 | 2650230.717 | 1205532.2739
30 | 2649850.534 | 1205031.8426 | 2649850.8935 | 1205031.6734 | 2649854.0565 | 1205019.0814 | 2649852.7686 | 1205012.1287
31 | 2649812.7578 | 1205020.2043 | 2649829.4779 | 1205031.0834 | 2649844.9521 | 1205034.4699 | 2649850.534 | 1205031.8426
32 | 2649850.534 | 1205031.8426 | 2650115.6714 | 1205088.3655
33 | 2649807.2714 | 1205007.6624 | 2649812.7578 | 1205020.2043
34 | 2649812.7578 | 1205020.2043 | 2649820.1625 | 1205037.1314 | 2649825.7458 | 1205060.042
35 | 2650115.6714 | 1205088.3655 | 2650115.0774 | 1205095.6981 | 2650115.0316 | 1205095.9263
36 | 2650115.6714 | 1205088.3655 | 2650125.2161 | 1204813.9421
37 | 2650033.9759 | 1204687.0977 | 2650035.1794 | 1204691.4055 | 2650036.2565 | 1204693.4036
38 | 2650079.2666 | 1204811.6111 | 2650088.7263 | 1204795.6922 | 2650092.9065 | 1204784.3318 | 2650092.0493 | 1204765.0023 | 2650090.6977 | 1204755.6411 | 2650072.6798 | 1204739.8254 | 2650061.1492 | 1204724.1975 | 2650055.3552 | 1204716.6224 | 2650046.3802 | 1204708.2868 | 2650040.333 | 1204700.9653 | 2650036.2565 | 1204693.4036
39 | 2650079.2666 | 1204811.6111 | 2650125.2161 | 1204813.9421
40 | 2649661.3757 | 1204784.2634 | 2649658.2526 | 1204787.5171 | 2649655.0458 | 1204790.7812 | 2649652.5579 | 1204797.2309 | 2649652.1382 | 1204802.8752 | 2649652.6319 | 1204811.2063 | 2649651.6044 | 1204814.9333 | 2649650.5564 | 1204816.7725
41 | 2649620.2927 | 1204831.5717 | 2649625.6232 | 1204835.4738 | 2649632.6013 | 1204836.0876 | 2649637.4108 | 1204834.9491 | 2649642.9353 | 1204830.1478 | 2649650.5564 | 1204816.7725
42 | 2649650.5564 | 1204816.7725 | 2649807.2714 | 1205007.6624
43 | 2649585.0079 | 1204710.1642 | 2649661.3757 | 1204784.2634
44 | 2649826.5904 | 1205063.5076 | 2649825.7458 | 1205060.042
45 | 2650115.0316 | 1205095.9263 | 2650113.6087 | 1205103.0233 | 2650111.6197 | 1205109.7995
46 | 2649573.8221 | 1205430.7472 | 2649575.6035 | 1205431.5704 | 2649581.8917 | 1205436.4031 | 2649586.3673 | 1205432.3601 | 2649589.5693 | 1205427.8063 | 2649597.142 | 1205422.6773 | 2649600.6042 | 1205421.258
47 | 2649354.0118 | 1205310.1435 | 2649573.8221 | 1205430.7472
48 | 2649585.0079 | 1204710.1642 | 2649596.7609 | 1204706.4929 | 2649615.0997 | 1204699.4077 | 2649629.6129 | 1204692.3253
49 | 2649585.0079 | 1204710.1642 | 2649564.4008 | 1204685.6922
50 | 2649399.0933 | 1204415.3533 | 2649398.4427 | 1204406.3862
51 | 2649400.2071 | 1204430.7056 | 2649399.0933 | 1204415.3533
52 | 2649395.7819 | 1204369.7115 | 2649398.4427 | 1204406.3862
53 | 2649400.2071 | 1204430.7056 | 2649402.4035 | 1204446.5996 | 2649405.061 | 1204458.2505 | 2649408.811 | 1204469.3434 | 2649413.2685 | 1204479.5195 | 2649415.2548 | 1204483.3757
54 | 2649395.7819 | 1204369.7115 | 2649390.8036 | 1204366.3907 | 2649358.805 | 1204312.2173 | 2649340.7248 | 1204301.7175 | 2649326.6457 | 1204300.4783 | 2649301.2986 | 1204295.6886 | 2649292.0306 | 1204295.9123 | 2649275.9043 | 1204296.602 | 2649270.3389 | 1204295.2775 | 2649265.7782 | 1204291.1153
55 | 2649430.3455 | 1204508.7756 | 2649428.5744 | 1204506.1948 | 2649419.7673 | 1204492.1361 | 2649415.2548 | 1204483.3757
56 | 2649265.7782 | 1204291.1153 | 2649252.3935 | 1204308.9931 | 2649241.6498 | 1204307.3592 | 2649212.0182 | 1204325.8146 | 2649181.3903 | 1204354.4235 | 2649171.8222 | 1204366.1626
57 | 2649438.5566 | 1204520.7413 | 2649430.3455 | 1204508.7756
58 | 2649129.2278 | 1204465.1028 | 2649164.7156 | 1204443.0152 | 2649187.2247 | 1204434.8624 | 2649199.7618 | 1204423.7814 | 2649201.8859 | 1204413.4262 | 2649190.4618 | 1204389.1293 | 2649185.9506 | 1204383.5778 | 2649179.1349 | 1204375.1836 | 2649171.8222 | 1204366.1626
59 | 2649145.6786 | 1204289.9258 | 2649155.4775 | 1204288.9614 | 2649161.5438 | 1204289.5227 | 2649164.8496 | 1204290.8729 | 2649166.9156 | 1204293.1246 | 2649167.8567 | 1204295.2446 | 2649167.553 | 1204299.7892 | 2649166.5448 | 1204307.6744 | 2649165.7653 | 1204315.4947 | 2649165.6129 | 1204334.0041 | 2649168.8474 | 1204362.5027 | 2649171.8222 | 1204366.1626
60 | 2649438.5566 | 1204520.7413 | 2649486.1514 | 1204590.142 | 2649537.5656 | 1204653.827
61 | 2649438.5566 | 1204520.7413 | 2649428.6509 | 1204526.0525
62 | 2649537.5656 | 1204653.827 | 2649558.8462 | 1204679.0958
63 | 2649537.5656 | 1204653.827 | 2649548.5791 | 1204637.52 | 2649555.6929 | 1204628.2292 | 2649562.5515 | 1204620.3482 | 2649564.8878 | 1204618.2906
64 | 2649558.8462 | 1204679.0958 | 2649564.4008 | 1204685.6922
65 | 2649558.8462 | 1204679.0958 | 2649555.9059 | 1204679.5717 | 2649553.481 | 1204679.3515 | 2649550.5988 | 1204678.327 | 2649548.0493 | 1204676.6271 | 2649535.7962 | 1204664.4989
66 | 2649564.8878 | 1204618.2906 | 2649566.7846 | 1204616.6202
67 | 2649535.7962 | 1204664.4989 | 2649533.902 | 1204662.624 | 2649527.8122 | 1204657.6039 | 2649522.9897 | 1204654.8068 | 2649513.8611 | 1204652.0518 | 2649511.905 | 1204651.6397
68 | 2649497.5841 | 1204650.8385 | 2649507.5429 | 1204650.7209 | 2649511.905 | 1204651.6397
69 | 2649629.6129 | 1204692.3253 | 2649632.3285 | 1204691.0001
70 | 2649632.7514 | 1204690.7937 | 2649632.3285 | 1204691.0001
71 | 2649354.0118 | 1205310.1435 | 2649352.4107 | 1205297.7119 | 2649348.7908 | 1205291.1894 | 2649344.0847 | 1205279.8662 | 2649341.2205 | 1205268.5746
72 | 2649341.2205 | 1205268.5746 | 2649336.4236 | 1205249.6632 | 2649335.2347 | 1205246.0486
73 | 2649123.2331 | 1204500.2515 | 2649150.3145 | 1204516.0722 | 2649165.6229 | 1204522.2573 | 2649180.6662 | 1204527.3618 | 2649236.0967 | 1204538.0132
74 | 2649129.2278 | 1204465.1028 | 2649123.2331 | 1204500.2515
75 | 2648801.6353 | 1204750.2499 | 2648811.5147 | 1204739.3465 | 2648814.2371 | 1204737.4545
76 | 2648584.6159 | 1204611.6017 | 2648801.6353 | 1204750.2499
77 | 2648584.6159 | 1204611.6017 | 2648578.9464 | 1204601.5832 | 2648574.4426 | 1204593.1973 | 2648579.1212 | 1204592.2459 | 2648582.4807 | 1204590.7279 | 2648585.9351 | 1204587.8432 | 2648589.0303 | 1204584.2107 | 2648612.1387 | 1204544.32 | 2648619.9244 | 1204531.7539
78 | 2649144.0923 | 1205257.4162 | 2648920.8889 | 1205611.0147
79 | 2649144.0923 | 1205257.4162 | 2649141.9133 | 1205253.2291 | 2649132.9497 | 1205243.4498 | 2649132.9497 | 1205243.4498
80 | 2649165.5974 | 1205203.6175 | 2649163.9083 | 1205209.2179 | 2649161.296 | 1205218.8465 | 2649159.9308 | 1205231.3091 | 2649158.3463 | 1205238.9894 | 2649156.1655 | 1205243.3295 | 2649150.2889 | 1205250.3408 | 2649144.0923 | 1205257.4162
81 | 2649129.2347 | 1205241.1543 | 2649132.9497 | 1205243.4498
82 | 2649165.5974 | 1205203.6175 | 2649167.6563 | 1205199.2875 | 2649173.3135 | 1205193.8178
83 | 2649165.5974 | 1205203.6175 | 2649153.9834 | 1205196.736
84 | 2649189.9096 | 1205184.9067 | 2649180.332 | 1205188.7301 | 2649173.7904 | 1205193.3567 | 2649173.3135 | 1205193.8178
85 | 2649153.9834 | 1205196.736 | 2649148.2252 | 1205193.3242 | 2649141.1216 | 1205188.5964 | 2649136.2335 | 1205184.793
86 | 2649189.9096 | 1205184.9067 | 2649186.2924 | 1205178.9513 | 2649178.7645 | 1205171.2516 | 2649168.123 | 1205162.9136
87 | 2649192.6404 | 1205183.9842 | 2649189.9096 | 1205184.9067
88 | 2649136.2335 | 1205184.793 | 2649134.6819 | 1205183.5857
89 | 2648619.9244 | 1204531.7539 | 2648627.7441 | 1204534.6303 | 2648631.9803 | 1204535.6987 | 2648635.9472 | 1204536.2091 | 2648639.5377 | 1204535.2933 | 2648643.3028 | 1204534.4918
90 | 2648649.7492 | 1204533.1196 | 2648643.3028 | 1204534.4918
91 | 2648803.3088 | 1204340.6051 | 2648649.7492 | 1204533.1196
92 | 2648803.3088 | 1204340.6051 | 2648808.5284 | 1204335.0569
93 | 2648857.0321 | 1204316.5857 | 2648847.285 | 1204319.5967 | 2648829.3251 | 1204323.1186 | 2648820.8931 | 1204326.2515 | 2648815.4895 | 1204329.3091 | 2648810.1696 | 1204333.3124 | 2648808.5284 | 1204335.0569
94 | 2648727.9913 | 1204287.7712 | 2648726.6448 | 1204300.8121 | 2648741.7442 | 1204300.0904 | 2648780.579 | 1204296.6275 | 2648788.6938 | 1204296.9383 | 2648797.3655 | 1204297.9875 | 2648805.2765 | 1204299.9644 | 2648825.6042 | 1204306.4675 | 2648857.0321 | 1204316.5857
95 | 2648857.0321 | 1204316.5857 | 2648908.8278 | 1204185.5765
96 | 2648727.9913 | 1204287.7712 | 2648728.2023 | 1204274.9544 | 2648726.9082 | 1204267.5952 | 2648724.1551 | 1204259.09 | 2648719.0676 | 1204247.6531 | 2648711.1878 | 1204230.6457 | 2648706.5066 | 1204222.9987
97 | 2648908.8278 | 1204185.5765 | 2648913.612 | 1204188.1189 | 2648929.1607 | 1204194.8167 | 2648939.9056 | 1204200.0521 | 2648944.5359 | 1204203.1571
98 | 2648974.2891 | 1204245.0153 | 2648968.235 | 1204229.9681 | 2648964.9672 | 1204223.9712 | 2648961.1188 | 1204218.2697 | 2648954.3905 | 1204211.2216 | 2648950.8637 | 1204208.0465 | 2648945.2095 | 1204203.6087 | 2648944.5359 | 1204203.1571
99 | 2649107.7501 | 1204214.1359 | 2648974.2891 | 1204245.0153
100 | 2649107.7501 | 1204214.1359 | 2649107.9777 | 1204213.7275 | 2649112.526 | 1204210.1628 | 2649116.7474 | 1204210.2754 | 2649123.0661 | 1204211.6059 | 2649126.639 | 1204212.6618
101 | 2649145.6786 | 1204289.9258 | 2649138.4521 | 1204263.9292 | 2649135.0731 | 1204253.9067 | 2649129.6521 | 1204244.2566 | 2649114.103 | 1204229.3313 | 2649107.0187 | 1204220.2567 | 2649106.14 | 1204217.0254 | 2649107.7501 | 1204214.1359
102 | 2649154.7169 | 1204219.604 | 2649147.0491 | 1204217.6621 | 2649137.1898 | 1204215.7799 | 2649126.639 | 1204212.6618
103 | 2649310.8147 | 1205245.8242 | 2649310.7845 | 1205244.7932 | 2649310.0942 | 1205236.7413
104 | 2649310.8147 | 1205245.8242 | 2649311.1822 | 1205258.3488 | 2649310.765 | 1205262.7775
105 | 2649309.6625 | 1205220.3809 | 2649309.1124 | 1205225.2903 | 2649310.0942 | 1205236.7413
106 | 2649310.187 | 1205268.9118 | 2649310.765 | 1205262.7775
107 | 2649314.4354 | 1205216.2624 | 2649314.4354 | 1205216.2624 | 2649312.2817 | 1205217.3119 | 2649309.6625 | 1205220.3809 | 2649309.6625 | 1205220.3809
108 | 2649310.187 | 1205268.9118 | 2649308.5312 | 1205286.4868
109 | 2649325.4489 | 1205224.283 | 2649324.8156 | 1205223.0297 | 2649321.7544 | 1205218.8354 | 2649318.038 | 1205216.6034 | 2649314.4354 | 1205216.2624
110 | 2649308.1482 | 1205290.5521 | 2649308.5312 | 1205286.4868
111 | 2649335.2347 | 1205246.0486 | 2649332.9732 | 1205239.1731 | 2649325.4489 | 1205224.283
112 | 2649305.404 | 1205311.4237 | 2649305.8161 | 1205310.379 | 2649306.8136 | 1205304.7173 | 2649308.1482 | 1205290.5521
113 | 2649305.404 | 1205311.4237 | 2649304.7911 | 1205312.9772
114 | 2649304.7911 | 1205312.9772 | 2649303.2368 | 1205316.9171 | 2649300.9207 | 1205321.0559 | 2649298.4356 | 1205323.5591 | 2649294.316 | 1205325.0371 | 2649289.8879 | 1205325.1895 | 2649286.1622 | 1205324.0915 | 2649281.9503 | 1205321.0884 | 2649279.5244 | 1205316.4101 | 2649275.9853 | 1205303.5819
115 | 2649268.0787 | 1205275.5095 | 2649269.0814 | 1205278.5576 | 2649275.9853 | 1205303.5819
116 | 2649268.0787 | 1205275.5095 | 2649261.802 | 1205256.4293 | 2649259.851 | 1205252.2997
117 | 2649257.0773 | 1205246.429 | 2649257.0773 | 1205246.429 | 2649259.851 | 1205252.2997
118 | 2649241.8871 | 1205221.4086 | 2649245.5832 | 1205228.9908 | 2649257.0773 | 1205246.429
119 | 2649241.8871 | 1205221.4086 | 2649237.4974 | 1205212.4035 | 2649232.1485 | 1205194.1377 | 2649229.4739 | 1205188.2567 | 2649226.5382 | 1205184.5081 | 2649225.7751 | 1205184.0216
120 | 2649225.7751 | 1205184.0216 | 2649221.9452 | 1205181.5797 | 2649212.2738 | 1205180.1659 | 2649203.294 | 1205180.6589 | 2649201.9179 | 1205181.0884
121 | 2649192.6404 | 1205183.9842 | 2649201.9179 | 1205181.0884
122 | 2649192.6404 | 1205183.9842 | 2649198.6856 | 1205194.3734 | 2649202.8198 | 1205206.8257 | 2649205.3262 | 1205217.4414 | 2649205.3262 | 1205217.4414
123 | 2649205.8735 | 1205226.9254 | 2649205.9625 | 1205225.14 | 2649205.3262 | 1205217.4414
124 | 2649205.507 | 1205234.2748 | 2649205.8735 | 1205226.9254
125 | 2649205.507 | 1205234.2748 | 2649188.3477 | 1205261.6048
126 | 2649205.507 | 1205234.2748 | 2649204.4982 | 1205245.0421
127 | 2649204.4982 | 1205245.0421 | 2649204.256 | 1205247.6278 | 2649201.1264 | 1205263.9058
128 | 2649134.6819 | 1205183.5857 | 2649128.6734 | 1205178.9106 | 2649121.3408 | 1205170.6347
129 | 2649117.1235 | 1205165.1584 | 2649120.9635 | 1205170.2089 | 2649121.3408 | 1205170.6347
130 | 2649117.1235 | 1205165.1584 | 2649103.7757 | 1205147.603

## bus_geodata
| x | y | coords
0 | 2649592.7551 | 1206068.0319
1 | 2649612.0353 | 1206033.255
2 | 2649616.3212 | 1206091.3466
3 | 2649588.4853 | 1206019.9518
4 | 2649621.879 | 1205996.382
5 | 2649586.1311 | 1206112.0413
6 | 2649496.4805 | 1205987.1769
7 | 2649703.3643 | 1205784.4642
8 | 2649728.9 | 1205733.0954
9 | 2649798.82 | 1205716.4487
10 | 2649744.5466 | 1205701.6199
11 | 2649798.1565 | 1205718.4874
12 | 2649742.7562 | 1205705.2216
13 | 2649784.6719 | 1205598.9056
14 | 2649826.9887 | 1205594.6893
15 | 2649917.0031 | 1205468.9063
16 | 2649897.955 | 1205674.1812
17 | 2649825.3741 | 1205339.0704
18 | 2650230.6628 | 1205496.3007
19 | 2650362.6926 | 1205617.7341
20 | 2650326.4735 | 1205715.7457
21 | 2650388.8754 | 1205749.5735
22 | 2650244.7371 | 1205600.5577
23 | 2649641.4786 | 1205369.3629
24 | 2649837.8102 | 1205116.0942
25 | 2650243.6505 | 1205599.2161
26 | 2650232.8317 | 1205576.0045
27 | 2650232.2946 | 1205553.8143
28 | 2650230.717 | 1205532.2739
29 | 2649852.7686 | 1205012.1287
30 | 2649850.534 | 1205031.8426
31 | 2649812.7578 | 1205020.2043
32 | 2650115.6714 | 1205088.3655
33 | 2650036.2565 | 1204693.4036
34 | 2650033.9759 | 1204687.0977
35 | 2650079.2666 | 1204811.6111
36 | 2649650.5564 | 1204816.7725
37 | 2649661.3757 | 1204784.2634
38 | 2649620.2927 | 1204831.5717
39 | 2649807.2714 | 1205007.6625
40 | 2649825.7458 | 1205060.042
41 | 2650115.0316 | 1205095.9263
42 | 2650125.2161 | 1204813.9421
43 | 2650111.6197 | 1205109.7995
44 | 2649826.5904 | 1205063.5076
45 | 2649600.6042 | 1205421.258
46 | 2649573.8221 | 1205430.7472
47 | 2649585.0079 | 1204710.1642
48 | 2649399.0933 | 1204415.3533
49 | 2649398.4427 | 1204406.3862
50 | 2649400.2071 | 1204430.7056
51 | 2649395.7819 | 1204369.7115
52 | 2649415.2548 | 1204483.3757
53 | 2649265.7782 | 1204291.1153
54 | 2649430.3455 | 1204508.7756
55 | 2649171.8222 | 1204366.1626
56 | 2649438.5566 | 1204520.7413
57 | 2649537.5656 | 1204653.827
58 | 2649428.6509 | 1204526.0525
59 | 2649558.8462 | 1204679.0958
60 | 2649564.8878 | 1204618.2906
61 | 2649564.4008 | 1204685.6922
62 | 2649535.7962 | 1204664.4989
63 | 2649566.7846 | 1204616.6202
64 | 2649511.905 | 1204651.6397
65 | 2649497.5841 | 1204650.8385
66 | 2649629.6129 | 1204692.3253
67 | 2649632.3285 | 1204691.0001
68 | 2649354.0118 | 1205310.1435
69 | 2649341.2205 | 1205268.5746
70 | 2649632.7514 | 1204690.7937
71 | 2649236.0967 | 1204538.0132
72 | 2649123.2331 | 1204500.2515
73 | 2649129.2278 | 1204465.1028
74 | 2648814.2371 | 1204737.4545
75 | 2648801.6353 | 1204750.2499
76 | 2648584.6159 | 1204611.6017
77 | 2648920.8889 | 1205611.0147
78 | 2649144.0923 | 1205257.4162
79 | 2649132.9497 | 1205243.4498
80 | 2649165.5974 | 1205203.6175
81 | 2649129.2347 | 1205241.1543
82 | 2649173.3135 | 1205193.8178
83 | 2649153.9834 | 1205196.736
84 | 2649189.9096 | 1205184.9067
85 | 2649136.2335 | 1205184.793
86 | 2648643.3028 | 1204534.4918
87 | 2648619.9244 | 1204531.7539
88 | 2648649.7492 | 1204533.1196
89 | 2648803.3088 | 1204340.6051
90 | 2648808.5284 | 1204335.0569
91 | 2648857.0321 | 1204316.5857
92 | 2648727.9913 | 1204287.7712
93 | 2648908.8278 | 1204185.5765
94 | 2648706.5066 | 1204222.9987
95 | 2648944.5359 | 1204203.1571
96 | 2648974.2891 | 1204245.0153
97 | 2649107.7501 | 1204214.1359
98 | 2649126.639 | 1204212.6618
99 | 2649145.6786 | 1204289.9258
100 | 2649154.7169 | 1204219.604
101 | 2649310.8147 | 1205245.8242
102 | 2649310.0942 | 1205236.7413
103 | 2649310.765 | 1205262.7775
104 | 2649309.6625 | 1205220.3809
105 | 2649310.187 | 1205268.9118
106 | 2649314.4354 | 1205216.2624
107 | 2649308.5312 | 1205286.4868
108 | 2649325.4489 | 1205224.283
109 | 2649308.1482 | 1205290.5521
110 | 2649305.404 | 1205311.4237
111 | 2649304.7911 | 1205312.9772
112 | 2649275.9853 | 1205303.5819
113 | 2649268.0787 | 1205275.5095
114 | 2649259.851 | 1205252.2997
115 | 2649335.2347 | 1205246.0486
116 | 2649257.0773 | 1205246.429
117 | 2649241.8871 | 1205221.4086
118 | 2649225.7751 | 1205184.0216
119 | 2649201.9179 | 1205181.0884
120 | 2649192.6404 | 1205183.9842
121 | 2649205.8735 | 1205226.9254
122 | 2649205.3262 | 1205217.4414
123 | 2649205.507 | 1205234.2748
124 | 2649188.3477 | 1205261.6048
125 | 2649204.4982 | 1205245.0421
126 | 2649201.1264 | 1205263.9058
127 | 2649168.123 | 1205162.9136
128 | 2649134.6819 | 1205183.5857
129 | 2649121.3408 | 1205170.6347
130 | 2649117.1235 | 1205165.1584
131 | 2649103.7757 | 1205147.603
132 | 2649314.4354 | 1205216.2624

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98808 | -0.085816 | 0.00023132 | 5.7974e-05
1 | 0.98809 | -0.08572 | 0 | 0
2 | 0.98806 | -0.085935 | 0 | 0
3 | 0.98808 | -0.085759 | 0 | 0
4 | 0.98813 | -0.085426 | 0 | 0
5 | 0.98804 | -0.086094 | 0.00034811 | 8.7245e-05
6 | 0.98807 | -0.085894 | 0.00012739 | 3.1928e-05
7 | 0.98836 | -0.083692 | 7.7714e-05 | 1.9477e-05
8 | 0.98842 | -0.0832 | 0.00034444 | 8.6325e-05
9 | 0.98833 | -0.083879 | 0.00042137 | 0.00010561
10 | 0.98848 | -0.082772 | 0 | 0
11 | 0.98832 | -0.083893 | 0.00060976 | 0.00015282
12 | 0.98848 | -0.082823 | 4.624e-05 | 1.1589e-05
13 | 0.98883 | -0.080192 | 0 | 0
14 | 0.989 | -0.078942 | 0 | 0
15 | 0.98952 | -0.075078 | 0.00033984 | 8.5173e-05
16 | 0.98899 | -0.079081 | 9.0318e-05 | 2.2636e-05
17 | 0.99032 | -0.06913 | 0.00014312 | 3.587e-05
18 | 0.98915 | -0.077972 | 6.2381e-05 | 1.5634e-05
19 | 0.98901 | -0.079008 | 9.2049e-05 | 2.307e-05
20 | 0.98904 | -0.078835 | 0 | 0
21 | 0.98903 | -0.078887 | 6.089e-05 | 1.5261e-05
22 | 0.98907 | -0.078569 | 7.0267e-05 | 1.761e-05
23 | 0.99297 | -0.050104 | 0.00066609 | 0.00016694
24 | 0.98753 | -0.089102 | 0.0017793 | 0.00044593
25 | 0.98907 | -0.078565 | 4.0372e-05 | 1.0118e-05
26 | 0.98908 | -0.078483 | 0.00013445 | 3.3697e-05
27 | 0.98909 | -0.078384 | 5.7413e-05 | 1.4389e-05
28 | 0.98911 | -0.078274 | 0.00032086 | 8.0415e-05
29 | 0.98618 | -0.098852 | 0.00047468 | 0.00011897
30 | 0.98619 | -0.098752 | 0.00016411 | 4.1129e-05
31 | 0.98639 | -0.097301 | 0 | 0
32 | 0.98515 | -0.10632 | 0.00010154 | 2.5448e-05
33 | 0.98471 | -0.10957 | 0.00052656 | 0.00013197
34 | 0.98471 | -0.10958 | 0.00013348 | 3.3453e-05
35 | 0.98484 | -0.10859 | 0 | 0
36 | 0.98386 | -0.11547 | 0.00025276 | 6.3347e-05
37 | 0.98355 | -0.11768 | 0 | 0
38 | 0.98373 | -0.1164 | 0.0021836 | 0.00054727
39 | 0.98626 | -0.098254 | 0 | 0
40 | 0.98687 | -0.093887 | 0.00011896 | 2.9813e-05
41 | 0.98513 | -0.10646 | 0.00075605 | 0.00018948
42 | 0.98489 | -0.10827 | 0 | 0
43 | 0.98511 | -0.10663 | 0.0011387 | 0.00028539
44 | 0.98691 | -0.093596 | 0.00058262 | 0.00014602
45 | 0.99398 | -0.042888 | 0.0013766 | 0.000345
46 | 0.9945 | -0.039155 | 0.00036186 | 9.069e-05
47 | 0.98265 | -0.12421 | 0 | 0
48 | 0.9779 | -0.1588 | 0.00015308 | 3.8364e-05
49 | 0.97783 | -0.15932 | 0.00015971 | 4.0026e-05
50 | 0.97803 | -0.15787 | 0 | 0
51 | 0.97755 | -0.16142 | 0 | 0
52 | 0.97848 | -0.15455 | 0.0011716 | 0.00029363
53 | 0.97627 | -0.17093 | 0 | 0
54 | 0.97877 | -0.15241 | 0.00019379 | 4.8568e-05
55 | 0.97531 | -0.17805 | 0 | 0
56 | 0.97892 | -0.15133 | 0 | 0
57 | 0.98117 | -0.13486 | 0 | 0
58 | 0.97888 | -0.15161 | 0.0023981 | 0.00060103
59 | 0.98164 | -0.1315 | 0 | 0
60 | 0.98116 | -0.13499 | 0.00013067 | 3.275e-05
61 | 0.98185 | -0.12998 | 0.00046678 | 0.00011699
62 | 0.98134 | -0.13364 | 0.00098491 | 0.00024684
63 | 0.98116 | -0.13499 | 0.0001306 | 3.2731e-05
64 | 0.98109 | -0.13541 | 0.00077455 | 0.00019412
65 | 0.98098 | -0.13621 | 0.0053959 | 0.0013523
66 | 0.98262 | -0.12438 | 0.00013064 | 3.2743e-05
67 | 0.98262 | -0.12439 | 0.00013066 | 3.2746e-05
68 | 0.99835 | -0.011706 | 0.00035428 | 8.8792e-05
69 | 0.99903 | -0.0068632 | 0.0001096 | 2.7469e-05
70 | 0.98262 | -0.12439 | 9.1355e-05 | 2.2896e-05
71 | 0.97468 | -0.18255 | 0.0011491 | 0.00028799
72 | 0.97489 | -0.18109 | 0.00012352 | 3.0957e-05
73 | 0.97495 | -0.18061 | 0.00034136 | 8.5554e-05
74 | 0.97135 | -0.2074 | 0.00026876 | 6.7357e-05
75 | 0.97136 | -0.20735 | 0.00065368 | 0.00016383
76 | 0.97171 | -0.2048 | 0 | 0
77 | 0.98597 | -0.098792 | 0.00032617 | 8.1745e-05
78 | 0.98617 | -0.097307 | 0 | 0
79 | 0.98605 | -0.098117 | 0.0022108 | 0.00055409
80 | 0.98657 | -0.094399 | 0 | 0
81 | 0.98604 | -0.098214 | 0.0021745 | 0.00054499
82 | 0.98678 | -0.092876 | 0.0014726 | 0.00036908
83 | 0.98644 | -0.095364 | 0.002193 | 0.00054962
84 | 0.98715 | -0.090308 | 0 | 0
85 | 0.98629 | -0.096413 | 0.00099581 | 0.00024957
86 | 0.97187 | -0.20355 | 0.00018724 | 4.6927e-05
87 | 0.97184 | -0.2038 | 0 | 0
88 | 0.97188 | -0.20347 | 0.00060492 | 0.00015161
89 | 0.9725 | -0.19889 | 0.00035301 | 8.8472e-05
90 | 0.97253 | -0.19872 | 0.00022868 | 5.7313e-05
91 | 0.9727 | -0.1974 | 0 | 0
92 | 0.97257 | -0.19837 | 0 | 0
93 | 0.9733 | -0.19295 | 6.7859e-05 | 1.7007e-05
94 | 0.97251 | -0.19882 | 0.0006108 | 0.00015308
95 | 0.97348 | -0.19166 | 5.3536e-05 | 1.3417e-05
96 | 0.97371 | -0.18993 | 0 | 0
97 | 0.97432 | -0.1854 | 0.00044145 | 0.00011064
98 | 0.97431 | -0.18544 | 0.0001121 | 2.8096e-05
99 | 0.97479 | -0.1819 | 0 | 0
100 | 0.97431 | -0.18546 | 5.9373e-05 | 1.488e-05
101 | 0.99848 | -0.010546 | 0.00012808 | 3.21e-05
102 | 0.99891 | -0.0075866 | 0.0004938 | 0.00012376
103 | 0.99769 | -0.016044 | 0.00052491 | 0.00013155
104 | 0.99969 | -0.0021754 | 0.00093708 | 0.00023485
105 | 0.99741 | -0.018009 | 0.0001893 | 4.7442e-05
106 | 1 | 0 | -0.068139 | -0.016862
107 | 0.99661 | -0.023611 | 0.00054668 | 0.00013701
108 | 0.99977 | -0.001625 | 0.00016032 | 4.0179e-05
109 | 0.99643 | -0.024885 | 0.00016511 | 4.138e-05
110 | 0.99549 | -0.031444 | 0.00015432 | 3.8677e-05
111 | 0.99542 | -0.031961 | 0.0013091 | 0.00032809
112 | 0.99334 | -0.046498 | 0.00067813 | 0.00016996
113 | 0.99214 | -0.054988 | 0.00063082 | 0.0001581
114 | 0.99114 | -0.062022 | 0.0011275 | 0.00028258
115 | 0.9994 | -0.0042848 | 0.00019823 | 4.9681e-05
116 | 0.99089 | -0.063802 | 0.0017019 | 0.00042654
117 | 0.98982 | -0.071344 | 0.00088247 | 0.00022117
118 | 0.98837 | -0.08159 | 0.00048881 | 0.00012251
119 | 0.98752 | -0.087639 | 0.0011572 | 0.00029001
120 | 0.9872 | -0.089902 | 0 | 0
121 | 0.98662 | -0.094014 | 0.0031724 | 0.00079508
122 | 0.98674 | -0.093206 | 0.00066632 | 0.000167
123 | 0.98657 | -0.094399 | 0 | 0
124 | 0.98643 | -0.095407 | 0.0030445 | 0.00076303
125 | 0.98654 | -0.094627 | 0.001149 | 0.00028798
126 | 0.98651 | -0.094806 | 0.00090674 | 0.00022725
127 | 0.98712 | -0.090495 | 0.00058252 | 0.00014599
128 | 0.98628 | -0.096489 | 0.00048977 | 0.00012275
129 | 0.98619 | -0.097119 | 0.00091927 | 0.00023039
130 | 0.98616 | -0.097287 | 0.001515 | 0.0003797
131 | 0.98614 | -0.097479 | 0.00084871 | 0.00021271
132 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00023132 | -5.7974e-05 | 0.00023132 | 5.7463e-05 | 3.0232e-09 | -5.1046e-07 | 0.00034836 | 0.00034818 | 0.00034836 | 0.98808 | -0.085816 | 0.98809 | -0.08572 | 0.12902
1 | 0.00034813 | 8.5924e-05 | -0.00034812 | -8.6676e-05 | 1.0101e-08 | -7.5144e-07 | 0.0005238 | 0.00052406 | 0.00052406 | 0.98809 | -0.08572 | 0.98806 | -0.085935 | 0.1941
2 | 0.0001274 | 3.0299e-05 | -0.0001274 | -3.0653e-05 | 6.3096e-10 | -3.5348e-07 | 0.00019129 | 0.00019141 | 0.00019141 | 0.98809 | -0.08572 | 0.98808 | -0.085759 | 0.070893
3 | -0.00070685 | -0.00017369 | 0.00070687 | 0.00017319 | 2.7669e-08 | -4.9184e-07 | 0.0010633 | 0.0010631 | 0.0010633 | 0.98809 | -0.08572 | 0.98813 | -0.085426 | 0.3938
4 | 0.00034812 | 8.6676e-05 | -0.00034811 | -8.7245e-05 | 7.6575e-09 | -5.6911e-07 | 0.00052406 | 0.00052427 | 0.00052427 | 0.98806 | -0.085935 | 0.98804 | -0.086094 | 0.19417
5 | 0.0001274 | 3.0653e-05 | -0.00012739 | -3.1928e-05 | 2.283e-09 | -1.2752e-06 | 0.00019141 | 0.00019185 | 0.00019185 | 0.98808 | -0.085759 | 0.98807 | -0.085894 | 0.071057
6 | -0.00070687 | -0.00017319 | 0.00070703 | 0.00017035 | 1.5996e-07 | -2.8475e-06 | 0.0010631 | 0.0010621 | 0.0010631 | 0.98813 | -0.085426 | 0.98836 | -0.083692 | 0.39373
7 | -0.00078475 | -0.00018982 | 0.0007848 | 0.00018911 | 4.9754e-08 | -7.1609e-07 | 0.0011791 | 0.0011788 | 0.0011791 | 0.98836 | -0.083692 | 0.98842 | -0.0832 | 0.4367
8 | -0.0011292 | -0.00027543 | 0.0011293 | 0.00027506 | 5.5955e-08 | -3.7748e-07 | 0.0016973 | 0.0016972 | 0.0016973 | 0.98842 | -0.0832 | 0.98848 | -0.082823 | 0.62865
9 | -0.0010311 | -0.0002584 | 0.0010313 | 0.00025712 | 1.5722e-07 | -1.2798e-06 | 0.0015525 | 0.001552 | 0.0015525 | 0.98833 | -0.083879 | 0.98848 | -0.082772 | 0.57498
10 | 0.00060976 | 0.00015279 | -0.00060976 | -0.00015282 | 1.1276e-09 | -2.7041e-08 | 0.00091804 | 0.00091805 | 0.00091805 | 0.98833 | -0.083879 | 0.98832 | -0.083893 | 0.34002
11 | 0.0011755 | 0.0002866 | -0.0011755 | -0.00028664 | 7.8346e-09 | -4.8545e-08 | 0.0017668 | 0.0017668 | 0.0017668 | 0.98848 | -0.082772 | 0.98848 | -0.082823 | 0.65438
12 | -0.0022068 | -0.00054372 | 0.0022076 | 0.00054259 | 7.6107e-07 | -1.1275e-06 | 0.0033188 | 0.0033183 | 0.0033188 | 0.98848 | -0.082772 | 0.98883 | -0.080192 | 1.2292
13 | -0.0022076 | -0.00054259 | 0.002208 | 0.00054204 | 3.6735e-07 | -5.4473e-07 | 0.0033183 | 0.003318 | 0.0033183 | 0.98883 | -0.080192 | 0.989 | -0.078942 | 1.229
14 | -0.0022983 | -0.00056288 | 0.0022995 | 0.00056131 | 1.1728e-06 | -1.5728e-06 | 0.0034533 | 0.0034526 | 0.0034533 | 0.989 | -0.078942 | 0.98952 | -0.075078 | 1.279
15 | 9.032e-05 | 2.084e-05 | -9.0318e-05 | -2.2636e-05 | 1.6062e-09 | -1.7963e-06 | 0.00013528 | 0.00013589 | 0.00013589 | 0.989 | -0.078942 | 0.98899 | -0.079081 | 0.05033
16 | -0.0034783 | -0.00084639 | 0.003481 | 0.00084538 | 2.7034e-06 | -1.0032e-06 | 0.0052217 | 0.005221 | 0.0052217 | 0.98952 | -0.075078 | 0.99032 | -0.06913 | 1.934
17 | 0.00083905 | 0.00019991 | -0.00083873 | -0.00020383 | 3.1133e-07 | -3.9233e-06 | 0.0012581 | 0.0012595 | 0.0012595 | 0.98952 | -0.075078 | 0.98915 | -0.077972 | 0.46649
18 | -0.029655 | -0.0073662 | 0.029732 | 0.0073886 | 7.6884e-05 | 2.2358e-05 | 0.044536 | 0.044533 | 0.044536 | 0.99032 | -0.06913 | 0.99297 | -0.050104 | 5.4982
19 | 0.026031 | 0.006485 | -0.02596 | -0.0064663 | 7.1019e-05 | 1.8719e-05 | 0.0391 | 0.039103 | 0.039103 | 0.99032 | -0.06913 | 0.98753 | -0.089102 | 4.8275
20 | 0.00077635 | 0.00018819 | -0.00077632 | -0.00018864 | 3.0506e-08 | -4.5e-07 | 0.0011657 | 0.0011658 | 0.0011658 | 0.98915 | -0.077972 | 0.98911 | -0.078274 | 0.43179
21 | -9.2049e-05 | -2.307e-05 | 9.2051e-05 | 2.09e-05 | 2.0131e-09 | -2.1696e-06 | 0.00013849 | 0.00013776 | 0.00013849 | 0.98901 | -0.079008 | 0.98904 | -0.078835 | 0.051293
22 | 6.0891e-05 | 1.4254e-05 | -6.089e-05 | -1.5261e-05 | 4.093e-10 | -1.0067e-06 | 9.1265e-05 | 9.1611e-05 | 9.1611e-05 | 0.98904 | -0.078835 | 0.98903 | -0.078887 | 0.03393
23 | -0.00015294 | -3.5154e-05 | 0.00015295 | 3.3334e-05 | 4.6334e-09 | -1.8197e-06 | 0.00022902 | 0.00022844 | 0.00022902 | 0.98904 | -0.078835 | 0.98907 | -0.078569 | 0.084822
24 | -0.00022321 | -5.0945e-05 | 0.00022321 | 5.0923e-05 | 1.2029e-10 | -2.211e-08 | 0.00033412 | 0.00033411 | 0.00033412 | 0.98907 | -0.078569 | 0.98907 | -0.078565 | 0.12375
25 | -0.030398 | -0.0075555 | 0.030428 | 0.0075643 | 2.9892e-05 | 8.8039e-06 | 0.045531 | 0.04553 | 0.045531 | 0.99297 | -0.050104 | 0.99398 | -0.042888 | 5.6211
26 | 0.024181 | 0.0060203 | -0.024166 | -0.0060167 | 1.4845e-05 | 3.6459e-06 | 0.036422 | 0.036422 | 0.036422 | 0.98753 | -0.089102 | 0.98691 | -0.093596 | 4.4966
27 | -0.00026358 | -6.1041e-05 | 0.00026359 | 6.0702e-05 | 2.5742e-09 | -3.3873e-07 | 0.00039484 | 0.00039472 | 0.00039484 | 0.98907 | -0.078565 | 0.98908 | -0.078483 | 0.14624
28 | -0.00039804 | -9.4399e-05 | 0.00039804 | 9.4116e-05 | 4.9354e-09 | -2.8299e-07 | 0.00059698 | 0.00059688 | 0.00059698 | 0.98908 | -0.078483 | 0.98909 | -0.078384 | 0.2211
29 | -0.00045546 | -0.0001085 | 0.00045546 | 0.00010823 | 6.2984e-09 | -2.7513e-07 | 0.00068325 | 0.00068315 | 0.00068325 | 0.98909 | -0.078384 | 0.98911 | -0.078274 | 0.25305
30 | -0.00047468 | -0.00011897 | 0.00047468 | 0.00011871 | 6.5457e-09 | -2.5843e-07 | 0.00071623 | 0.00071613 | 0.00071623 | 0.98618 | -0.098852 | 0.98619 | -0.098752 | 0.26527
31 | -0.0032982 | -0.00081704 | 0.0032988 | 0.00081676 | 6.4749e-07 | -2.8643e-07 | 0.0049731 | 0.0049729 | 0.0049731 | 0.98619 | -0.098752 | 0.98639 | -0.097301 | 1.8419
32 | 0.0026594 | 0.00065721 | -0.0026567 | -0.00065962 | 2.7201e-06 | -2.4092e-06 | 0.0040094 | 0.0040106 | 0.0040106 | 0.98619 | -0.098752 | 0.98515 | -0.10632 | 1.4854
33 | 0.020154 | 0.0050213 | -0.020151 | -0.0050208 | 2.6293e-06 | 4.8727e-07 | 0.030392 | 0.030392 | 0.030392 | 0.98639 | -0.097301 | 0.98626 | -0.098254 | 3.7521
34 | -0.023452 | -0.005838 | 0.023463 | 0.0058406 | 1.0941e-05 | 2.5966e-06 | 0.035365 | 0.035364 | 0.035365 | 0.98639 | -0.097301 | 0.98687 | -0.093887 | 4.3661
35 | 0.0018948 | 0.00047462 | -0.0018948 | -0.0004747 | 3.879e-08 | -8.1711e-08 | 0.0028619 | 0.002862 | 0.002862 | 0.98515 | -0.10632 | 0.98513 | -0.10646 | 1.06
36 | 0.00066033 | 0.00015955 | -0.00066016 | -0.00016298 | 1.6995e-07 | -3.4299e-06 | 0.00099531 | 0.00099652 | 0.00099652 | 0.98515 | -0.10632 | 0.98489 | -0.10827 | 0.36908
37 | 0.00013348 | 3.3368e-05 | -0.00013348 | -3.3453e-05 | 1.7115e-10 | -8.5708e-08 | 0.00020167 | 0.00020171 | 0.00020171 | 0.98471 | -0.10957 | 0.98471 | -0.10958 | 0.074706
38 | -0.00066004 | -0.00016534 | 0.00066013 | 0.00016355 | 8.8518e-08 | -1.7815e-06 | 0.00099737 | 0.00099673 | 0.00099737 | 0.98471 | -0.10957 | 0.98484 | -0.10859 | 0.3694
39 | -0.00066013 | -0.00016355 | 0.00066016 | 0.00016298 | 2.8433e-08 | -5.7283e-07 | 0.00099673 | 0.00099652 | 0.00099673 | 0.98484 | -0.10859 | 0.98489 | -0.10827 | 0.36916
40 | 0.017667 | 0.0044018 | -0.017662 | -0.0044011 | 5.3405e-06 | 6.8345e-07 | 0.026711 | 0.026711 | 0.026711 | 0.98386 | -0.11547 | 0.98355 | -0.11768 | 3.2977
41 | 0.0021839 | 0.00054686 | -0.0021836 | -0.00054727 | 2.8092e-07 | -4.1594e-07 | 0.0033028 | 0.003303 | 0.003303 | 0.98386 | -0.11547 | 0.98373 | -0.1164 | 1.2233
42 | -0.020104 | -0.005012 | 0.020151 | 0.0050208 | 4.7457e-05 | 8.8203e-06 | 0.030396 | 0.030392 | 0.030396 | 0.98386 | -0.11547 | 0.98626 | -0.098254 | 3.7526
43 | 0.017662 | 0.0044011 | -0.017646 | -0.0043991 | 1.577e-05 | 2.0234e-06 | 0.026711 | 0.026712 | 0.026712 | 0.98355 | -0.11768 | 0.98265 | -0.12421 | 3.2978
44 | -0.023582 | -0.0058704 | 0.023583 | 0.0058707 | 9.3734e-07 | 2.2378e-07 | 0.035544 | 0.035544 | 0.035544 | 0.98687 | -0.093887 | 0.98691 | -0.093596 | 4.3881
45 | 0.0011387 | 0.00028522 | -0.0011387 | -0.00028539 | 2.6399e-08 | -1.7191e-07 | 0.00172 | 0.00172 | 0.00172 | 0.98513 | -0.10646 | 0.98511 | -0.10663 | 0.63705
46 | -0.031805 | -0.0079093 | 0.031821 | 0.0079142 | 1.6196e-05 | 4.8916e-06 | 0.047591 | 0.04759 | 0.047591 | 0.99398 | -0.042888 | 0.9945 | -0.039155 | 5.8754
47 | -0.032183 | -0.0080049 | 0.032304 | 0.0080416 | 0.00012081 | 3.6667e-05 | 0.048132 | 0.048128 | 0.048132 | 0.9945 | -0.039155 | 0.99835 | -0.011706 | 5.9422
48 | 0.00035267 | 8.7734e-05 | -0.00035266 | -8.834e-05 | 8.56e-09 | -6.063e-07 | 0.00053381 | 0.00053402 | 0.00053402 | 0.98265 | -0.12421 | 0.98262 | -0.12438 | 0.19779
49 | 0.017293 | 0.0043113 | -0.017279 | -0.0043065 | 1.3681e-05 | 4.8571e-06 | 0.026179 | 0.026179 | 0.026179 | 0.98265 | -0.12421 | 0.98185 | -0.12998 | 9.6959
50 | 0.0054401 | 0.0013397 | -0.0054397 | -0.0013397 | 3.8364e-07 | 3.4767e-08 | 0.0082694 | 0.0082695 | 0.0082695 | 0.9779 | -0.1588 | 0.97783 | -0.15932 | 3.0628
51 | -0.0055932 | -0.0013781 | 0.0055939 | 0.0013781 | 6.9434e-07 | 7.3914e-08 | 0.0085023 | 0.0085023 | 0.0085023 | 0.9779 | -0.1588 | 0.97803 | -0.15787 | 3.149
52 | 0.00528 | 0.0012996 | -0.0052785 | -0.0012995 | 1.4782e-06 | 1.0743e-07 | 0.0080264 | 0.0080266 | 0.0080266 | 0.97783 | -0.15932 | 0.97755 | -0.16142 | 2.9728
53 | -0.0055939 | -0.0013781 | 0.0055964 | 0.0013784 | 2.4877e-06 | 2.6439e-07 | 0.0085023 | 0.008502 | 0.0085023 | 0.97803 | -0.15787 | 0.97848 | -0.15455 | 3.149
54 | 0.0052785 | 0.0012995 | -0.0052718 | -0.001299 | 6.7162e-06 | 4.9167e-07 | 0.0080266 | 0.0080273 | 0.0080273 | 0.97755 | -0.16142 | 0.97627 | -0.17093 | 2.9731
55 | -0.006768 | -0.001672 | 0.0067699 | 0.0016724 | 1.9516e-06 | 3.7904e-07 | 0.010284 | 0.010284 | 0.010284 | 0.97848 | -0.15455 | 0.97877 | -0.15241 | 3.8088
56 | 0.0052718 | 0.001299 | -0.0052668 | -0.0012987 | 5.0252e-06 | 3.7173e-07 | 0.0080273 | 0.0080279 | 0.0080279 | 0.97627 | -0.17093 | 0.97531 | -0.17805 | 2.9733
57 | -0.0069637 | -0.001721 | 0.0069647 | 0.0017212 | 1.0133e-06 | 2.0731e-07 | 0.010578 | 0.010578 | 0.010578 | 0.97877 | -0.15241 | 0.97892 | -0.15133 | 3.9179
58 | 0.0016149 | 0.00040104 | -0.0016143 | -0.00040268 | 5.6493e-07 | -1.6447e-06 | 0.0024625 | 0.0024631 | 0.0024631 | 0.97531 | -0.17805 | 0.97495 | -0.18061 | 0.91228
59 | 0.0036519 | 0.00089762 | -0.00365 | -0.0008981 | 1.877e-06 | -4.8926e-07 | 0.0055654 | 0.0055658 | 0.0055658 | 0.97531 | -0.17805 | 0.97479 | -0.1819 | 2.0614
60 | -0.0093629 | -0.0023221 | 0.0093839 | 0.0023281 | 2.0936e-05 | 5.9624e-06 | 0.014224 | 0.014223 | 0.014224 | 0.97892 | -0.15133 | 0.98117 | -0.13486 | 5.268
61 | 0.0023982 | 0.00060092 | -0.0023981 | -0.00060103 | 9.3205e-08 | -1.0545e-07 | 0.0036454 | 0.0036455 | 0.0036455 | 0.97892 | -0.15133 | 0.97888 | -0.15161 | 1.3502
62 | -0.0096451 | -0.0023929 | 0.0096495 | 0.0023942 | 4.4005e-06 | 1.2755e-06 | 0.014619 | 0.014619 | 0.014619 | 0.98117 | -0.13486 | 0.98164 | -0.1315 | 5.4144
63 | 0.00026128 | 6.4883e-05 | -0.00026127 | -6.5449e-05 | 4.4004e-09 | -5.6589e-07 | 0.00039603 | 0.00039623 | 0.00039623 | 0.98117 | -0.13486 | 0.98116 | -0.13499 | 0.14675
64 | -0.016809 | -0.0041882 | 0.016813 | 0.0041895 | 3.4912e-06 | 1.2337e-06 | 0.025471 | 0.025471 | 0.025471 | 0.98164 | -0.1315 | 0.98185 | -0.12998 | 9.4339
65 | 0.0071596 | 0.001794 | -0.0071575 | -0.0017936 | 2.115e-06 | 4.4978e-07 | 0.010853 | 0.010853 | 0.010853 | 0.98164 | -0.1315 | 0.98134 | -0.13364 | 4.0196
66 | 0.0001306 | 3.2699e-05 | -0.0001306 | -3.2731e-05 | 6.1844e-11 | -3.1896e-08 | 0.00019805 | 0.00019806 | 0.00019806 | 0.98116 | -0.13499 | 0.98116 | -0.13499 | 0.073357
67 | 0.0061726 | 0.0015467 | -0.006171 | -0.0015465 | 1.5123e-06 | 2.3221e-07 | 0.0093594 | 0.0093596 | 0.0093596 | 0.98134 | -0.13364 | 0.98109 | -0.13541 | 3.4665
68 | 0.0053965 | 0.0013524 | -0.0053959 | -0.0013523 | 6.0268e-07 | 4.9764e-08 | 0.0081848 | 0.0081849 | 0.0081849 | 0.98109 | -0.13541 | 0.98098 | -0.13621 | 3.0314
69 | 0.00022201 | 5.5597e-05 | -0.00022201 | -5.5636e-05 | 2.131e-10 | -3.8195e-08 | 0.00033618 | 0.0003362 | 0.0003362 | 0.98262 | -0.12438 | 0.98262 | -0.12439 | 0.12452
70 | 9.1355e-05 | 2.289e-05 | -9.1355e-05 | -2.2896e-05 | 5.6378e-12 | -5.9581e-09 | 0.00013834 | 0.00013834 | 0.00013834 | 0.98262 | -0.12439 | 0.98262 | -0.12439 | 0.051237
71 | -0.032658 | -0.0081304 | 0.032679 | 0.008137 | 2.162e-05 | 6.5919e-06 | 0.048657 | 0.048656 | 0.048657 | 0.99835 | -0.011706 | 0.99903 | -0.0068632 | 6.007
72 | -0.032789 | -0.0081644 | 0.032801 | 0.008168 | 1.1558e-05 | 3.5292e-06 | 0.048819 | 0.048819 | 0.048819 | 0.99903 | -0.0068632 | 0.9994 | -0.0042848 | 6.0271
73 | -0.0011491 | -0.00028799 | 0.0011493 | 0.00028658 | 2.3077e-07 | -1.4097e-06 | 0.0017543 | 0.0017538 | 0.0017543 | 0.97468 | -0.18255 | 0.97489 | -0.18109 | 0.64974
74 | -0.0012729 | -0.00031754 | 0.0012729 | 0.00031713 | 8.3931e-08 | -4.1233e-07 | 0.0019423 | 0.0019421 | 0.0019423 | 0.97489 | -0.18109 | 0.97495 | -0.18061 | 0.71937
75 | -0.00026876 | -6.7357e-05 | 0.00026876 | 6.7135e-05 | 1.9066e-09 | -2.2243e-07 | 0.00041171 | 0.00041163 | 0.00041171 | 0.97135 | -0.2074 | 0.97136 | -0.20735 | 0.15249
76 | -0.00092244 | -0.00023096 | 0.00092276 | 0.0002279 | 3.2058e-07 | -3.0657e-06 | 0.001413 | 0.0014119 | 0.001413 | 0.97136 | -0.20735 | 0.97171 | -0.2048 | 0.52333
77 | -0.00092276 | -0.0002279 | 0.00092289 | 0.00022671 | 1.2391e-07 | -1.1869e-06 | 0.0014119 | 0.0014114 | 0.0014119 | 0.97171 | -0.2048 | 0.97184 | -0.2038 | 0.52291
78 | -0.00032617 | -8.1745e-05 | 0.00032623 | 7.6435e-05 | 6.2985e-08 | -5.3098e-06 | 0.00049225 | 0.00049041 | 0.00049225 | 0.98597 | -0.098792 | 0.98617 | -0.097307 | 0.18231
79 | 0.0043859 | 0.001099 | -0.0043854 | -0.001099 | 4.9152e-07 | -4.0405e-08 | 0.0066178 | 0.0066178 | 0.0066178 | 0.98617 | -0.097307 | 0.98605 | -0.098117 | 2.4511
80 | -0.0047121 | -0.0011754 | 0.004714 | 0.0011754 | 1.8789e-06 | -3.8049e-08 | 0.0071081 | 0.0071078 | 0.0071081 | 0.98617 | -0.097307 | 0.98657 | -0.094399 | 2.6326
81 | 0.0021746 | 0.00054495 | -0.0021745 | -0.00054499 | 2.9344e-08 | -4.4417e-08 | 0.0032815 | 0.0032816 | 0.0032816 | 0.98605 | -0.098117 | 0.98604 | -0.098214 | 1.2154
82 | -0.011678 | -0.0029198 | 0.01168 | 0.0029206 | 2.4507e-06 | 7.8083e-07 | 0.017611 | 0.017611 | 0.017611 | 0.98657 | -0.094399 | 0.98678 | -0.092876 | 6.5224
83 | 0.0069636 | 0.0017444 | -0.0069627 | -0.0017443 | 9.2921e-07 | 1.8503e-07 | 0.010503 | 0.010503 | 0.010503 | 0.98657 | -0.094399 | 0.98644 | -0.095364 | 3.8899
84 | -0.013153 | -0.0032897 | 0.013157 | 0.0032912 | 4.6598e-06 | 1.5496e-06 | 0.019831 | 0.019831 | 0.019831 | 0.98678 | -0.092876 | 0.98715 | -0.090308 | 7.3449
85 | 0.0047697 | 0.0011946 | -0.004769 | -0.0011946 | 6.9188e-07 | -7.2916e-09 | 0.0071947 | 0.0071948 | 0.0071948 | 0.98644 | -0.095364 | 0.98629 | -0.096413 | 2.6647
86 | 0.00058253 | 0.0001456 | -0.00058252 | -0.00014599 | 1.5036e-08 | -3.9378e-07 | 0.00087797 | 0.00087811 | 0.00087811 | 0.98715 | -0.090308 | 0.98712 | -0.090495 | 0.32523
87 | -0.01374 | -0.0034368 | 0.013741 | 0.0034371 | 7.6939e-07 | 2.5916e-07 | 0.020709 | 0.020709 | 0.020709 | 0.98715 | -0.090308 | 0.9872 | -0.089902 | 7.67
88 | 0.0037732 | 0.00094507 | -0.0037731 | -0.00094508 | 3.9752e-08 | -9.8003e-09 | 0.0056924 | 0.0056924 | 0.0056924 | 0.98629 | -0.096413 | 0.98628 | -0.096489 | 2.1083
89 | 0.00092292 | 0.00022642 | -0.00092289 | -0.00022671 | 3.0149e-08 | -2.8896e-07 | 0.0014113 | 0.0014114 | 0.0014114 | 0.97187 | -0.20355 | 0.97184 | -0.2038 | 0.52275
90 | -0.0011102 | -0.00027335 | 0.0011102 | 0.00027327 | 1.1857e-08 | -7.7111e-08 | 0.001698 | 0.001698 | 0.001698 | 0.97187 | -0.20355 | 0.97188 | -0.20347 | 0.62889
91 | -0.0017151 | -0.00042488 | 0.0017161 | 0.00042223 | 1.0577e-06 | -2.6467e-06 | 0.0026241 | 0.002623 | 0.0026241 | 0.97188 | -0.20347 | 0.9725 | -0.19889 | 0.9719
92 | -0.0020692 | -0.0005107 | 0.0020692 | 0.00051063 | 4.756e-08 | -7.6226e-08 | 0.0031632 | 0.0031631 | 0.0031632 | 0.9725 | -0.19889 | 0.97253 | -0.19872 | 1.1715
93 | -0.0022979 | -0.00056794 | 0.0022983 | 0.00056744 | 4.0628e-07 | -4.9853e-07 | 0.003513 | 0.0035128 | 0.003513 | 0.97253 | -0.19872 | 0.9727 | -0.1974 | 1.3011
94 | 0.00061092 | 0.00015045 | -0.00061084 | -0.00015223 | 7.9783e-08 | -1.7886e-06 | 0.00093361 | 0.00093426 | 0.00093426 | 0.9727 | -0.1974 | 0.97257 | -0.19837 | 0.34602
95 | -0.0029092 | -0.00071789 | 0.0029109 | 0.00071681 | 1.7377e-06 | -1.0814e-06 | 0.0044464 | 0.0044458 | 0.0044464 | 0.9727 | -0.1974 | 0.9733 | -0.19295 | 1.6468
96 | 0.00061084 | 0.00015223 | -0.0006108 | -0.00015308 | 3.7843e-08 | -8.4733e-07 | 0.00093426 | 0.00093457 | 0.00093457 | 0.97257 | -0.19837 | 0.97251 | -0.19882 | 0.34614
97 | -0.0029788 | -0.00073381 | 0.0029793 | 0.00073352 | 5.15e-07 | -2.9759e-07 | 0.0045495 | 0.0045494 | 0.0045495 | 0.9733 | -0.19295 | 0.97348 | -0.19166 | 1.685
98 | -0.0030329 | -0.00074693 | 0.0030336 | 0.00074655 | 7.0147e-07 | -3.8202e-07 | 0.0046312 | 0.004631 | 0.0046312 | 0.97348 | -0.19166 | 0.97371 | -0.18993 | 1.7153
99 | -0.0030336 | -0.00074655 | 0.0030354 | 0.00074555 | 1.8329e-06 | -1e-06 | 0.004631 | 0.0046304 | 0.004631 | 0.97371 | -0.18993 | 0.97432 | -0.1854 | 1.7152
100 | 0.00017148 | 4.2359e-05 | -0.00017148 | -4.2616e-05 | 8.8267e-10 | -2.5686e-07 | 0.00026167 | 0.00026176 | 0.00026176 | 0.97432 | -0.1854 | 0.97431 | -0.18544 | 0.096947
101 | -0.0036483 | -0.00089855 | 0.00365 | 0.0008981 | 1.708e-06 | -4.4393e-07 | 0.0055662 | 0.0055658 | 0.0055662 | 0.97432 | -0.1854 | 0.97479 | -0.1819 | 2.0616
102 | 5.9373e-05 | 1.452e-05 | -5.9373e-05 | -1.488e-05 | 1.4832e-10 | -3.6047e-07 | 9.055e-05 | 9.0678e-05 | 9.0678e-05 | 0.97431 | -0.18544 | 0.97431 | -0.18546 | 0.033584
103 | -0.03268 | -0.008221 | 0.032694 | 0.0082261 | 1.3494e-05 | 5.0707e-06 | 0.048713 | 0.048713 | 0.048713 | 0.99848 | -0.010546 | 0.99891 | -0.0075866 | 18.042
104 | 0.032552 | 0.0081889 | -0.032527 | -0.0081796 | 2.4944e-05 | 9.372e-06 | 0.048522 | 0.048523 | 0.048523 | 0.99848 | -0.010546 | 0.99769 | -0.016044 | 17.9713
105 | -0.033188 | -0.0083499 | 0.033213 | 0.0083593 | 2.5074e-05 | 9.4284e-06 | 0.049449 | 0.049449 | 0.049449 | 0.99891 | -0.0075866 | 0.99969 | -0.0021754 | 18.3144
106 | 0.032002 | 0.008048 | -0.031994 | -0.0080447 | 8.7624e-06 | 3.2897e-06 | 0.04774 | 0.04774 | 0.04774 | 0.99769 | -0.016044 | 0.99741 | -0.018009 | 17.6814
107 | -0.03415 | -0.0085942 | 0.03416 | 0.0085981 | 1.0373e-05 | 3.9053e-06 | 0.050844 | 0.050844 | 0.050844 | 0.99969 | -0.0021754 | 1 | 0 | 18.831
108 | 0.031804 | 0.0079973 | -0.031779 | -0.007988 | 2.4809e-05 | 9.3117e-06 | 0.047457 | 0.047457 | 0.047457 | 0.99741 | -0.018009 | 0.99661 | -0.023611 | 17.5768
109 | 0.033178 | 0.0082638 | -0.033171 | -0.0082615 | 7.3715e-06 | 2.2627e-06 | 0.049352 | 0.049352 | 0.049352 | 1 | 0 | 0.99977 | -0.001625 | 6.0929
110 | 0.031233 | 0.007851 | -0.031227 | -0.0078489 | 5.5429e-06 | 2.0787e-06 | 0.046641 | 0.046641 | 0.046641 | 0.99661 | -0.023611 | 0.99643 | -0.024885 | 17.2745
111 | 0.033011 | 0.0082213 | -0.032999 | -0.0082176 | 1.2002e-05 | 3.6754e-06 | 0.049114 | 0.049114 | 0.049114 | 0.99977 | -0.001625 | 0.9994 | -0.0042848 | 6.0635
112 | 0.031062 | 0.0078075 | -0.031034 | -0.0077969 | 2.834e-05 | 1.0625e-05 | 0.046395 | 0.046395 | 0.046395 | 0.99643 | -0.024885 | 0.99549 | -0.031444 | 17.1832
113 | 0.030879 | 0.0077582 | -0.030877 | -0.0077574 | 2.2208e-06 | 8.3246e-07 | 0.046164 | 0.046164 | 0.046164 | 0.99549 | -0.031444 | 0.99542 | -0.031961 | 17.0978
114 | 0.029568 | 0.0074293 | -0.029508 | -0.007407 | 5.969e-05 | 2.2323e-05 | 0.044207 | 0.044207 | 0.044207 | 0.99542 | -0.031961 | 0.99334 | -0.046498 | 16.3731
115 | 0.02883 | 0.007237 | -0.028796 | -0.0072243 | 3.3954e-05 | 1.2682e-05 | 0.043191 | 0.043192 | 0.043192 | 0.99334 | -0.046498 | 0.99214 | -0.054988 | 15.9969
116 | 0.028166 | 0.0070662 | -0.028138 | -0.007056 | 2.7455e-05 | 1.0242e-05 | 0.042246 | 0.042246 | 0.042246 | 0.99214 | -0.054988 | 0.99114 | -0.062022 | 15.6465
117 | 0.027011 | 0.0067734 | -0.027004 | -0.0067709 | 6.663e-06 | 2.479e-06 | 0.040553 | 0.040553 | 0.040553 | 0.99114 | -0.062022 | 0.99089 | -0.063802 | 15.0196
118 | 0.025302 | 0.0063444 | -0.025276 | -0.0063346 | 2.6416e-05 | 9.7826e-06 | 0.037997 | 0.037997 | 0.037997 | 0.99089 | -0.063802 | 0.98982 | -0.071344 | 14.0731
119 | 0.024393 | 0.0061134 | -0.024359 | -0.0061007 | 3.4553e-05 | 1.2761e-05 | 0.036671 | 0.036671 | 0.036671 | 0.98982 | -0.071344 | 0.98837 | -0.08159 | 13.5818
120 | 0.02387 | 0.0059782 | -0.02385 | -0.0059708 | 1.9944e-05 | 7.3539e-06 | 0.035935 | 0.035935 | 0.035935 | 0.98837 | -0.08159 | 0.98752 | -0.087639 | 13.3093
121 | 0.022693 | 0.0056808 | -0.022686 | -0.0056782 | 7.0899e-06 | 2.6026e-06 | 0.034191 | 0.034191 | 0.034191 | 0.98752 | -0.087639 | 0.9872 | -0.089902 | 12.6635
122 | 0.0089448 | 0.0022411 | -0.0089407 | -0.00224 | 4.0889e-06 | 1.112e-06 | 0.013482 | 0.013483 | 0.013483 | 0.9872 | -0.089902 | 0.98674 | -0.093206 | 4.9935
123 | -0.0082735 | -0.0020728 | 0.0082744 | 0.002073 | 9.2417e-07 | 2.3395e-07 | 0.012478 | 0.012478 | 0.012478 | 0.98662 | -0.094014 | 0.98674 | -0.093206 | 4.6214
124 | 0.0051011 | 0.0012777 | -0.0051008 | -0.0012777 | 2.7176e-07 | 1.0555e-08 | 0.0076931 | 0.0076932 | 0.0076932 | 0.98662 | -0.094014 | 0.98657 | -0.094399 | 2.8493
125 | 0.0030449 | 0.00076278 | -0.0030445 | -0.00076303 | 4.2471e-07 | -2.4866e-07 | 0.0045925 | 0.0045926 | 0.0045926 | 0.98657 | -0.094399 | 0.98643 | -0.095407 | 1.701
126 | 0.0020559 | 0.00051488 | -0.0020558 | -0.00051499 | 6.488e-08 | -1.1313e-07 | 0.0031007 | 0.0031007 | 0.0031007 | 0.98657 | -0.094399 | 0.98654 | -0.094627 | 1.1484
127 | 0.00090676 | 0.00022701 | -0.00090674 | -0.00022725 | 2.2378e-08 | -2.362e-07 | 0.0013676 | 0.0013677 | 0.0013677 | 0.98654 | -0.094627 | 0.98651 | -0.094806 | 0.50655
128 | 0.0032834 | 0.00082233 | -0.0032831 | -0.00082246 | 2.8587e-07 | -1.2829e-07 | 0.0049535 | 0.0049536 | 0.0049536 | 0.98628 | -0.096489 | 0.98619 | -0.097119 | 1.8347
129 | 0.0023638 | 0.00059207 | -0.0023638 | -0.00059214 | 5.4876e-08 | -6.7104e-08 | 0.0035665 | 0.0035666 | 0.0035666 | 0.98619 | -0.097119 | 0.98616 | -0.097287 | 1.321
130 | 0.00084873 | 0.00021243 | -0.00084871 | -0.00021271 | 2.2567e-08 | -2.7269e-07 | 0.0012805 | 0.0012806 | 0.0012806 | 0.98616 | -0.097287 | 0.98614 | -0.097479 | 0.47431

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.068321 | 0.016908

## res_load
| p_mw | q_mvar
0 | 0.00023132 | 5.7974e-05
1 | 0.00034811 | 8.7245e-05
2 | 0.00012739 | 3.1928e-05
3 | 7.7714e-05 | 1.9477e-05
4 | 0.00034444 | 8.6325e-05
5 | 0.00042137 | 0.00010561
6 | 0.00060976 | 0.00015282
7 | 4.624e-05 | 1.1589e-05
8 | 0.00033984 | 8.5173e-05
9 | 9.0318e-05 | 2.2636e-05
10 | 0.00014312 | 3.587e-05
11 | 6.2381e-05 | 1.5634e-05
12 | 9.2049e-05 | 2.307e-05
13 | 6.089e-05 | 1.5261e-05
14 | 7.0267e-05 | 1.761e-05
15 | 0.00066609 | 0.00016694
16 | 0.0017793 | 0.00044593
17 | 4.0372e-05 | 1.0118e-05
18 | 0.00013445 | 3.3697e-05
19 | 5.7413e-05 | 1.4389e-05
20 | 0.00032086 | 8.0415e-05
21 | 0.00047468 | 0.00011897
22 | 0.00016411 | 4.1129e-05
23 | 0.00010154 | 2.5448e-05
24 | 0.00052656 | 0.00013197
25 | 0.00013348 | 3.3453e-05
26 | 0.00025276 | 6.3347e-05
27 | 0.0021836 | 0.00054727
28 | 0.00011896 | 2.9813e-05
29 | 0.00075605 | 0.00018948
30 | 0.0011387 | 0.00028539
31 | 0.00058262 | 0.00014602
32 | 0.0013766 | 0.000345
33 | 0.00036186 | 9.069e-05
34 | 0.00015308 | 3.8364e-05
35 | 0.00015971 | 4.0026e-05
36 | 0.0011716 | 0.00029363
37 | 0.00019379 | 4.8568e-05
38 | 0.0023981 | 0.00060103
39 | 0.00013067 | 3.275e-05
40 | 0.00046678 | 0.00011699
41 | 0.00098491 | 0.00024684
42 | 0.0001306 | 3.2731e-05
43 | 0.00077455 | 0.00019412
44 | 0.0053959 | 0.0013523
45 | 0.00013064 | 3.2743e-05
46 | 0.00013066 | 3.2746e-05
47 | 0.00035428 | 8.8792e-05
48 | 0.0001096 | 2.7469e-05
49 | 9.1355e-05 | 2.2896e-05
50 | 0.0011491 | 0.00028799
51 | 0.00012352 | 3.0957e-05
52 | 0.00034136 | 8.5554e-05
53 | 0.00026876 | 6.7357e-05
54 | 0.00065368 | 0.00016383
55 | 0.00032617 | 8.1745e-05
56 | 0.0022108 | 0.00055409
57 | 0.0021745 | 0.00054499
58 | 0.0014726 | 0.00036908
59 | 0.002193 | 0.00054962
60 | 0.00099581 | 0.00024957
61 | 0.00018724 | 4.6927e-05
62 | 0.00060492 | 0.00015161
63 | 0.00035301 | 8.8472e-05
64 | 0.00022868 | 5.7313e-05
65 | 6.7859e-05 | 1.7007e-05
66 | 0.0006108 | 0.00015308
67 | 5.3536e-05 | 1.3417e-05
68 | 0.00044145 | 0.00011064
69 | 0.0001121 | 2.8096e-05
70 | 5.9373e-05 | 1.488e-05
71 | 0.00012808 | 3.21e-05
72 | 0.0004938 | 0.00012376
73 | 0.00052491 | 0.00013155
74 | 0.00093708 | 0.00023485
75 | 0.0001893 | 4.7442e-05
76 | 0.00018286 | 4.583e-05
77 | 0.00054668 | 0.00013701
78 | 0.00016032 | 4.0179e-05
79 | 0.00016511 | 4.138e-05
80 | 0.00015432 | 3.8677e-05
81 | 0.0013091 | 0.00032809
82 | 0.00067813 | 0.00016996
83 | 0.00063082 | 0.0001581
84 | 0.0011275 | 0.00028258
85 | 0.00019823 | 4.9681e-05
86 | 0.0017019 | 0.00042654
87 | 0.00088247 | 0.00022117
88 | 0.00048881 | 0.00012251
89 | 0.0011572 | 0.00029001
90 | 0.0031724 | 0.00079508
91 | 0.00066632 | 0.000167
92 | 0.0030445 | 0.00076303
93 | 0.001149 | 0.00028798
94 | 0.00090674 | 0.00022725
95 | 0.00058252 | 0.00014599
96 | 0.00048977 | 0.00012275
97 | 0.00091927 | 0.00023039
98 | 0.001515 | 0.0003797
99 | 0.00084871 | 0.00021271

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1