## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1002-5_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1002-5_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1002-5_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1002-5_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1002-5_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1002-5_0_2_node_231 | 0.4 | n |  | TRUE
6 | bus_LV_1002-5_0_2_node_21 | 0.4 | n |  | TRUE
7 | bus_LV_1002-5_0_2_node_105 | 0.4 | n |  | TRUE
8 | bus_LV_1002-5_0_2_node_241 | 0.4 | n |  | TRUE
9 | bus_LV_1002-5_0_2_node_41 | 0.4 | n |  | TRUE
10 | bus_LV_1002-5_0_2_node_95 | 0.4 | n |  | TRUE
11 | bus_LV_1002-5_0_2_node_108 | 0.4 | n |  | TRUE
12 | bus_LV_1002-5_0_2_node_94 | 0.4 | n |  | TRUE
13 | bus_LV_1002-5_0_2_node_350 | 0.4 | n |  | TRUE
14 | bus_LV_1002-5_0_2_node_244 | 0.4 | n |  | TRUE
15 | bus_LV_1002-5_0_2_node_259 | 0.4 | n |  | TRUE
16 | bus_LV_1002-5_0_2_node_313 | 0.4 | n |  | TRUE
17 | bus_LV_1002-5_0_2_node_234 | 0.4 | n |  | TRUE
18 | bus_LV_1002-5_0_2_node_109 | 0.4 | n |  | TRUE
19 | bus_LV_1002-5_0_2_node_227 | 0.4 | n |  | TRUE
20 | bus_LV_1002-5_0_2_node_228 | 0.4 | n |  | TRUE
21 | bus_LV_1002-5_0_2_node_229 | 0.4 | n |  | TRUE
22 | bus_LV_1002-5_0_2_node_230 | 0.4 | n |  | TRUE
23 | bus_LV_1002-5_0_2_node_232 | 0.4 | n |  | TRUE
24 | bus_LV_1002-5_0_2_node_237 | 0.4 | n |  | TRUE
25 | bus_LV_1002-5_0_2_node_233 | 0.4 | n |  | TRUE
26 | bus_LV_1002-5_0_2_node_235 | 0.4 | n |  | TRUE
27 | bus_LV_1002-5_0_2_node_236 | 0.4 | n |  | TRUE
28 | bus_LV_1002-5_0_2_node_319 | 0.4 | n |  | TRUE
29 | bus_LV_1002-5_0_2_node_317 | 0.4 | n |  | TRUE
30 | bus_LV_1002-5_0_2_node_238 | 0.4 | n |  | TRUE
31 | bus_LV_1002-5_0_2_node_315 | 0.4 | n |  | TRUE
32 | bus_LV_1002-5_0_2_node_324 | 0.4 | n |  | TRUE
33 | bus_LV_1002-5_0_2_node_239 | 0.4 | n |  | TRUE
34 | bus_LV_1002-5_0_2_node_240 | 0.4 | n |  | TRUE
35 | bus_LV_1002-5_0_2_node_242 | 0.4 | n |  | TRUE
36 | bus_LV_1002-5_0_2_node_329 | 0.4 | n |  | TRUE
37 | bus_LV_1002-5_0_2_node_247 | 0.4 | n |  | TRUE
38 | bus_LV_1002-5_0_2_node_248 | 0.4 | n |  | TRUE
39 | bus_LV_1002-5_0_2_node_249 | 0.4 | n |  | TRUE
40 | bus_LV_1002-5_0_2_node_251 | 0.4 | n |  | TRUE
41 | bus_LV_1002-5_0_2_node_250 | 0.4 | n |  | TRUE
42 | bus_LV_1002-5_0_2_node_252 | 0.4 | n |  | TRUE
43 | bus_LV_1002-5_0_2_node_253 | 0.4 | n |  | TRUE
44 | bus_LV_1002-5_0_2_node_254 | 0.4 | n |  | TRUE
45 | bus_LV_1002-5_0_2_node_327 | 0.4 | n |  | TRUE
46 | bus_LV_1002-5_0_2_node_330 | 0.4 | n |  | TRUE
47 | bus_LV_1002-5_0_2_node_256 | 0.4 | n |  | TRUE
48 | bus_LV_1002-5_0_2_node_333 | 0.4 | n |  | TRUE
49 | bus_LV_1002-5_0_2_node_257 | 0.4 | n |  | TRUE
50 | bus_LV_1002-5_0_2_node_258 | 0.4 | n |  | TRUE
51 | bus_LV_1002-5_0_2_node_260 | 0.4 | n |  | TRUE
52 | bus_LV_1002-5_0_2_node_261 | 0.4 | n |  | TRUE
53 | bus_LV_1002-5_0_2_node_262 | 0.4 | n |  | TRUE
54 | bus_LV_1002-5_0_2_node_263 | 0.4 | n |  | TRUE
55 | bus_LV_1002-5_0_2_node_264 | 0.4 | n |  | TRUE
56 | bus_LV_1002-5_0_2_node_265 | 0.4 | n |  | TRUE
57 | bus_LV_1002-5_0_2_node_266 | 0.4 | n |  | TRUE
58 | bus_LV_1002-5_0_2_node_339 | 0.4 | n |  | TRUE
59 | bus_LV_1002-5_0_2_node_267 | 0.4 | n |  | TRUE
60 | bus_LV_1002-5_0_2_node_300 | 0.4 | n |  | TRUE
61 | bus_LV_1002-5_0_2_node_301 | 0.4 | n |  | TRUE
62 | bus_LV_1002-5_0_2_node_302 | 0.4 | n |  | TRUE
63 | bus_LV_1002-5_0_2_node_303 | 0.4 | n |  | TRUE
64 | bus_LV_1002-5_0_2_node_304 | 0.4 | n |  | TRUE
65 | bus_LV_1002-5_0_2_node_311 | 0.4 | n |  | TRUE
66 | bus_LV_1002-5_0_2_node_305 | 0.4 | n |  | TRUE
67 | bus_LV_1002-5_0_2_node_306 | 0.4 | n |  | TRUE
68 | bus_LV_1002-5_0_2_node_307 | 0.4 | n |  | TRUE
69 | bus_LV_1002-5_0_2_node_308 | 0.4 | n |  | TRUE
70 | bus_LV_1002-5_0_2_node_309 | 0.4 | n |  | TRUE
71 | bus_LV_1002-5_0_2_node_310 | 0.4 | n |  | TRUE
72 | bus_LV_1002-5_0_2_node_341 | 0.4 | n |  | TRUE
73 | bus_LV_1002-5_0_2_node_349 | 0.4 | n |  | TRUE
74 | bus_LV_1002-5_0_2_node_348 | 0.4 | n |  | TRUE
75 | bus_LV_1002-5_0_2_node_312 | 0.4 | n |  | TRUE
76 | bus_LV_1002-5_0_2_node_314 | 0.4 | n |  | TRUE
77 | bus_LV_1002-5_0_2_node_316 | 0.4 | n |  | TRUE
78 | bus_LV_1002-5_0_2_node_318 | 0.4 | n |  | TRUE
79 | bus_LV_1002-5_0_2_node_320 | 0.4 | n |  | TRUE
80 | bus_LV_1002-5_0_2_node_322 | 0.4 | n |  | TRUE
81 | bus_LV_1002-5_0_2_node_325 | 0.4 | n |  | TRUE
82 | bus_LV_1002-5_0_2_node_321 | 0.4 | n |  | TRUE
83 | bus_LV_1002-5_0_2_node_323 | 0.4 | n |  | TRUE
84 | bus_LV_1002-5_0_2_node_334 | 0.4 | n |  | TRUE
85 | bus_LV_1002-5_0_2_node_347 | 0.4 | n |  | TRUE
86 | bus_LV_1002-5_0_2_node_342 | 0.4 | n |  | TRUE
87 | bus_LV_1002-5_0_2_node_328 | 0.4 | n |  | TRUE
88 | bus_LV_1002-5_0_2_node_326 | 0.4 | n |  | TRUE
89 | bus_LV_1002-5_0_2_node_331 | 0.4 | n |  | TRUE
90 | bus_LV_1002-5_0_2_node_332 | 0.4 | n |  | TRUE
91 | bus_LV_1002-5_0_2_node_335 | 0.4 | n |  | TRUE
92 | bus_LV_1002-5_0_2_node_340 | 0.4 | n |  | TRUE
93 | bus_LV_1002-5_0_2_node_337 | 0.4 | n |  | TRUE
94 | bus_LV_1002-5_0_2_node_336 | 0.4 | n |  | TRUE
95 | bus_LV_1002-5_0_2_node_338 | 0.4 | n |  | TRUE
96 | bus_MV_0_node_317 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1002-5_0_2_load_0 | 0 | 0.0011697 | 0.00029315 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1002-5_0_2_load_1 | 1 | 0.00050791 | 0.00012729 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1002-5_0_2_load_3 | 3 | 0.00036421 | 9.128e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1002-5_0_2_load_4 | 4 | 6.812e-05 | 1.7072e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1002-5_0_2_load_108 | 11 | 0.0012647 | 0.00031697 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1002-5_0_2_load_350 | 13 | 0.00062088 | 0.00015561 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1002-5_0_2_load_313 | 16 | 0.00046997 | 0.00011779 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1002-5_0_2_load_234 | 17 | 0.0014633 | 0.00036673 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1002-5_0_2_load_109 | 18 | 0.00055356 | 0.00013873 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1002-5_0_2_load_227 | 19 | 0.00010781 | 2.7019e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1002-5_0_2_load_228 | 20 | 0.00026607 | 6.6684e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1002-5_0_2_load_229 | 21 | 7.58e-05 | 1.8997e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1002-5_0_2_load_230 | 22 | 0.0001636 | 4.1001e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1002-5_0_2_load_232 | 23 | 0.00043356 | 0.00010866 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1002-5_0_2_load_233 | 25 | 0.00045119 | 0.00011308 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1002-5_0_2_load_235 | 26 | 0.0010291 | 0.00025792 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1002-5_0_2_load_317 | 29 | 0.00079487 | 0.00019921 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1002-5_0_2_load_315 | 31 | 0.00016701 | 4.1856e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1002-5_0_2_load_324 | 32 | 0.001227 | 0.00030751 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1002-5_0_2_load_239 | 33 | 0.00012714 | 3.1864e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1002-5_0_2_load_240 | 34 | 0.00032339 | 8.1048e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1002-5_0_2_load_242 | 35 | 0.00026744 | 6.7026e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1002-5_0_2_load_329 | 36 | 0.0001418 | 3.5539e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1002-5_0_2_load_247 | 37 | 8.2667e-05 | 2.0718e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1002-5_0_2_load_248 | 38 | 7.5917e-05 | 1.9027e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1002-5_0_2_load_249 | 39 | 0.00018681 | 4.6819e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1002-5_0_2_load_251 | 40 | 0.00052549 | 0.0001317 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1002-5_0_2_load_253 | 43 | 0.00021947 | 5.5003e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1002-5_0_2_load_327 | 45 | 0.00012935 | 3.2417e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1002-5_0_2_load_333 | 48 | 0.00029267 | 7.335e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1002-5_0_2_load_257 | 49 | 9.3427e-05 | 2.3415e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1002-5_0_2_load_258 | 50 | 0.00013135 | 3.292e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1002-5_0_2_load_260 | 51 | 4.1991e-05 | 1.0524e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1002-5_0_2_load_261 | 52 | 0.0010785 | 0.0002703 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1002-5_0_2_load_262 | 53 | 0.00034907 | 8.7484e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1002-5_0_2_load_264 | 55 | 0.00034657 | 8.6857e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1002-5_0_2_load_266 | 57 | 0.00012519 | 3.1377e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1002-5_0_2_load_339 | 58 | 0.00050118 | 0.00012561 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1002-5_0_2_load_267 | 59 | 0.00011788 | 2.9543e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1002-5_0_2_load_300 | 60 | 0.0008811 | 0.00022082 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1002-5_0_2_load_301 | 61 | 0.00033629 | 8.4281e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1002-5_0_2_load_302 | 62 | 0.00067495 | 0.00016916 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1002-5_0_2_load_304 | 64 | 0.00090754 | 0.00022745 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1002-5_0_2_load_311 | 65 | 0.00050011 | 0.00012534 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1002-5_0_2_load_305 | 66 | 0.00046035 | 0.00011537 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1002-5_0_2_load_306 | 67 | 0.00063209 | 0.00015842 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1002-5_0_2_load_308 | 69 | 0.00061934 | 0.00015522 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1002-5_0_2_load_341 | 72 | 0.00047097 | 0.00011804 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1002-5_0_2_load_349 | 73 | 0.00019477 | 4.8814e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1002-5_0_2_load_348 | 74 | 0.00045599 | 0.00011428 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1002-5_0_2_load_312 | 75 | 0.001199 | 0.00030049 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1002-5_0_2_load_314 | 76 | 0.00019774 | 4.9558e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1002-5_0_2_load_316 | 77 | 0.00012448 | 3.1196e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1002-5_0_2_load_320 | 79 | 0.0019895 | 0.00049861 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1002-5_0_2_load_325 | 81 | 0.00046486 | 0.00011651 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1002-5_0_2_load_334 | 84 | 0.00016255 | 4.074e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1002-5_0_2_load_347 | 85 | 0.00026789 | 6.714e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1002-5_0_2_load_342 | 86 | 0.0012043 | 0.00030182 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1002-5_0_2_load_328 | 87 | 0.0001668 | 4.1805e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1002-5_0_2_load_326 | 88 | 0.0003229 | 8.0926e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1002-5_0_2_load_331 | 89 | 9.505e-05 | 2.3822e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1002-5_0_2_load_332 | 90 | 0.00061476 | 0.00015407 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1002-5_0_2_load_337 | 93 | 0.00029498 | 7.3929e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1002-5_0_2_load_336 | 94 | 0.0017917 | 0.00044904 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1002-5_0_2_load_338 | 95 | 0.00060464 | 0.00015154 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1002-5_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0051639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1002-5_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.016229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1002-5_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.045328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1002-5_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.1793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1002-5_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.031787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1002-5_0_2_line_5 | NAYY 4x150 SE | 5 | 23 | 0.022495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1002-5_0_2_line_6 | NAYY 4x150 SE | 5 | 22 | 0.017549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1002-5_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.006009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1002-5_0_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.10663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1002-5_0_2_line_9 | NAYY 4x150 SE | 7 | 17 | 0.091691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1002-5_0_2_line_10 | NAYY 4x150 SE | 8 | 30 | 0.16434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1002-5_0_2_line_11 | NAYY 4x150 SE | 8 | 33 | 0.043596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1002-5_0_2_line_12 | NAYY 4x150 SE | 9 | 10 | 0.37027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1002-5_0_2_line_13 | NAYY 4x150 SE | 9 | 11 | 0.064721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1002-5_0_2_line_14 | NAYY 4x150 SE | 10 | 15 | 0.092023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1002-5_0_2_line_15 | NAYY 4x150 SE | 10 | 16 | 0.11457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1002-5_0_2_line_16 | NAYY 4x150 SE | 11 | 18 | 0.019593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1002-5_0_2_line_17 | NAYY 4x150 SE | 12 | 13 | 0.035686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1002-5_0_2_line_18 | NAYY 4x150 SE | 12 | 14 | 0.13299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1002-5_0_2_line_19 | NAYY 4x150 SE | 14 | 36 | 0.16186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1002-5_0_2_line_20 | NAYY 4x150 SE | 15 | 52 | 0.12204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1002-5_0_2_line_21 | NAYY 4x150 SE | 15 | 49 | 0.21136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1002-5_0_2_line_22 | NAYY 4x150 SE | 17 | 25 | 0.020597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1002-5_0_2_line_23 | NAYY 4x150 SE | 19 | 20 | 0.023329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1002-5_0_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.01277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1002-5_0_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.045762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1002-5_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.052397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1002-5_0_2_line_27 | NAYY 4x150 SE | 24 | 30 | 0.13431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1002-5_0_2_line_28 | NAYY 4x150 SE | 24 | 31 | 0.067859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1002-5_0_2_line_29 | NAYY 4x150 SE | 25 | 26 | 0.014252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1002-5_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.004923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1002-5_0_2_line_31 | NAYY 4x150 SE | 27 | 29 | 0.013738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1002-5_0_2_line_32 | NAYY 4x150 SE | 28 | 81 | 0.039404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1002-5_0_2_line_33 | NAYY 4x150 SE | 28 | 32 | 0.078397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1002-5_0_2_line_34 | NAYY 4x150 SE | 29 | 78 | 0.13551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1002-5_0_2_line_35 | NAYY 4x150 SE | 30 | 32 | 0.055398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1002-5_0_2_line_36 | NAYY 4x150 SE | 31 | 76 | 0.0074534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1002-5_0_2_line_37 | NAYY 4x150 SE | 33 | 34 | 0.018992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1002-5_0_2_line_38 | NAYY 4x150 SE | 34 | 35 | 0.0048955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1002-5_0_2_line_39 | NAYY 4x150 SE | 36 | 42 | 0.031428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1002-5_0_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.013941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1002-5_0_2_line_41 | NAYY 4x150 SE | 37 | 39 | 0.016323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1002-5_0_2_line_42 | NAYY 4x150 SE | 39 | 40 | 0.00021904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1002-5_0_2_line_43 | NAYY 4x150 SE | 40 | 44 | 0.027124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1002-5_0_2_line_44 | NAYY 4x150 SE | 41 | 42 | 0.005812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1002-5_0_2_line_45 | NAYY 4x150 SE | 41 | 43 | 0.024673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1002-5_0_2_line_46 | NAYY 4x150 SE | 42 | 45 | 0.027669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1002-5_0_2_line_47 | NAYY 4x150 SE | 43 | 46 | 0.051471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1002-5_0_2_line_48 | NAYY 4x150 SE | 44 | 47 | 0.058472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1002-5_0_2_line_49 | NAYY 4x150 SE | 45 | 88 | 0.012972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1002-5_0_2_line_50 | NAYY 4x150 SE | 46 | 89 | 0.0085356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1002-5_0_2_line_51 | NAYY 4x150 SE | 46 | 47 | 0.12559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1002-5_0_2_line_52 | NAYY 4x150 SE | 47 | 48 | 0.13712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1002-5_0_2_line_53 | NAYY 4x150 SE | 49 | 50 | 0.020524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1002-5_0_2_line_54 | NAYY 4x150 SE | 50 | 51 | 0.019173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1002-5_0_2_line_55 | NAYY 4x150 SE | 51 | 53 | 0.024619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1002-5_0_2_line_56 | NAYY 4x150 SE | 53 | 54 | 0.079149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1002-5_0_2_line_57 | NAYY 4x150 SE | 54 | 55 | 0.10327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1002-5_0_2_line_58 | NAYY 4x150 SE | 54 | 56 | 0.35229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1002-5_0_2_line_59 | NAYY 4x150 SE | 55 | 57 | 0.0073743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1002-5_0_2_line_60 | NAYY 4x150 SE | 56 | 58 | 0.32979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1002-5_0_2_line_61 | NAYY 4x150 SE | 57 | 59 | 0.0041057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1002-5_0_2_line_62 | NAYY 4x150 SE | 58 | 95 | 0.064059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1002-5_0_2_line_63 | NAYY 4x150 SE | 60 | 61 | 0.028044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1002-5_0_2_line_64 | NAYY 4x150 SE | 60 | 62 | 0.038128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1002-5_0_2_line_65 | NAYY 4x150 SE | 61 | 63 | 0.0079759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1002-5_0_2_line_66 | NAYY 4x150 SE | 63 | 64 | 0.029815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1002-5_0_2_line_67 | NAYY 4x150 SE | 63 | 65 | 0.22247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1002-5_0_2_line_68 | NAYY 4x150 SE | 65 | 75 | 0.020597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1002-5_0_2_line_69 | NAYY 4x150 SE | 65 | 71 | 0.011384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1002-5_0_2_line_70 | NAYY 4x150 SE | 66 | 67 | 0.30494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1002-5_0_2_line_71 | NAYY 4x150 SE | 66 | 68 | 0.018187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1002-5_0_2_line_72 | NAYY 4x150 SE | 67 | 69 | 0.023751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1002-5_0_2_line_73 | NAYY 4x150 SE | 68 | 70 | 0.18846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1002-5_0_2_line_74 | NAYY 4x150 SE | 68 | 71 | 0.019776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1002-5_0_2_line_75 | NAYY 4x150 SE | 69 | 72 | 0.010034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1002-5_0_2_line_76 | NAYY 4x150 SE | 70 | 73 | 0.026285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1002-5_0_2_line_77 | NAYY 4x150 SE | 70 | 74 | 0.006565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1002-5_0_2_line_78 | NAYY 4x150 SE | 72 | 83 | 0.036085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1002-5_0_2_line_79 | NAYY 4x150 SE | 76 | 77 | 0.021595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1002-5_0_2_line_80 | NAYY 4x150 SE | 78 | 79 | 0.028831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1002-5_0_2_line_81 | NAYY 4x150 SE | 78 | 80 | 0.02762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1002-5_0_2_line_82 | NAYY 4x150 SE | 80 | 85 | 0.035553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1002-5_0_2_line_83 | NAYY 4x150 SE | 80 | 82 | 0.027835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1002-5_0_2_line_84 | NAYY 4x150 SE | 81 | 87 | 0.039413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1002-5_0_2_line_85 | NAYY 4x150 SE | 82 | 83 | 0.20384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1002-5_0_2_line_86 | NAYY 4x150 SE | 82 | 84 | 0.057725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1002-5_0_2_line_87 | NAYY 4x150 SE | 83 | 86 | 0.014903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1002-5_0_2_line_88 | NAYY 4x150 SE | 86 | 92 | 0.014261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1002-5_0_2_line_89 | NAYY 4x150 SE | 87 | 88 | 0.010281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1002-5_0_2_line_90 | NAYY 4x150 SE | 89 | 90 | 0.0257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1002-5_0_2_line_91 | NAYY 4x150 SE | 91 | 92 | 0.005429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1002-5_0_2_line_92 | NAYY 4x150 SE | 91 | 93 | 0.27705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1002-5_0_2_line_93 | NAYY 4x150 SE | 93 | 94 | 0.0044542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1002-5_0_2_line_94 | NAYY 4x150 SE | 94 | 95 | 0.029092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1002-5_0_2_trafo_317 | 0.25 MVA 20/0.4 kV | 96 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33
0 | 2648047.9781 | 1207137.6347 | 2648050.7088 | 1207142.0175
1 | 2648059.2911 | 1207155.7918 | 2648050.7088 | 1207142.0175
2 | 2648059.2911 | 1207155.7918 | 2648051.3008 | 1207183.0099 | 2648049.1708 | 1207187.8401 | 2648047.058 | 1207190.5469 | 2648044.8177 | 1207192.0742 | 2648039.6082 | 1207193.9493
3 | 2648059.2911 | 1207155.7918 | 2648068.0263 | 1207163.5666 | 2648182.1624 | 1207283.1332 | 2648183.8379 | 1207284.7221
4 | 2648211.7801 | 1207299.0259 | 2648202.2192 | 1207295.6245 | 2648197.3584 | 1207293.9955 | 2648192.9048 | 1207291.8361 | 2648187.4597 | 1207288.1567 | 2648183.8379 | 1207284.7221
5 | 2648211.7801 | 1207299.0259 | 2648213.7048 | 1207294.2053 | 2648216.3192 | 1207289.6571 | 2648218.9008 | 1207286.3538 | 2648221.9209 | 1207283.3542 | 2648224.6085 | 1207280.945
6 | 2648211.7801 | 1207299.0259 | 2648208.6161 | 1207316.2868
7 | 2648463.2732 | 1207473.5179 | 2648457.3435 | 1207472.4469
8 | 2648436.9744 | 1207370.189 | 2648449.9151 | 1207422.7578 | 2648463.2732 | 1207473.5179
9 | 2648457.3435 | 1207472.4469 | 2648454.6558 | 1207471.9582 | 2648444.2314 | 1207470.0725 | 2648415.5377 | 1207459.4893 | 2648405.9513 | 1207458.3443 | 2648400.8833 | 1207458.8368 | 2648392.0554 | 1207463.5458 | 2648381.5974 | 1207471.4324 | 2648371.8739 | 1207473.4601
10 | 2648436.9744 | 1207370.189 | 2648422.6643 | 1207312.0614 | 2648402.9667 | 1207233.7451 | 2648400.381 | 1207223.4738 | 2648399.128 | 1207218.583 | 2648397.1232 | 1207210.7511
11 | 2648436.9744 | 1207370.189 | 2648480.1587 | 1207364.2136 | 2648480.1587 | 1207364.2136
12 | 2649022.3237 | 1207385.8064 | 2649040.5353 | 1207376.4616 | 2649049.1108 | 1207372.9299 | 2649057.5856 | 1207370.5648 | 2649065.8151 | 1207369.365 | 2649084.8903 | 1207368.7436 | 2649090.8159 | 1207367.536 | 2649096.1673 | 1207365.8791 | 2649101.3044 | 1207362.5527 | 2649111.1666 | 1207353.2839 | 2649119.4153 | 1207342.3676 | 2649124.469 | 1207323.2981 | 2649131.5403 | 1207306.691 | 2649145.6196 | 1207281.1809 | 2649160.8829 | 1207260.5722 | 2649174.0541 | 1207245.6386 | 2649216.0285 | 1207201.2473 | 2649220.9552 | 1207197.6303 | 2649225.4546 | 1207196.0442 | 2649252.4545 | 1207186.1054 | 2649265.9697 | 1207179.3018 | 2649279.9155 | 1207170.067 | 2649291.8204 | 1207161.2156
13 | 2649291.8204 | 1207161.2156 | 2649289.4627 | 1207150.212 | 2649284.2571 | 1207138.7846 | 2649276.1891 | 1207127.745 | 2649263.953 | 1207115.9149 | 2649256.0708 | 1207109.4141
14 | 2649022.3237 | 1207385.8064 | 2649007.812 | 1207344.5967 | 2649005.64 | 1207336.8633 | 2649005.1207 | 1207333.4237 | 2649005.4276 | 1207329.3905 | 2649006.5562 | 1207325.2863 | 2649018.8349 | 1207299.5276
15 | 2649022.3237 | 1207385.8064 | 2649014.6317 | 1207385.4542 | 2649003.1643 | 1207381.8691 | 2648996.9645 | 1207380.3619 | 2648991.2466 | 1207379.4255 | 2648982.3262 | 1207379.5747 | 2648974.5489 | 1207380.3447 | 2648965.0401 | 1207381.7787 | 2648958.1549 | 1207382.2559 | 2648952.2559 | 1207382.0741 | 2648938.4214 | 1207379.7038 | 2648916.7275 | 1207373.2779 | 2648910.2548 | 1207370.9974
16 | 2649240.9551 | 1207096.9476 | 2649256.0708 | 1207109.4141
17 | 2648646.0981 | 1207394.558 | 2648653.3866 | 1207380.0423 | 2648657.7007 | 1207374.1073 | 2648660.9053 | 1207370.876 | 2648663.1836 | 1207369.3603 | 2648667.707 | 1207367.5961
18 | 2648621.6644 | 1207252.0874 | 2648626.7157 | 1207255.5305 | 2648631.4918 | 1207259.1604 | 2648635.6662 | 1207262.9077 | 2648639.7954 | 1207267.5328 | 2648643.3461 | 1207272.2312 | 2648646.1099 | 1207276.4561 | 2648669.888 | 1207319.2525 | 2648671.5129 | 1207323.2569 | 2648672.8202 | 1207327.9926 | 2648672.9619 | 1207332.0627 | 2648672.7455 | 1207335.2851 | 2648667.7784 | 1207366.296 | 2648667.707 | 1207367.5961
19 | 2648621.6644 | 1207252.0874 | 2648616.1318 | 1207247.0505 | 2648610.3017 | 1207241.1886 | 2648575.9543 | 1207204.8325 | 2648569.2016 | 1207198.3516 | 2648562.8338 | 1207193.1412 | 2648558.304 | 1207190.0804 | 2648553.7161 | 1207187.6084 | 2648544.8439 | 1207183.6673 | 2648527.3483 | 1207176.999 | 2648517.9995 | 1207172.754 | 2648505.4827 | 1207165.348 | 2648501.2006 | 1207161.7334 | 2648498.3676 | 1207158.5196 | 2648495.7654 | 1207154.6039
20 | 2649018.8349 | 1207299.5276 | 2649013.0839 | 1207288.7185 | 2649007.6451 | 1207279.7131 | 2648998.3842 | 1207266.674 | 2648986.397 | 1207248.5652 | 2648965.5 | 1207234.8525 | 2648955.9954 | 1207225.547 | 2648941.0494 | 1207207.5363
21 | 2649018.8349 | 1207299.5276 | 2649022.6521 | 1207292.1101 | 2649025.4732 | 1207285.6184 | 2649027.2032 | 1207280.5074 | 2649028.1653 | 1207275.3901 | 2649028.3211 | 1207269.3768 | 2649027.6208 | 1207255.5852 | 2649025.3658 | 1207235.7329 | 2649023.8642 | 1207221.3567 | 2649023.6227 | 1207214.6508 | 2649024.0867 | 1207206.2942 | 2649027.6231 | 1207174.7382 | 2649027.8473 | 1207168.7366 | 2649027.7377 | 1207164.4887 | 2649026.621 | 1207159.7324 | 2649024.6989 | 1207153.9688 | 2649013.4907 | 1207128.0173 | 2649011.6897 | 1207122.3214 | 2649010.3257 | 1207116.1955 | 2649009.0938 | 1207106.9356 | 2649009.3136 | 1207099.6109 | 2649010.3645 | 1207093.8607
22 | 2648351.5875 | 1207473.027 | 2648353.3305 | 1207473.8605 | 2648366.9205 | 1207474.4931 | 2648371.8739 | 1207473.4601
23 | 2648163.7191 | 1207383.0746 | 2648163.7846 | 1207382.9652 | 2648178.9065 | 1207365.3685
24 | 2648178.9065 | 1207365.3685 | 2648187.2297 | 1207355.6831
25 | 2648187.2297 | 1207355.6831 | 2648199.8301 | 1207341.0205 | 2648205.7909 | 1207328.8504 | 2648208.5507 | 1207316.6434 | 2648208.6161 | 1207316.2868
26 | 2648271.6964 | 1207258.7752 | 2648236.6442 | 1207272.7113 | 2648232.369 | 1207274.8225 | 2648228.6074 | 1207277.3602 | 2648224.6085 | 1207280.945
27 | 2648271.6964 | 1207258.7752 | 2648390.7623 | 1207213.1343 | 2648397.1232 | 1207210.7511
28 | 2648271.6964 | 1207258.7752 | 2648205.022 | 1207246.1503
29 | 2648341.9544 | 1207463.6736 | 2648344.8397 | 1207469.8005 | 2648351.5875 | 1207473.027
30 | 2648358.6754 | 1207082.443 | 2648363.468 | 1207081.2589
31 | 2648358.6754 | 1207082.443 | 2648355.2079 | 1207069.15
32 | 2648363.468 | 1207081.2589 | 2648366.9728 | 1207080.409 | 2648376.3488 | 1207079.4399 | 2648379.5047 | 1207080.3549 | 2648381.6189 | 1207081.2614 | 2648396.8282 | 1207095.4283
33 | 2648363.468 | 1207081.2589 | 2648366.4029 | 1207092.5559 | 2648383.1877 | 1207157.1348
34 | 2648321.5742 | 1206937.8811 | 2648324.8452 | 1206950.8817 | 2648352.4214 | 1207058.4673 | 2648355.2079 | 1207069.15
35 | 2648397.1232 | 1207210.7511 | 2648383.1877 | 1207157.1348
36 | 2648198.2589 | 1207243.4194 | 2648199.1666 | 1207244.2589 | 2648201.385 | 1207245.4331 | 2648204.9683 | 1207246.1402 | 2648205.022 | 1207246.1503
37 | 2648480.1587 | 1207364.2136 | 2648482.6684 | 1207363.2223 | 2648484.2902 | 1207362.0125 | 2648484.9274 | 1207360.3167 | 2648485.0278 | 1207358.2607 | 2648483.8784 | 1207347.9239
38 | 2648483.8784 | 1207347.9239 | 2648483.3374 | 1207343.0584
39 | 2648478.3702 | 1207128.4287 | 2648495.7654 | 1207154.6039
40 | 2648684.923 | 1207108.102 | 2648684.5138 | 1207108.9827 | 2648683.6514 | 1207110.2987 | 2648681.7867 | 1207112.3736 | 2648678.8804 | 1207114.4289 | 2648674.4352 | 1207116.8199
41 | 2648684.923 | 1207108.102 | 2648685.4348 | 1207107.0002 | 2648685.8941 | 1207104.7693 | 2648685.8878 | 1207101.812 | 2648684.6591 | 1207092.0151
42 | 2648684.6319 | 1207091.7978 | 2648684.6591 | 1207092.0151
43 | 2648695.5545 | 1207069.8722 | 2648693.6541 | 1207070.7239 | 2648688.9444 | 1207073.8651 | 2648686.5194 | 1207076.5691 | 2648685.1766 | 1207078.9818 | 2648684.2908 | 1207082.2432 | 2648683.9743 | 1207086.5542 | 2648684.6319 | 1207091.7978
44 | 2648484.0631 | 1207129.6756 | 2648478.3702 | 1207128.4287
45 | 2648484.0631 | 1207129.6756 | 2648483.4117 | 1207105.0116
46 | 2648478.3702 | 1207128.4287 | 2648451.3444 | 1207122.4996
47 | 2648526.5701 | 1207079.0803 | 2648525.6333 | 1207081.1405 | 2648524.3825 | 1207082.5312 | 2648517.8484 | 1207085.6132 | 2648502.7755 | 1207090.4937 | 2648500.6609 | 1207091.5104 | 2648497.7715 | 1207093.3658 | 2648493.7386 | 1207096.5127 | 2648483.4117 | 1207105.0116
48 | 2648695.5545 | 1207069.8722 | 2648693.2495 | 1207066.2513 | 2648692.003 | 1207065.2517 | 2648689.5057 | 1207064.7088 | 2648680.4238 | 1207065.0239 | 2648674.2345 | 1207064.9734 | 2648672.2778 | 1207064.346 | 2648670.1078 | 1207062.8274 | 2648668.8725 | 1207061.3832 | 2648667.0736 | 1207057.255 | 2648665.7031 | 1207055.5985 | 2648663.6091 | 1207054.0805 | 2648660.7801 | 1207053.1903 | 2648651.4385 | 1207052.7139 | 2648644.7221 | 1207052.9594
49 | 2648438.6739 | 1207119.7199 | 2648451.3444 | 1207122.4996
50 | 2648526.5701 | 1207079.0803 | 2648526.5441 | 1207076.6676 | 2648525.9965 | 1207072.9387 | 2648525.1177 | 1207070.755
51 | 2648526.5701 | 1207079.0803 | 2648538.9197 | 1207083.6833 | 2648546.6701 | 1207085.325 | 2648552.8616 | 1207085.1085 | 2648556.9681 | 1207084.1302 | 2648560.7202 | 1207082.7933 | 2648606.4395 | 1207059.9296 | 2648613.8464 | 1207057.066 | 2648621.1659 | 1207054.6575 | 2648630.3766 | 1207053.4651 | 2648644.7221 | 1207052.9594
52 | 2648644.7221 | 1207052.9594 | 2648649.514 | 1207048.1289 | 2648654.3453 | 1207040.3415 | 2648672.1952 | 1207005.4556 | 2648673.39 | 1206999.7397 | 2648673.0558 | 1206986.6294 | 2648669.3359 | 1206955.0919 | 2648669.653 | 1206948.8464 | 2648671.2109 | 1206942.4331 | 2648674.359 | 1206934.9767 | 2648678.2861 | 1206929.9057 | 2648680.8959 | 1206927.0171
53 | 2649010.3645 | 1207093.8607 | 2649012.0481 | 1207088.8604 | 2649015.7332 | 1207080.8749 | 2649019.3123 | 1207075.5055
54 | 2649019.3123 | 1207075.5055 | 2649020.0522 | 1207074.3955 | 2649031.1698 | 1207060.4445
55 | 2649031.1698 | 1207060.4445 | 2649036.0719 | 1207054.2931 | 2649039.4145 | 1207050.9741 | 2649041.8953 | 1207048.9044 | 2649049.76 | 1207044.9299
56 | 2649096.3676 | 1206992.9304 | 2649092.0547 | 1206996.7972 | 2649089.5365 | 1206999.7115 | 2649087.3539 | 1207003.4402 | 2649085.688 | 1207008.1292 | 2649085.3356 | 1207013.0737 | 2649086.0015 | 1207023.652 | 2649085.6528 | 1207026.2951 | 2649084.6957 | 1207028.9443 | 2649082.6132 | 1207031.5954 | 2649079.5989 | 1207033.8164 | 2649075.0058 | 1207035.6908 | 2649068.4723 | 1207036.7934 | 2649061.5728 | 1207038.9602 | 2649049.76 | 1207044.9299
57 | 2649096.3676 | 1206992.9304 | 2649114.1695 | 1206994.7222 | 2649121.0359 | 1206994.7453 | 2649124.1286 | 1206994.0926 | 2649126.7709 | 1206992.7247 | 2649128.6295 | 1206990.4831 | 2649130.2066 | 1206986.427 | 2649133.0507 | 1206972.5424 | 2649137.8672 | 1206954.6271 | 2649138.7641 | 1206949.1313 | 2649138.7882 | 1206944.3509 | 2649138.6476 | 1206938.3352 | 2649138.9909 | 1206935.4363 | 2649139.7864 | 1206932.0965 | 2649142.1359 | 1206928.4248 | 2649144.9732 | 1206923.9314
58 | 2648902.8532 | 1206831.7495 | 2648909.372 | 1206831.5249 | 2648917.4102 | 1206829.6341 | 2648923.4412 | 1206827.6935 | 2648927.3435 | 1206827.5364 | 2648931.0389 | 1206828.5006 | 2648940.928 | 1206831.8057 | 2648948.2046 | 1206832.8326 | 2648968.0435 | 1206832.0169 | 2648972.0838 | 1206830.8049 | 2648974.7496 | 1206828.4254 | 2648978.0351 | 1206825.6062 | 2648982.7099 | 1206821.1976 | 2648987.6357 | 1206818.6476 | 2649022.4821 | 1206803.4691 | 2649027.4453 | 1206819.508 | 2649027.3952 | 1206825.6111 | 2649024.053 | 1206835.3449 | 2649021.5511 | 1206841.8281 | 2649022.9051 | 1206851.0446 | 2649027.1081 | 1206860.5735 | 2649029.4797 | 1206869.954 | 2649030.2067 | 1206880.5106 | 2649032.1276 | 1206894.7568 | 2649029.2061 | 1206903.2711 | 2649030.1358 | 1206914.1406 | 2649038.2431 | 1206937.1428 | 2649048.8231 | 1206959.9873 | 2649055.908 | 1206970.4405 | 2649061.0592 | 1206976.5419 | 2649064.8289 | 1206979.5524 | 2649072.6976 | 1206983.4526 | 2649088.6549 | 1206990.41 | 2649096.3676 | 1206992.9304
59 | 2649144.9732 | 1206923.9314 | 2649148.3305 | 1206918.6145 | 2649149.198 | 1206917.961
60 | 2648902.8532 | 1206831.7495 | 2648899.0402 | 1206831.2179 | 2648894.1929 | 1206829.7663 | 2648886.5151 | 1206824.8006 | 2648862.594 | 1206810.5744 | 2648848.7656 | 1206801.7117 | 2648836.0906 | 1206793.1476 | 2648829.0277 | 1206789.232 | 2648819.0217 | 1206785.3369 | 2648807.4851 | 1206782.6188 | 2648787.5385 | 1206779.8431 | 2648770.4639 | 1206778.3028 | 2648751.7452 | 1206777.872 | 2648743.4753 | 1206778.3493 | 2648736.7807 | 1206777.7499 | 2648729.4392 | 1206775.3441 | 2648722.0153 | 1206771.8482 | 2648716.8332 | 1206767.6146 | 2648712.5677 | 1206761.9543 | 2648710.4524 | 1206757.4456 | 2648709.7153 | 1206751.7807 | 2648709.4274 | 1206740.4607 | 2648708.0722 | 1206734.1348 | 2648706.5241 | 1206730.0087 | 2648701.5487 | 1206724.6762 | 2648697.4161 | 1206722.2855 | 2648693.8527 | 1206720.9668 | 2648688.4845 | 1206720.8897 | 2648678.6959 | 1206722.0217 | 2648668.2973 | 1206724.2827 | 2648663.3502 | 1206725.7211 | 2648653.8364 | 1206730.4574 | 2648644.0331 | 1206734.3243 | 2648625.0443 | 1206740.1149
61 | 2649149.198 | 1206917.961 | 2649151.1923 | 1206916.459 | 2649152.7555 | 1206916.0774
62 | 2648563.113 | 1206755.7819 | 2648564.8951 | 1206755.5594 | 2648581.9631 | 1206753.2524 | 2648625.0443 | 1206740.1149
63 | 2647739.4065 | 1206748.1847 | 2647740.2156 | 1206752.3217 | 2647745.0026 | 1206766.1124 | 2647747.1143 | 1206773.0667 | 2647747.1886 | 1206775.0285
64 | 2647739.4065 | 1206748.1847 | 2647737.6001 | 1206738.9486 | 2647736.4038 | 1206729.7449 | 2647735.7685 | 1206713.1413 | 2647735.8527 | 1206710.3224
65 | 2647745.7985 | 1206782.6061 | 2647747.3655 | 1206779.6947 | 2647747.1886 | 1206775.0285
66 | 2647745.7985 | 1206782.6061 | 2647742.5454 | 1206783.3583 | 2647738.5367 | 1206782.548 | 2647732.0663 | 1206779.5724 | 2647726.8527 | 1206774.4389 | 2647722.4193 | 1206767.7774
67 | 2647953.4509 | 1206862.4266 | 2647745.7985 | 1206782.6061
68 | 2647953.4509 | 1206862.4266 | 2647953.4815 | 1206862.3491 | 2647957.1953 | 1206859.1548 | 2647961.5806 | 1206858.5007 | 2647972.3403 | 1206861.5407
69 | 2647950.6328 | 1206873.3437 | 2647951.1296 | 1206868.3003 | 2647953.4509 | 1206862.4266
70 | 2647971.6017 | 1206886.4158 | 2647977.0265 | 1206884.8178 | 2647988.7488 | 1206881.4767 | 2647994.3755 | 1206879.643 | 2647998.4891 | 1206877.7972 | 2648003.8431 | 1206874.883 | 2648010.2772 | 1206870.9991 | 2648015.5909 | 1206867.4286 | 2648043.3437 | 1206843.2266 | 2648057.7624 | 1206832.7365 | 2648076.9918 | 1206826.3764 | 2648097.8703 | 1206816.3831 | 2648110.5232 | 1206807.9913 | 2648131.1245 | 1206783.3429 | 2648155.0001 | 1206756.2974 | 2648167.8422 | 1206746.1617 | 2648181.2002 | 1206738.0536 | 2648219.797 | 1206718.5837
71 | 2647954.4865 | 1206892.4968 | 2647960.8352 | 1206889.7684 | 2647967.4376 | 1206887.6424 | 2647971.6017 | 1206886.4158
72 | 2648219.797 | 1206718.5837 | 2648229.8773 | 1206713.4988 | 2648241.631 | 1206709.3599
73 | 2647954.4865 | 1206892.4968 | 2647939.785 | 1206904.1634 | 2647934.0858 | 1206909.3429 | 2647928.1973 | 1206916.3219 | 2647923.7605 | 1206922.4454 | 2647918.4205 | 1206932.1415 | 2647914.0036 | 1206943.3682 | 2647911.2693 | 1206952.4404 | 2647910.0431 | 1206960.2684 | 2647909.4641 | 1206968.9244 | 2647909.6638 | 1206979.0985 | 2647912.3722 | 1207006.425 | 2647918.2864 | 1207034.1218 | 2647918.5471 | 1207036.6921 | 2647918.2834 | 1207040.1809 | 2647917.282 | 1207044.631 | 2647916.8301 | 1207045.9837 | 2647915.6017 | 1207047.4413 | 2647913.9198 | 1207048.5618 | 2647901.38 | 1207055.2763
74 | 2647954.4865 | 1206892.4968 | 2647951.0116 | 1206882.9968 | 2647950.6328 | 1206873.3437
75 | 2648251.4464 | 1206707.514 | 2648244.3213 | 1206708.4125 | 2648241.631 | 1206709.3599
76 | 2647901.38 | 1207055.2763 | 2647897.1712 | 1207049.1167 | 2647896.1911 | 1207047.1188 | 2647895.8494 | 1207044.2144 | 2647896.1484 | 1207041.0594 | 2647897.3771 | 1207034.8212 | 2647898.3023 | 1207032.2938 | 2647899.0424 | 1207031.0324
77 | 2647895.5761 | 1207058.376 | 2647901.38 | 1207055.2763
78 | 2648283.0132 | 1206692.4269 | 2648279.2802 | 1206692.3189 | 2648276.6785 | 1206693.3763 | 2648274.8197 | 1206694.7287 | 2648268.875 | 1206700.1171 | 2648264.7424 | 1206703.3523 | 2648257.8308 | 1206706.0647 | 2648251.4464 | 1206707.514
79 | 2648198.2589 | 1207243.4194 | 2648196.9476 | 1207242.2065 | 2648195.0353 | 1207238.9003 | 2648187.6361 | 1207224.7258
80 | 2648293.6886 | 1206945.5044 | 2648321.5742 | 1206937.8811
81 | 2648321.4376 | 1206915.3002 | 2648316.152 | 1206916.3136 | 2648321.5742 | 1206937.8811
82 | 2648321.4376 | 1206915.3002 | 2648332.0722 | 1206913.8854 | 2648342.0429 | 1206912.7654 | 2648346.9369 | 1206913.1497 | 2648350.9585 | 1206914.2162 | 2648353.1844 | 1206915.4238 | 2648355.6535 | 1206917.5895
83 | 2648321.4376 | 1206915.3002 | 2648314.4315 | 1206888.3612
84 | 2648428.6315 | 1207117.5167 | 2648426.8004 | 1207117.115 | 2648422.2488 | 1207115.7773 | 2648418.1501 | 1207113.9208 | 2648413.3694 | 1207110.8358 | 2648396.8282 | 1207095.4283
85 | 2648283.0132 | 1206692.4269 | 2648287.7409 | 1206692.7208 | 2648285.625 | 1206720.2086 | 2648284.9253 | 1206736.2122 | 2648285.027 | 1206750.9104 | 2648285.898 | 1206762.6243 | 2648286.9628 | 1206772.9389 | 2648288.6706 | 1206784.6261 | 2648291.72 | 1206798.7256 | 2648314.4315 | 1206888.3612
86 | 2648314.4315 | 1206888.3612 | 2648317.8415 | 1206887.9552 | 2648325.503 | 1206887.4725 | 2648329.8365 | 1206887.5854 | 2648336.317 | 1206888.3271 | 2648350.046 | 1206889.8058 | 2648360.3443 | 1206890.4895 | 2648367.9778 | 1206891.5742 | 2648370.5561 | 1206891.5172 | 2648371.8315 | 1206891.1119
87 | 2648283.0132 | 1206692.4269 | 2648283.8835 | 1206677.5491
88 | 2648284.7163 | 1206663.3127 | 2648283.8835 | 1206677.5491
89 | 2648438.6739 | 1207119.7199 | 2648428.6315 | 1207117.5167
90 | 2648509.6196 | 1207051.2767 | 2648514.1988 | 1207053.754 | 2648517.3764 | 1207056.6704 | 2648519.9572 | 1207060.0377 | 2648522.3517 | 1207063.8816 | 2648525.1177 | 1207070.755
91 | 2648284.7163 | 1206663.3127 | 2648290.1603 | 1206663.4234
92 | 2648290.1603 | 1206663.4234 | 2648294.296 | 1206665.458 | 2648296.4836 | 1206666.7098 | 2648297.8473 | 1206668.2773 | 2648298.4018 | 1206670.2384 | 2648300.0192 | 1206680.8688 | 2648302.817 | 1206687.5397 | 2648306.202 | 1206693.0592 | 2648317.9226 | 1206705.9726 | 2648332.7175 | 1206719.5557 | 2648346.8816 | 1206730.2765 | 2648354.0915 | 1206734.8708 | 2648359.4103 | 1206737.282 | 2648364.4105 | 1206738.6677 | 2648373.521 | 1206739.5642 | 2648459.035 | 1206741.2693 | 2648511.4622 | 1206751.3451 | 2648529.7192 | 1206753.6766
93 | 2648534.1452 | 1206754.1713 | 2648532.1022 | 1206753.9809 | 2648529.7192 | 1206753.6766
94 | 2648534.1452 | 1206754.1713 | 2648556.6689 | 1206756.2708 | 2648559.7949 | 1206756.1961 | 2648563.113 | 1206755.7819

## bus_geodata
| x | y | coords
0 | 2648050.7088 | 1207142.0175
1 | 2648047.978 | 1207137.6347
2 | 2648059.2911 | 1207155.7918
3 | 2648039.6082 | 1207193.9493
4 | 2648183.8379 | 1207284.7221
5 | 2648211.7801 | 1207299.0259
6 | 2648463.2732 | 1207473.5179
7 | 2648457.3435 | 1207472.4469
8 | 2648436.9744 | 1207370.189
9 | 2649291.8204 | 1207161.2156
10 | 2649022.3237 | 1207385.8064
11 | 2649256.0708 | 1207109.4141
12 | 2648667.707 | 1207367.5961
13 | 2648646.0981 | 1207394.558
14 | 2648621.6644 | 1207252.0874
15 | 2649018.8349 | 1207299.5276
16 | 2648910.2548 | 1207370.9974
17 | 2648371.8739 | 1207473.4601
18 | 2649240.9551 | 1207096.9476
19 | 2648163.7191 | 1207383.0746
20 | 2648178.9065 | 1207365.3685
21 | 2648187.2297 | 1207355.6831
22 | 2648208.6161 | 1207316.2868
23 | 2648224.6085 | 1207280.945
24 | 2648271.6964 | 1207258.7752
25 | 2648351.5875 | 1207473.027
26 | 2648341.9544 | 1207463.6736
27 | 2648358.6754 | 1207082.443
28 | 2648363.468 | 1207081.2589
29 | 2648355.2079 | 1207069.15
30 | 2648397.1232 | 1207210.7511
31 | 2648205.022 | 1207246.1503
32 | 2648383.1877 | 1207157.1348
33 | 2648480.1587 | 1207364.2136
34 | 2648483.8784 | 1207347.9239
35 | 2648483.3374 | 1207343.0584
36 | 2648495.7654 | 1207154.6039
37 | 2648684.923 | 1207108.102
38 | 2648674.4352 | 1207116.8199
39 | 2648684.6591 | 1207092.0151
40 | 2648684.6319 | 1207091.7978
41 | 2648484.0631 | 1207129.6756
42 | 2648478.3702 | 1207128.4287
43 | 2648483.4117 | 1207105.0116
44 | 2648695.5545 | 1207069.8722
45 | 2648451.3444 | 1207122.4996
46 | 2648526.5701 | 1207079.0803
47 | 2648644.7221 | 1207052.9594
48 | 2648680.8959 | 1206927.0171
49 | 2649010.3645 | 1207093.8607
50 | 2649019.3123 | 1207075.5055
51 | 2649031.1698 | 1207060.4445
52 | 2648941.0494 | 1207207.5363
53 | 2649049.76 | 1207044.9299
54 | 2649096.3676 | 1206992.9304
55 | 2649144.9732 | 1206923.9314
56 | 2648902.8532 | 1206831.7495
57 | 2649149.198 | 1206917.961
58 | 2648625.0443 | 1206740.1149
59 | 2649152.7555 | 1206916.0774
60 | 2647739.4065 | 1206748.1847
61 | 2647747.1886 | 1206775.0285
62 | 2647735.8527 | 1206710.3224
63 | 2647745.7985 | 1206782.6061
64 | 2647722.4193 | 1206767.7774
65 | 2647953.4509 | 1206862.4266
66 | 2647971.6017 | 1206886.4158
67 | 2648219.797 | 1206718.5837
68 | 2647954.4865 | 1206892.4968
69 | 2648241.631 | 1206709.3599
70 | 2647901.38 | 1207055.2763
71 | 2647950.6328 | 1206873.3437
72 | 2648251.4464 | 1206707.514
73 | 2647899.0424 | 1207031.0324
74 | 2647895.5761 | 1207058.376
75 | 2647972.3403 | 1206861.5407
76 | 2648198.2589 | 1207243.4194
77 | 2648187.6361 | 1207224.7258
78 | 2648321.5742 | 1206937.8811
79 | 2648293.6886 | 1206945.5045
80 | 2648321.4376 | 1206915.3002
81 | 2648396.8282 | 1207095.4283
82 | 2648314.4315 | 1206888.3612
83 | 2648283.0132 | 1206692.4269
84 | 2648371.8315 | 1206891.1119
85 | 2648355.6535 | 1206917.5895
86 | 2648283.8835 | 1206677.5491
87 | 2648428.6315 | 1207117.5167
88 | 2648438.6739 | 1207119.7199
89 | 2648525.1177 | 1207070.755
90 | 2648509.6196 | 1207051.2767
91 | 2648290.1603 | 1206663.4234
92 | 2648284.7163 | 1206663.3127
93 | 2648529.7192 | 1206753.6766
94 | 2648534.1452 | 1206754.1713
95 | 2648563.113 | 1206755.7819
96 | 2648355.2079 | 1207069.15

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99645 | -0.025221 | 0.0011697 | 0.00029315
1 | 0.99645 | -0.025247 | 0.00050791 | 0.00012729
2 | 0.99649 | -0.024947 | 0 | 0
3 | 0.99647 | -0.025114 | 0.00036421 | 9.128e-05
4 | 0.99701 | -0.021242 | 6.812e-05 | 1.7072e-05
5 | 0.99711 | -0.02056 | 0 | 0
6 | 0.99682 | -0.022532 | 0 | 0
7 | 0.9968 | -0.02271 | 0 | 0
8 | 0.99727 | -0.019362 | 0 | 0
9 | 0.97826 | -0.15677 | 0 | 0
10 | 0.97924 | -0.14965 | 0 | 0
11 | 0.97809 | -0.158 | 0.0012647 | 0.00031697
12 | 0.99874 | -0.0090526 | 0 | 0
13 | 0.99871 | -0.0092749 | 0.00062088 | 0.00015561
14 | 0.99886 | -0.0082132 | 0 | 0
15 | 0.97955 | -0.14741 | 0 | 0
16 | 0.97916 | -0.15022 | 0.00046997 | 0.00011779
17 | 0.99641 | -0.02543 | 0.0014633 | 0.00036673
18 | 0.97807 | -0.15811 | 0.00055356 | 0.00013873
19 | 0.99705 | -0.020953 | 0.00010781 | 2.7019e-05
20 | 0.99706 | -0.020928 | 0.00026607 | 6.6684e-05
21 | 0.99706 | -0.020879 | 7.58e-05 | 1.8997e-05
22 | 0.99709 | -0.02067 | 0.0001636 | 4.1001e-05
23 | 0.9972 | -0.019937 | 0.00043356 | 0.00010866
24 | 0.99743 | -0.018256 | 0 | 0
25 | 0.99637 | -0.025737 | 0.00045119 | 0.00011308
26 | 0.99635 | -0.025884 | 0.0010291 | 0.00025792
27 | 0.99976 | -0.0017413 | 0 | 0
28 | 0.99967 | -0.0023654 | 0 | 0
29 | 1 | 0 | -0.032275 | -0.007847
30 | 0.99813 | -0.013266 | 0 | 0
31 | 0.99739 | -0.018593 | 0.00016701 | 4.1856e-05
32 | 0.99871 | -0.0091491 | 0.001227 | 0.00030751
33 | 0.99723 | -0.019678 | 0.00012714 | 3.1864e-05
34 | 0.99721 | -0.019791 | 0.00032339 | 8.1048e-05
35 | 0.99721 | -0.019804 | 0.00026744 | 6.7026e-05
36 | 0.999 | -0.0071686 | 0.0001418 | 3.5539e-05
37 | 0.99849 | -0.010837 | 8.2667e-05 | 2.0718e-05
38 | 0.99849 | -0.010848 | 7.5917e-05 | 1.9027e-05
39 | 0.99849 | -0.010811 | 0.00018681 | 4.6819e-05
40 | 0.99849 | -0.01081 | 0.00052549 | 0.0001317
41 | 0.99902 | -0.0070427 | 0 | 0
42 | 0.99903 | -0.0069183 | 0 | 0
43 | 0.99894 | -0.0075706 | 0.00021947 | 5.5003e-05
44 | 0.99853 | -0.010573 | 0 | 0
45 | 0.99915 | -0.0061048 | 0.00012935 | 3.2417e-05
46 | 0.99881 | -0.0085571 | 0 | 0
47 | 0.9986 | -0.010058 | 0 | 0
48 | 0.99854 | -0.010469 | 0.00029267 | 7.335e-05
49 | 0.98058 | -0.13983 | 9.3427e-05 | 2.3415e-05
50 | 0.98069 | -0.13907 | 0.00013135 | 3.292e-05
51 | 0.98079 | -0.13834 | 4.1991e-05 | 1.0524e-05
52 | 0.97936 | -0.14878 | 0.0010785 | 0.0002703
53 | 0.98092 | -0.13739 | 0.00034907 | 8.7484e-05
54 | 0.98138 | -0.13403 | 0 | 0
55 | 0.98129 | -0.13467 | 0.00034657 | 8.6857e-05
56 | 0.98372 | -0.11689 | 0 | 0
57 | 0.98129 | -0.13469 | 0.00012519 | 3.1377e-05
58 | 0.98591 | -0.10081 | 0.00050118 | 0.00012561
59 | 0.98128 | -0.13469 | 0.00011788 | 2.9543e-05
60 | 0.98571 | -0.10184 | 0.0008811 | 0.00022082
61 | 0.98578 | -0.10139 | 0.00033629 | 8.4281e-05
62 | 0.98568 | -0.1021 | 0.00067495 | 0.00016916
63 | 0.9858 | -0.10123 | 0 | 0
64 | 0.98576 | -0.10151 | 0.00090754 | 0.00022745
65 | 0.9867 | -0.094793 | 0.00050011 | 0.00012534
66 | 0.98704 | -0.092374 | 0.00046035 | 0.00011537
67 | 0.98951 | -0.074665 | 0.00063209 | 0.00015842
68 | 0.9869 | -0.093345 | 0 | 0
69 | 0.98972 | -0.073132 | 0.00061934 | 0.00015522
70 | 0.98672 | -0.094625 | 0 | 0
71 | 0.98677 | -0.094264 | 0 | 0
72 | 0.98982 | -0.072421 | 0.00047097 | 0.00011804
73 | 0.98672 | -0.094678 | 0.00019477 | 4.8814e-05
74 | 0.98672 | -0.094656 | 0.00045599 | 0.00011428
75 | 0.98666 | -0.095046 | 0.001199 | 0.00030049
76 | 0.99738 | -0.018617 | 0.00019774 | 4.9558e-05
77 | 0.99738 | -0.018644 | 0.00012448 | 3.1196e-05
78 | 0.99634 | -0.025901 | 0 | 0
79 | 0.99625 | -0.026478 | 0.0019895 | 0.00049861
80 | 0.99567 | -0.030647 | 0 | 0
81 | 0.99945 | -0.0039532 | 0.00046486 | 0.00011651
82 | 0.99501 | -0.03536 | 0 | 0
83 | 0.9902 | -0.069693 | 0 | 0
84 | 0.99499 | -0.035456 | 0.00016255 | 4.074e-05
85 | 0.99566 | -0.030743 | 0.00026789 | 6.714e-05
86 | 0.99001 | -0.071087 | 0.0012043 | 0.00030182
87 | 0.99925 | -0.0053574 | 0.0001668 | 4.1805e-05
88 | 0.9992 | -0.0057064 | 0.0003229 | 8.0926e-05
89 | 0.9988 | -0.008618 | 9.505e-05 | 2.3822e-05
90 | 0.99878 | -0.0087764 | 0.00061476 | 0.00015407
91 | 0.98979 | -0.072688 | 0 | 0
92 | 0.98985 | -0.072247 | 0 | 0
93 | 0.98667 | -0.095253 | 0.00029498 | 7.3929e-05
94 | 0.98662 | -0.095603 | 0.0017917 | 0.00044904
95 | 0.98638 | -0.097353 | 0.00060464 | 0.00015154
96 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00050791 | 0.00012723 | -0.00050791 | -0.00012729 | 1.8536e-09 | -6.6554e-08 | 0.00075844 | 0.00075847 | 0.00075847 | 0.99645 | -0.025221 | 0.99645 | -0.025247 | 0.28091
1 | -0.0016776 | -0.00042038 | 0.0016777 | 0.00042019 | 6.3554e-08 | -1.8697e-07 | 0.0025052 | 0.0025051 | 0.0025052 | 0.99645 | -0.025221 | 0.99649 | -0.024947 | 0.92784
2 | 0.00036422 | 9.0692e-05 | -0.00036421 | -9.128e-05 | 8.3632e-09 | -5.8727e-07 | 0.00054366 | 0.00054387 | 0.00054387 | 0.99649 | -0.024947 | 0.99647 | -0.025114 | 0.20143
3 | -0.0020419 | -0.00051088 | 0.0020429 | 0.00050895 | 1.0397e-06 | -1.9372e-06 | 0.0030488 | 0.0030479 | 0.0030488 | 0.99649 | -0.024947 | 0.99701 | -0.021242 | 1.1292
4 | -0.002111 | -0.00052602 | 0.0021112 | 0.00052568 | 1.9676e-07 | -3.389e-07 | 0.0031496 | 0.0031495 | 0.0031496 | 0.99701 | -0.021242 | 0.99711 | -0.02056 | 1.1665
5 | -0.0027245 | -0.0006781 | 0.0027248 | 0.00067789 | 2.3186e-07 | -2.0426e-07 | 0.0040643 | 0.0040641 | 0.0040643 | 0.99711 | -0.02056 | 0.9972 | -0.019937 | 1.5053
6 | 0.0006133 | 0.00015241 | -0.00061329 | -0.00015264 | 9.1646e-09 | -2.2537e-07 | 0.0009148 | 0.00091488 | 0.00091488 | 0.99711 | -0.02056 | 0.99709 | -0.02067 | 0.33884
7 | 0.0029448 | 0.00073648 | -0.0029447 | -0.00073653 | 7.2439e-08 | -5.0471e-08 | 0.0043953 | 0.0043954 | 0.0043954 | 0.99682 | -0.022532 | 0.9968 | -0.02271 | 1.6279
8 | -0.0029448 | -0.00073648 | 0.0029461 | 0.00073558 | 1.2853e-06 | -8.963e-07 | 0.0043953 | 0.0043949 | 0.0043953 | 0.99682 | -0.022532 | 0.99727 | -0.019362 | 1.6279
9 | 0.0029447 | 0.00073653 | -0.0029436 | -0.0007373 | 1.1055e-06 | -7.6959e-07 | 0.0043954 | 0.0043958 | 0.0043958 | 0.9968 | -0.02271 | 0.99641 | -0.02543 | 1.6281
10 | -0.0036641 | -0.00091466 | 0.0036672 | 0.00091369 | 3.0634e-06 | -9.6798e-07 | 0.0054659 | 0.0054651 | 0.0054659 | 0.99727 | -0.019362 | 0.99813 | -0.013266 | 2.0244
11 | 0.000718 | 0.00017907 | -0.00071797 | -0.00017963 | 3.121e-08 | -5.568e-07 | 0.001071 | 0.0010712 | 0.0010712 | 0.99727 | -0.019362 | 0.99723 | -0.019678 | 0.39675
12 | -0.0018186 | -0.00045477 | 0.0018204 | 0.0004508 | 1.7665e-06 | -3.974e-06 | 0.0027659 | 0.0027642 | 0.0027659 | 0.97826 | -0.15677 | 0.97924 | -0.14965 | 1.0244
13 | 0.0018186 | 0.00045477 | -0.0018183 | -0.00045546 | 3.0899e-07 | -6.936e-07 | 0.0027659 | 0.0027662 | 0.0027662 | 0.97826 | -0.15677 | 0.97809 | -0.158 | 1.0245
14 | -0.0022904 | -0.00056716 | 0.0022911 | 0.00056626 | 6.945e-07 | -8.9093e-07 | 0.0034779 | 0.0034775 | 0.0034779 | 0.97924 | -0.14965 | 0.97955 | -0.14741 | 1.2881
15 | 0.00047001 | 0.00011636 | -0.00046997 | -0.00011779 | 3.6441e-08 | -1.4272e-06 | 0.00071369 | 0.00071421 | 0.00071421 | 0.97924 | -0.14965 | 0.97916 | -0.15022 | 0.26452
16 | 0.00055356 | 0.00013849 | -0.00055356 | -0.00013873 | 8.6704e-09 | -2.4257e-07 | 0.00084208 | 0.00084217 | 0.00084217 | 0.97809 | -0.158 | 0.97807 | -0.15811 | 0.31191
17 | 0.0006209 | 0.00015515 | -0.00062088 | -0.00015561 | 1.9053e-08 | -4.5965e-07 | 0.00092491 | 0.00092508 | 0.00092508 | 0.99874 | -0.0090526 | 0.99871 | -0.0092749 | 0.34262
18 | -0.0006209 | -0.00015515 | 0.00062097 | 0.00015343 | 7.0946e-08 | -1.7133e-06 | 0.00092491 | 0.00092431 | 0.00092491 | 0.99874 | -0.0090526 | 0.99886 | -0.0082132 | 0.34256
19 | -0.00062097 | -0.00015343 | 0.00062106 | 0.00015135 | 8.6222e-08 | -2.0858e-06 | 0.00092431 | 0.00092358 | 0.00092431 | 0.99886 | -0.0082132 | 0.999 | -0.0071686 | 0.34234
20 | 0.0010787 | 0.00026884 | -0.0010785 | -0.0002703 | 2.0441e-07 | -1.4573e-06 | 0.0016381 | 0.0016386 | 0.0016386 | 0.97955 | -0.14741 | 0.97936 | -0.14878 | 0.6069
21 | -0.0033698 | -0.0008351 | 0.0033732 | 0.00083377 | 3.4509e-06 | -1.3362e-06 | 0.0051156 | 0.0051147 | 0.0051156 | 0.97955 | -0.14741 | 0.98058 | -0.13983 | 1.8947
22 | 0.0014804 | 0.00037057 | -0.0014803 | -0.00037082 | 6.2808e-08 | -2.4411e-07 | 0.0022106 | 0.0022107 | 0.0022107 | 0.99641 | -0.02543 | 0.99637 | -0.025737 | 0.81877
23 | -0.00010781 | -2.7019e-05 | 0.00010781 | 2.6715e-05 | 3.7659e-10 | -3.0412e-07 | 0.00016089 | 0.00016079 | 0.00016089 | 0.99705 | -0.020953 | 0.99706 | -0.020928 | 0.05959
24 | -0.00037388 | -9.3399e-05 | 0.00037388 | 9.3234e-05 | 2.4798e-09 | -1.656e-07 | 0.00055788 | 0.00055782 | 0.00055788 | 0.99706 | -0.020928 | 0.99706 | -0.020879 | 0.20662
25 | -0.00044968 | -0.00011223 | 0.0004497 | 0.00011164 | 1.2851e-08 | -5.9192e-07 | 0.00067094 | 0.00067073 | 0.00067094 | 0.99706 | -0.020879 | 0.99709 | -0.02067 | 0.2485
26 | -0.0031583 | -0.00078655 | 0.0031591 | 0.00078615 | 7.2563e-07 | -4.0464e-07 | 0.0047111 | 0.0047109 | 0.0047111 | 0.9972 | -0.019937 | 0.99743 | -0.018256 | 1.7449
27 | -0.0036483 | -0.0009075 | 0.0036508 | 0.0009067 | 2.4802e-06 | -8.003e-07 | 0.0054403 | 0.0054397 | 0.0054403 | 0.99743 | -0.018256 | 0.99813 | -0.013266 | 2.0149
28 | 0.00048924 | 0.00012135 | -0.00048922 | -0.00012223 | 2.254e-08 | -8.7699e-07 | 0.00072943 | 0.00072974 | 0.00072974 | 0.99743 | -0.018256 | 0.99739 | -0.018593 | 0.27028
29 | 0.0010291 | 0.00025774 | -0.0010291 | -0.00025792 | 2.1006e-08 | -1.7754e-07 | 0.0015369 | 0.0015369 | 0.0015369 | 0.99637 | -0.025737 | 0.99635 | -0.025884 | 0.56923
30 | 0.012501 | 0.0031067 | -0.0125 | -0.0031064 | 1.0624e-06 | 3.4406e-07 | 0.018596 | 0.018597 | 0.018597 | 0.99976 | -0.0017413 | 0.99967 | -0.0023654 | 6.8876
31 | -0.012501 | -0.0031067 | 0.012504 | 0.0031077 | 2.9646e-06 | 9.6004e-07 | 0.018596 | 0.018596 | 0.018596 | 0.99976 | -0.0017413 | 1 | 0 | 6.8876
32 | 0.0039426 | 0.0009756 | -0.0039417 | -0.0009758 | 8.4557e-07 | -1.9127e-07 | 0.0058642 | 0.0058644 | 0.0058644 | 0.99967 | -0.0023654 | 0.99945 | -0.0039532 | 2.172
33 | 0.008557 | 0.0021308 | -0.0085491 | -0.0021288 | 7.9307e-06 | 2.0234e-06 | 0.012732 | 0.012733 | 0.012733 | 0.99967 | -0.0023654 | 0.99871 | -0.0091491 | 4.7158
34 | 0.018972 | 0.0047393 | -0.018904 | -0.0047151 | 6.7364e-05 | 2.4138e-05 | 0.028225 | 0.028226 | 0.028226 | 1 | 0 | 0.99634 | -0.025901 | 10.4539
35 | -0.0073179 | -0.0018204 | 0.0073221 | 0.0018212 | 4.1106e-06 | 8.565e-07 | 0.010905 | 0.010905 | 0.010905 | 0.99813 | -0.013266 | 0.99871 | -0.0091491 | 4.0388
36 | 0.00032222 | 8.0376e-05 | -0.00032221 | -8.0473e-05 | 1.0743e-09 | -9.686e-08 | 0.00048059 | 0.00048062 | 0.00048062 | 0.99739 | -0.018593 | 0.99738 | -0.018617 | 0.17801
37 | 0.00059083 | 0.00014777 | -0.00059082 | -0.00014801 | 9.2098e-09 | -2.4424e-07 | 0.0008815 | 0.00088159 | 0.00088159 | 0.99723 | -0.019678 | 0.99721 | -0.019791 | 0.32651
38 | 0.00026744 | 6.6962e-05 | -0.00026744 | -6.7026e-05 | 4.8643e-10 | -6.368e-08 | 0.00039904 | 0.00039906 | 0.00039906 | 0.99721 | -0.019791 | 0.99721 | -0.019804 | 0.1478
39 | -0.00076286 | -0.00018689 | 0.00076289 | 0.00018649 | 2.5251e-08 | -4.0179e-07 | 0.0011348 | 0.0011347 | 0.0011348 | 0.999 | -0.0071686 | 0.99903 | -0.0069183 | 0.42029
40 | 7.5917e-05 | 1.8844e-05 | -7.5917e-05 | -1.9027e-05 | 1.1129e-10 | -1.823e-07 | 0.00011307 | 0.00011314 | 0.00011314 | 0.99849 | -0.010837 | 0.99849 | -0.010848 | 0.041902
41 | -0.00015858 | -3.9563e-05 | 0.00015858 | 3.9349e-05 | 5.6842e-10 | -2.1329e-07 | 0.00023627 | 0.00023619 | 0.00023627 | 0.99849 | -0.010837 | 0.99849 | -0.010811 | 0.087507
42 | -0.00034539 | -8.6168e-05 | 0.00034539 | 8.6165e-05 | 3.5653e-11 | -2.8512e-09 | 0.00051459 | 0.00051459 | 0.00051459 | 0.99849 | -0.010811 | 0.99849 | -0.01081 | 0.19059
43 | -0.00087089 | -0.00021787 | 0.00087092 | 0.00021752 | 2.85e-08 | -3.4382e-07 | 0.0012977 | 0.0012976 | 0.0012977 | 0.99849 | -0.01081 | 0.99853 | -0.010573 | 0.48063
44 | -0.0020936 | -0.00051841 | 0.0020936 | 0.00051834 | 3.5217e-08 | -6.2556e-08 | 0.0031162 | 0.0031161 | 0.0031162 | 0.99902 | -0.0070427 | 0.99903 | -0.0069183 | 1.1541
45 | 0.0020936 | 0.00051841 | -0.0020934 | -0.00051867 | 1.4951e-07 | -2.6553e-07 | 0.0031162 | 0.0031163 | 0.0031163 | 0.99902 | -0.0070427 | 0.99894 | -0.0075706 | 1.1542
46 | -0.0028565 | -0.00070483 | 0.0028568 | 0.00070459 | 3.1196e-07 | -2.4235e-07 | 0.0042508 | 0.0042507 | 0.0042508 | 0.99903 | -0.0069183 | 0.99915 | -0.0061048 | 1.5744
47 | 0.001874 | 0.00046367 | -0.0018737 | -0.00046425 | 2.4992e-07 | -5.7763e-07 | 0.0027894 | 0.0027896 | 0.0027896 | 0.99894 | -0.0075706 | 0.99881 | -0.0085571 | 1.0332
48 | -0.00087092 | -0.00021752 | 0.00087098 | 0.00021678 | 6.1421e-08 | -7.4128e-07 | 0.0012976 | 0.0012973 | 0.0012976 | 0.99853 | -0.010573 | 0.9986 | -0.010058 | 0.48059
49 | -0.0029862 | -0.000737 | 0.0029863 | 0.0007369 | 1.598e-07 | -1.0844e-07 | 0.0044433 | 0.0044432 | 0.0044433 | 0.99915 | -0.0061048 | 0.9992 | -0.0057064 | 1.6457
50 | 0.00070983 | 0.00017745 | -0.00070982 | -0.00017756 | 5.9548e-09 | -1.0942e-07 | 0.0010573 | 0.0010574 | 0.0010574 | 0.99881 | -0.0085571 | 0.9988 | -0.008618 | 0.39162
51 | 0.0011639 | 0.00028679 | -0.0011637 | -0.00028834 | 2.3523e-07 | -1.5529e-06 | 0.0017323 | 0.0017328 | 0.0017328 | 0.99881 | -0.0085571 | 0.9986 | -0.010058 | 0.64179
52 | 0.00029269 | 7.1563e-05 | -0.00029267 | -7.335e-05 | 1.6252e-08 | -1.7875e-06 | 0.00043551 | 0.00043613 | 0.00043613 | 0.9986 | -0.010058 | 0.99854 | -0.010469 | 0.16153
53 | -0.0034667 | -0.00085718 | 0.003467 | 0.00085706 | 3.5385e-07 | -1.2284e-07 | 0.0052564 | 0.0052563 | 0.0052564 | 0.98058 | -0.13983 | 0.98069 | -0.13907 | 1.9468
54 | -0.0035984 | -0.00088998 | 0.0035987 | 0.00088987 | 3.5609e-07 | -1.0498e-07 | 0.0054556 | 0.0054556 | 0.0054556 | 0.98069 | -0.13907 | 0.98079 | -0.13834 | 2.0206
55 | -0.0036407 | -0.0009004 | 0.0036412 | 0.00090027 | 4.6796e-07 | -1.3075e-07 | 0.0055193 | 0.0055192 | 0.0055193 | 0.98079 | -0.13834 | 0.98092 | -0.13739 | 2.0442
56 | -0.0039902 | -0.00098775 | 0.003992 | 0.00098745 | 1.8069e-06 | -3.0465e-07 | 0.0060487 | 0.0060483 | 0.0060487 | 0.98092 | -0.13739 | 0.98138 | -0.13403 | 2.2402
57 | 0.00058969 | 0.00014635 | -0.00058964 | -0.00014763 | 5.1487e-08 | -1.285e-06 | 0.00089361 | 0.00089407 | 0.00089407 | 0.98138 | -0.13403 | 0.98129 | -0.13467 | 0.33114
58 | -0.0045817 | -0.0011338 | 0.0045923 | 0.0011334 | 1.0591e-05 | -3.8832e-07 | 0.0069419 | 0.0069404 | 0.0069419 | 0.98138 | -0.13403 | 0.98372 | -0.11689 | 2.5711
59 | 0.00024307 | 6.0775e-05 | -0.00024307 | -6.0868e-05 | 6.2505e-10 | -9.2919e-08 | 0.00036854 | 0.00036857 | 0.00036857 | 0.98129 | -0.13467 | 0.98129 | -0.13469 | 0.13651
60 | -0.0045923 | -0.0011334 | 0.0046022 | 0.001133 | 9.9104e-06 | -3.8448e-07 | 0.0069404 | 0.0069389 | 0.0069404 | 0.98372 | -0.11689 | 0.98591 | -0.10081 | 2.5705
61 | 0.00011788 | 2.9491e-05 | -0.00011788 | -2.9543e-05 | 8.1854e-11 | -5.1835e-08 | 0.00017873 | 0.00017875 | 0.00017875 | 0.98129 | -0.13469 | 0.98128 | -0.13469 | 0.066204
62 | -0.0051034 | -0.0012586 | 0.0051058 | 0.0012587 | 2.367e-06 | 9.3108e-08 | 0.0076953 | 0.007695 | 0.0076953 | 0.98591 | -0.10081 | 0.98638 | -0.097353 | 2.8501
63 | -0.0015561 | -0.00038951 | 0.0015562 | 0.00038918 | 9.6542e-08 | -3.2037e-07 | 0.0023488 | 0.0023487 | 0.0023488 | 0.98571 | -0.10184 | 0.98578 | -0.10139 | 0.86994
64 | 0.00067497 | 0.00016868 | -0.00067495 | -0.00016916 | 2.4697e-08 | -4.765e-07 | 0.0010188 | 0.0010189 | 0.0010189 | 0.98571 | -0.10184 | 0.98568 | -0.1021 | 0.37738
65 | -0.0018925 | -0.00047347 | 0.0018925 | 0.00047338 | 4.0605e-08 | -8.6067e-08 | 0.0028563 | 0.0028563 | 0.0028563 | 0.98578 | -0.10139 | 0.9858 | -0.10123 | 1.0579
66 | 0.00090757 | 0.00022708 | -0.00090754 | -0.00022745 | 3.4912e-08 | -3.6668e-07 | 0.0013698 | 0.0013699 | 0.0013699 | 0.9858 | -0.10123 | 0.98576 | -0.10151 | 0.50738
67 | -0.0028001 | -0.00070046 | 0.0028025 | 0.00069858 | 2.4787e-06 | -1.8855e-06 | 0.0042261 | 0.0042251 | 0.0042261 | 0.9858 | -0.10123 | 0.9867 | -0.094793 | 1.5652
68 | 0.001199 | 0.00030024 | -0.001199 | -0.00030049 | 4.2019e-08 | -2.469e-07 | 0.0018081 | 0.0018082 | 0.0018082 | 0.9867 | -0.094793 | 0.98666 | -0.095046 | 0.6697
69 | -0.0045017 | -0.0011242 | 0.004502 | 0.0011241 | 3.2724e-07 | -1.9547e-08 | 0.0067874 | 0.0067873 | 0.0067874 | 0.9867 | -0.094793 | 0.98677 | -0.094264 | 2.5139
70 | -0.0056145 | -0.0013998 | 0.0056281 | 0.0014012 | 1.3622e-05 | 1.3318e-06 | 0.0084615 | 0.0084602 | 0.0084615 | 0.98704 | -0.092374 | 0.98951 | -0.074665 | 3.1339
71 | 0.0051541 | 0.0012844 | -0.0051534 | -0.0012844 | 6.8474e-07 | 3.0935e-08 | 0.0077675 | 0.0077676 | 0.0077676 | 0.98704 | -0.092374 | 0.9869 | -0.093345 | 2.8769
72 | -0.0062602 | -0.0015596 | 0.0062615 | 0.0015598 | 1.3125e-06 | 1.9966e-07 | 0.0094107 | 0.0094106 | 0.0094107 | 0.98951 | -0.074665 | 0.98972 | -0.073132 | 3.4854
73 | 0.00065087 | 0.00016031 | -0.00065076 | -0.00016268 | 1.1313e-07 | -2.3642e-06 | 0.00098037 | 0.00098122 | 0.00098122 | 0.9869 | -0.093345 | 0.98672 | -0.094625 | 0.36342
74 | 0.0045025 | 0.0011241 | -0.004502 | -0.0011241 | 5.6848e-07 | -3.4014e-08 | 0.0067873 | 0.0067873 | 0.0067873 | 0.9869 | -0.093345 | 0.98677 | -0.094264 | 2.5138
75 | -0.0068808 | -0.001715 | 0.0068815 | 0.0017151 | 6.6963e-07 | 1.2859e-07 | 0.010342 | 0.010342 | 0.010342 | 0.98972 | -0.073132 | 0.98982 | -0.072421 | 3.8303
76 | 0.00019477 | 4.8479e-05 | -0.00019477 | -4.8814e-05 | 1.4145e-09 | -3.352e-07 | 0.00029361 | 0.00029372 | 0.00029372 | 0.98672 | -0.094625 | 0.98672 | -0.094678 | 0.10879
77 | 0.00045599 | 0.0001142 | -0.00045599 | -0.00011428 | 1.937e-09 | -8.3111e-08 | 0.00068762 | 0.00068765 | 0.00068765 | 0.98672 | -0.094625 | 0.98672 | -0.094656 | 0.25468
78 | -0.0073525 | -0.0018332 | 0.0073552 | 0.0018337 | 2.7492e-06 | 5.9339e-07 | 0.01105 | 0.01105 | 0.01105 | 0.98982 | -0.072421 | 0.9902 | -0.069693 | 4.0925
79 | 0.00012448 | 3.0915e-05 | -0.00012448 | -3.1196e-05 | 4.6448e-10 | -2.8165e-07 | 0.00018561 | 0.00018571 | 0.00018571 | 0.99738 | -0.018617 | 0.99738 | -0.018644 | 0.068781
80 | 0.0019896 | 0.00049829 | -0.0019895 | -0.00049861 | 1.5885e-07 | -3.1435e-07 | 0.0029714 | 0.0029715 | 0.0029715 | 0.99634 | -0.025901 | 0.99625 | -0.026478 | 1.1006
81 | 0.016915 | 0.0042168 | -0.016904 | -0.004213 | 1.0992e-05 | 3.8683e-06 | 0.025254 | 0.025254 | 0.025254 | 0.99634 | -0.025901 | 0.99567 | -0.030647 | 9.3534
82 | 0.0002679 | 6.6679e-05 | -0.00026789 | -6.714e-05 | 3.5547e-09 | -4.6102e-07 | 0.00040021 | 0.00040037 | 0.00040037 | 0.99567 | -0.030647 | 0.99566 | -0.030743 | 0.14829
83 | 0.016636 | 0.0041463 | -0.016625 | -0.0041425 | 1.0729e-05 | 3.7649e-06 | 0.024854 | 0.024854 | 0.024854 | 0.99567 | -0.030647 | 0.99501 | -0.03536 | 9.2053
84 | 0.0034769 | 0.00085929 | -0.0034762 | -0.00085955 | 6.5797e-07 | -2.6334e-07 | 0.0051723 | 0.0051724 | 0.0051724 | 0.99945 | -0.0039532 | 0.99925 | -0.0053574 | 1.9157
85 | 0.016463 | 0.0041025 | -0.016386 | -0.0040755 | 7.705e-05 | 2.7e-05 | 0.024611 | 0.024612 | 0.024612 | 0.99501 | -0.03536 | 0.9902 | -0.069693 | 9.1157
86 | 0.00016256 | 3.9991e-05 | -0.00016255 | -4.074e-05 | 2.1264e-09 | -7.4894e-07 | 0.00024284 | 0.0002431 | 0.0002431 | 0.99501 | -0.03536 | 0.99499 | -0.035456 | 0.090037
87 | 0.0090304 | 0.0022418 | -0.0090287 | -0.0022413 | 1.7107e-06 | 4.6628e-07 | 0.013563 | 0.013563 | 0.013563 | 0.9902 | -0.069693 | 0.99001 | -0.071087 | 5.0233
88 | 0.0078244 | 0.0019395 | -0.0078232 | -0.0019392 | 1.2292e-06 | 2.8941e-07 | 0.011753 | 0.011753 | 0.011753 | 0.99001 | -0.071087 | 0.98985 | -0.072247 | 4.3529
89 | 0.0033094 | 0.00081775 | -0.0033092 | -0.00081782 | 1.5555e-07 | -7.4846e-08 | 0.004924 | 0.0049241 | 0.0049241 | 0.99925 | -0.0053574 | 0.9992 | -0.0057064 | 1.8237
90 | 0.00061477 | 0.00015374 | -0.00061476 | -0.00015407 | 1.3451e-08 | -3.3117e-07 | 0.00091578 | 0.00091589 | 0.00091589 | 0.9988 | -0.008618 | 0.99878 | -0.0087764 | 0.33922
91 | -0.0078227 | -0.0019391 | 0.0078232 | 0.0019392 | 4.6794e-07 | 1.1019e-07 | 0.011753 | 0.011753 | 0.011753 | 0.98979 | -0.072688 | 0.98985 | -0.072247 | 4.3529
92 | 0.0078227 | 0.0019391 | -0.0077988 | -0.0019335 | 2.3882e-05 | 5.6358e-06 | 0.011753 | 0.011754 | 0.011754 | 0.98979 | -0.072688 | 0.98667 | -0.095253 | 4.3534
93 | 0.0075038 | 0.0018595 | -0.0075035 | -0.0018594 | 3.5548e-07 | 7.9839e-08 | 0.011309 | 0.011309 | 0.011309 | 0.98667 | -0.095253 | 0.98662 | -0.095603 | 4.1886
94 | 0.0057118 | 0.0014104 | -0.0057104 | -0.0014103 | 1.3448e-06 | 1.4582e-07 | 0.008607 | 0.0086072 | 0.0086072 | 0.98662 | -0.095603 | 0.98638 | -0.097353 | 3.1878

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.03307 | 0.0080462

## res_load
| p_mw | q_mvar
0 | 0.0011697 | 0.00029315
1 | 0.00050791 | 0.00012729
2 | 0.00036421 | 9.128e-05
3 | 6.812e-05 | 1.7072e-05
4 | 0.0012647 | 0.00031697
5 | 0.00062088 | 0.00015561
6 | 0.00046997 | 0.00011779
7 | 0.0014633 | 0.00036673
8 | 0.00055356 | 0.00013873
9 | 0.00010781 | 2.7019e-05
10 | 0.00026607 | 6.6684e-05
11 | 7.58e-05 | 1.8997e-05
12 | 0.0001636 | 4.1001e-05
13 | 0.00043356 | 0.00010866
14 | 0.00045119 | 0.00011308
15 | 0.0010291 | 0.00025792
16 | 0.00079487 | 0.00019921
17 | 0.00016701 | 4.1856e-05
18 | 0.001227 | 0.00030751
19 | 0.00012714 | 3.1864e-05
20 | 0.00032339 | 8.1048e-05
21 | 0.00026744 | 6.7026e-05
22 | 0.0001418 | 3.5539e-05
23 | 8.2667e-05 | 2.0718e-05
24 | 7.5917e-05 | 1.9027e-05
25 | 0.00018681 | 4.6819e-05
26 | 0.00052549 | 0.0001317
27 | 0.00021947 | 5.5003e-05
28 | 0.00012935 | 3.2417e-05
29 | 0.00029267 | 7.335e-05
30 | 9.3427e-05 | 2.3415e-05
31 | 0.00013135 | 3.292e-05
32 | 4.1991e-05 | 1.0524e-05
33 | 0.0010785 | 0.0002703
34 | 0.00034907 | 8.7484e-05
35 | 0.00034657 | 8.6857e-05
36 | 0.00012519 | 3.1377e-05
37 | 0.00050118 | 0.00012561
38 | 0.00011788 | 2.9543e-05
39 | 0.0008811 | 0.00022082
40 | 0.00033629 | 8.4281e-05
41 | 0.00067495 | 0.00016916
42 | 0.00090754 | 0.00022745
43 | 0.00050011 | 0.00012534
44 | 0.00046035 | 0.00011537
45 | 0.00063209 | 0.00015842
46 | 0.00061934 | 0.00015522
47 | 0.00047097 | 0.00011804
48 | 0.00019477 | 4.8814e-05
49 | 0.00045599 | 0.00011428
50 | 0.001199 | 0.00030049
51 | 0.00019774 | 4.9558e-05
52 | 0.00012448 | 3.1196e-05
53 | 0.0019895 | 0.00049861
54 | 0.00046486 | 0.00011651
55 | 0.00016255 | 4.074e-05
56 | 0.00026789 | 6.714e-05
57 | 0.0012043 | 0.00030182
58 | 0.0001668 | 4.1805e-05
59 | 0.0003229 | 8.0926e-05
60 | 9.505e-05 | 2.3822e-05
61 | 0.00061476 | 0.00015407
62 | 0.00029498 | 7.3929e-05
63 | 0.0017917 | 0.00044904
64 | 0.00060464 | 0.00015154

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1