## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1002-5_1_3_node_5 | 0.4 | n |  | TRUE
1 | bus_LV_1002-5_1_3_node_6 | 0.4 | n |  | TRUE
2 | bus_LV_1002-5_1_3_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_1002-5_1_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1002-5_1_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1002-5_1_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1002-5_1_3_node_72 | 0.4 | n |  | TRUE
7 | bus_LV_1002-5_1_3_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_1002-5_1_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1002-5_1_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1002-5_1_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1002-5_1_3_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1002-5_1_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1002-5_1_3_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1002-5_1_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1002-5_1_3_node_107 | 0.4 | n |  | TRUE
16 | bus_LV_1002-5_1_3_node_102 | 0.4 | n |  | TRUE
17 | bus_LV_1002-5_1_3_node_101 | 0.4 | n |  | TRUE
18 | bus_LV_1002-5_1_3_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1002-5_1_3_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_1002-5_1_3_node_113 | 0.4 | n |  | TRUE
21 | bus_LV_1002-5_1_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1002-5_1_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1002-5_1_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1002-5_1_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1002-5_1_3_node_245 | 0.4 | n |  | TRUE
26 | bus_LV_1002-5_1_3_node_106 | 0.4 | n |  | TRUE
27 | bus_LV_1002-5_1_3_node_93 | 0.4 | n |  | TRUE
28 | bus_LV_1002-5_1_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1002-5_1_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1002-5_1_3_node_90 | 0.4 | n |  | TRUE
31 | bus_LV_1002-5_1_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1002-5_1_3_node_344 | 0.4 | n |  | TRUE
33 | bus_LV_1002-5_1_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1002-5_1_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1002-5_1_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1002-5_1_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1002-5_1_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1002-5_1_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1002-5_1_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1002-5_1_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_1002-5_1_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1002-5_1_3_node_104 | 0.4 | n |  | TRUE
43 | bus_LV_1002-5_1_3_node_67 | 0.4 | n |  | TRUE
44 | bus_LV_1002-5_1_3_node_65 | 0.4 | n |  | TRUE
45 | bus_LV_1002-5_1_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_1002-5_1_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1002-5_1_3_node_98 | 0.4 | n |  | TRUE
48 | bus_LV_1002-5_1_3_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1002-5_1_3_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_1002-5_1_3_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_1002-5_1_3_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1002-5_1_3_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_1002-5_1_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_1002-5_1_3_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_1002-5_1_3_node_87 | 0.4 | n |  | TRUE
56 | bus_LV_1002-5_1_3_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_1002-5_1_3_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_1002-5_1_3_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_1002-5_1_3_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_1002-5_1_3_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_1002-5_1_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1002-5_1_3_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_1002-5_1_3_node_64 | 0.4 | n |  | TRUE
64 | bus_LV_1002-5_1_3_node_96 | 0.4 | n |  | TRUE
65 | bus_LV_1002-5_1_3_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1002-5_1_3_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_1002-5_1_3_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_1002-5_1_3_node_295 | 0.4 | n |  | TRUE
69 | bus_LV_1002-5_1_3_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_1002-5_1_3_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_1002-5_1_3_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_1002-5_1_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_1002-5_1_3_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1002-5_1_3_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_1002-5_1_3_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_1002-5_1_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_1002-5_1_3_node_99 | 0.4 | n |  | TRUE
78 | bus_LV_1002-5_1_3_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_1002-5_1_3_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_1002-5_1_3_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_1002-5_1_3_node_76 | 0.4 | n |  | TRUE
82 | bus_LV_1002-5_1_3_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_1002-5_1_3_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_1002-5_1_3_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_1002-5_1_3_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_1002-5_1_3_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_1002-5_1_3_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_1002-5_1_3_node_103 | 0.4 | n |  | TRUE
89 | bus_LV_1002-5_1_3_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_1002-5_1_3_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_1002-5_1_3_node_97 | 0.4 | n |  | TRUE
92 | bus_LV_1002-5_1_3_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_1002-5_1_3_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_1002-5_1_3_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_1002-5_1_3_node_91 | 0.4 | n |  | TRUE
96 | bus_LV_1002-5_1_3_node_110 | 0.4 | n |  | TRUE
97 | bus_LV_1002-5_1_3_node_218 | 0.4 | n |  | TRUE
98 | bus_LV_1002-5_1_3_node_111 | 0.4 | n |  | TRUE
99 | bus_LV_1002-5_1_3_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1002-5_1_3_node_114 | 0.4 | n |  | TRUE
101 | bus_LV_1002-5_1_3_node_115 | 0.4 | n |  | TRUE
102 | bus_LV_1002-5_1_3_node_116 | 0.4 | n |  | TRUE
103 | bus_LV_1002-5_1_3_node_118 | 0.4 | n |  | TRUE
104 | bus_LV_1002-5_1_3_node_119 | 0.4 | n |  | TRUE
105 | bus_LV_1002-5_1_3_node_120 | 0.4 | n |  | TRUE
106 | bus_LV_1002-5_1_3_node_288 | 0.4 | n |  | TRUE
107 | bus_LV_1002-5_1_3_node_217 | 0.4 | n |  | TRUE
108 | bus_LV_1002-5_1_3_node_246 | 0.4 | n |  | TRUE
109 | bus_LV_1002-5_1_3_node_286 | 0.4 | n |  | TRUE
110 | bus_LV_1002-5_1_3_node_287 | 0.4 | n |  | TRUE
111 | bus_LV_1002-5_1_3_node_289 | 0.4 | n |  | TRUE
112 | bus_LV_1002-5_1_3_node_290 | 0.4 | n |  | TRUE
113 | bus_LV_1002-5_1_3_node_291 | 0.4 | n |  | TRUE
114 | bus_LV_1002-5_1_3_node_292 | 0.4 | n |  | TRUE
115 | bus_LV_1002-5_1_3_node_293 | 0.4 | n |  | TRUE
116 | bus_LV_1002-5_1_3_node_294 | 0.4 | n |  | TRUE
117 | bus_MV_124_0_node_128 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1002-5_1_3_load_5 | 0 | 0.0064653 | 0.0016204 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1002-5_1_3_load_6 | 1 | 0.00172 | 0.00043106 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1002-5_1_3_load_8 | 3 | 0.0015007 | 0.00037611 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1002-5_1_3_load_9 | 4 | 0.001755 | 0.00043984 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1002-5_1_3_load_10 | 5 | 0.0071654 | 0.0017958 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1002-5_1_3_load_72 | 6 | 0.00099364 | 0.00024903 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1002-5_1_3_load_62 | 7 | 0.0016442 | 0.00041207 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1002-5_1_3_load_11 | 8 | 0.0080901 | 0.0020276 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1002-5_1_3_load_12 | 9 | 0.00046274 | 0.00011597 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1002-5_1_3_load_14 | 10 | 0.00038141 | 9.5592e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1002-5_1_3_load_17 | 14 | 0.0018332 | 0.00045943 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1002-5_1_3_load_107 | 15 | 0.00037378 | 9.3677e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1002-5_1_3_load_102 | 16 | 0.00020521 | 5.1429e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1002-5_1_3_load_101 | 17 | 0.0018626 | 0.00046681 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1002-5_1_3_load_28 | 18 | 0.0014966 | 0.00037509 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1002-5_1_3_load_60 | 19 | 0.0053091 | 0.0013306 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1002-5_1_3_load_113 | 20 | 0.0045508 | 0.0011405 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1002-5_1_3_load_18 | 21 | 0.00061639 | 0.00015448 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1002-5_1_3_load_19 | 22 | 0.0011529 | 0.00028895 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1002-5_1_3_load_245 | 25 | 0.0024965 | 0.00062569 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1002-5_1_3_load_106 | 26 | 0.0004568 | 0.00011449 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1002-5_1_3_load_93 | 27 | 0.0010545 | 0.00026427 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1002-5_1_3_load_90 | 30 | 0.0018861 | 0.00047269 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1002-5_1_3_load_344 | 32 | 0.003158 | 0.00079146 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1002-5_1_3_load_29 | 34 | 0.0048802 | 0.0012231 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1002-5_1_3_load_27 | 35 | 0.0013871 | 0.00034765 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1002-5_1_3_load_30 | 37 | 0.00079613 | 0.00019953 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1002-5_1_3_load_31 | 38 | 0.0010787 | 0.00027034 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1002-5_1_3_load_32 | 39 | 0.00083446 | 0.00020913 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1002-5_1_3_load_34 | 41 | 0.00069486 | 0.00017415 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1002-5_1_3_load_104 | 42 | 0.00088223 | 0.00022111 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1002-5_1_3_load_67 | 43 | 0.0013163 | 0.00032989 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1002-5_1_3_load_65 | 44 | 0.0011949 | 0.00029948 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1002-5_1_3_load_36 | 45 | 0.0011301 | 0.00028323 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1002-5_1_3_load_37 | 46 | 0.0030122 | 0.00075493 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1002-5_1_3_load_98 | 47 | 0.006672 | 0.0016722 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1002-5_1_3_load_43 | 48 | 0.0014382 | 0.00036044 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1002-5_1_3_load_44 | 49 | 0.0094398 | 0.0023658 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1002-5_1_3_load_46 | 51 | 0.00059861 | 0.00015003 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1002-5_1_3_load_48 | 52 | 0.00080933 | 0.00020284 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1002-5_1_3_load_55 | 53 | 0.0011064 | 0.00027728 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1002-5_1_3_load_47 | 54 | 0.00073466 | 0.00018412 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1002-5_1_3_load_49 | 56 | 0.0032995 | 0.00082692 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1002-5_1_3_load_50 | 57 | 0.00079892 | 0.00020023 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1002-5_1_3_load_52 | 59 | 0.002015 | 0.000505 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1002-5_1_3_load_53 | 60 | 0.0029763 | 0.00074594 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1002-5_1_3_load_54 | 61 | 0.00039984 | 0.00010021 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1002-5_1_3_load_63 | 62 | 0.0018642 | 0.0004672 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1002-5_1_3_load_64 | 63 | 0.0013116 | 0.00032871 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1002-5_1_3_load_96 | 64 | 0.000473 | 0.00011854 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1002-5_1_3_load_57 | 66 | 0.0004289 | 0.00010749 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1002-5_1_3_load_58 | 67 | 0.00052533 | 0.00013166 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1002-5_1_3_load_295 | 68 | 0.00019338 | 4.8465e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1002-5_1_3_load_100 | 69 | 0.00082233 | 0.00020609 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1002-5_1_3_load_59 | 70 | 0.00088344 | 0.00022141 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1002-5_1_3_load_66 | 72 | 0.0013627 | 0.00034152 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1002-5_1_3_load_69 | 74 | 0.0011133 | 0.00027902 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1002-5_1_3_load_70 | 75 | 0.0014786 | 0.00037057 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1002-5_1_3_load_71 | 76 | 0.0012557 | 0.0003147 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1002-5_1_3_load_99 | 77 | 0.0045909 | 0.0011506 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1002-5_1_3_load_73 | 78 | 0.00071123 | 0.00017825 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1002-5_1_3_load_74 | 79 | 0.0017862 | 0.00044767 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1002-5_1_3_load_77 | 82 | 0.0032559 | 0.00081601 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1002-5_1_3_load_78 | 83 | 0.0017963 | 0.0004502 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1002-5_1_3_load_79 | 84 | 0.0022595 | 0.00056629 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1002-5_1_3_load_88 | 85 | 0.00091854 | 0.00023021 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1002-5_1_3_load_80 | 87 | 0.0018438 | 0.00046209 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1002-5_1_3_load_103 | 88 | 0.00063125 | 0.00015821 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1002-5_1_3_load_97 | 91 | 0.00062978 | 0.00015784 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1002-5_1_3_load_84 | 92 | 0.00113 | 0.00028321 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1002-5_1_3_load_85 | 93 | 0.0020044 | 0.00050234 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1002-5_1_3_load_89 | 94 | 0.0069381 | 0.0017389 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1002-5_1_3_load_91 | 95 | 0.0023632 | 0.00059228 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1002-5_1_3_load_110 | 96 | 0.00047565 | 0.00011921 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1002-5_1_3_load_218 | 97 | 0.00085741 | 0.00021489 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1002-5_1_3_load_111 | 98 | 0.00069946 | 0.0001753 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1002-5_1_3_load_112 | 99 | 0.0021876 | 0.00054827 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1002-5_1_3_load_114 | 100 | 0.00089782 | 0.00022502 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1002-5_1_3_load_115 | 101 | 0.00037287 | 9.345e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1002-5_1_3_load_116 | 102 | 0.00087935 | 0.00022039 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1002-5_1_3_load_118 | 103 | 0.00013221 | 3.3134e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1002-5_1_3_load_119 | 104 | 0.00080602 | 0.00020201 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1002-5_1_3_load_120 | 105 | 0.00026213 | 6.5695e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1002-5_1_3_load_217 | 107 | 0.00085138 | 0.00021337 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1002-5_1_3_load_246 | 108 | 0.00082575 | 0.00020695 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1002-5_1_3_load_286 | 109 | 0.00055534 | 0.00013918 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1002-5_1_3_load_287 | 110 | 0.0001232 | 3.0876e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1002-5_1_3_load_289 | 111 | 0.0016669 | 0.00041778 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1002-5_1_3_load_292 | 114 | 0.00029604 | 7.4195e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1002-5_1_3_load_293 | 115 | 0.00040258 | 0.0001009 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1002-5_1_3_load_294 | 116 | 0.00038577 | 9.6683e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1002-5_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0015766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1002-5_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1002-5_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.023953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1002-5_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1002-5_1_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.021761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1002-5_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0030199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1002-5_1_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.010528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1002-5_1_3_line_7 | NAYY 4x150 SE | 6 | 76 | 0.024051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1002-5_1_3_line_8 | NAYY 4x150 SE | 7 | 71 | 0.030857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1002-5_1_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.042523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1002-5_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.10371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1002-5_1_3_line_11 | NAYY 4x150 SE | 10 | 15 | 0.010434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1002-5_1_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.033183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1002-5_1_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.004428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1002-5_1_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.01646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1002-5_1_3_line_15 | NAYY 4x150 SE | 12 | 16 | 0.24004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1002-5_1_3_line_16 | NAYY 4x150 SE | 12 | 17 | 0.12146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1002-5_1_3_line_17 | NAYY 4x150 SE | 13 | 18 | 0.016024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1002-5_1_3_line_18 | NAYY 4x150 SE | 13 | 19 | 0.00092319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1002-5_1_3_line_19 | NAYY 4x150 SE | 14 | 20 | 0.029892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1002-5_1_3_line_20 | NAYY 4x150 SE | 15 | 90 | 0.052558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1002-5_1_3_line_21 | NAYY 4x150 SE | 16 | 96 | 0.0065319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1002-5_1_3_line_22 | NAYY 4x150 SE | 19 | 70 | 0.026083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1002-5_1_3_line_23 | NAYY 4x150 SE | 20 | 100 | 0.022017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1002-5_1_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.020619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1002-5_1_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.10227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1002-5_1_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.020923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1002-5_1_3_line_27 | NAYY 4x150 SE | 23 | 25 | 0.15693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1002-5_1_3_line_28 | NAYY 4x150 SE | 24 | 26 | 0.095789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1002-5_1_3_line_29 | NAYY 4x150 SE | 24 | 27 | 0.21911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1002-5_1_3_line_30 | NAYY 4x150 SE | 25 | 108 | 0.039482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1002-5_1_3_line_31 | NAYY 4x150 SE | 26 | 98 | 0.13725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1002-5_1_3_line_32 | NAYY 4x150 SE | 27 | 28 | 0.045542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1002-5_1_3_line_33 | NAYY 4x150 SE | 28 | 29 | 0.034884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1002-5_1_3_line_34 | NAYY 4x150 SE | 28 | 30 | 0.010403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1002-5_1_3_line_35 | NAYY 4x150 SE | 29 | 31 | 0.046854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1002-5_1_3_line_36 | NAYY 4x150 SE | 29 | 33 | 0.037576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1002-5_1_3_line_37 | NAYY 4x150 SE | 30 | 95 | 0.033687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1002-5_1_3_line_38 | NAYY 4x150 SE | 31 | 32 | 0.013005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1002-5_1_3_line_39 | NAYY 4x150 SE | 33 | 34 | 0.01451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1002-5_1_3_line_40 | NAYY 4x150 SE | 33 | 35 | 0.030169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1002-5_1_3_line_41 | NAYY 4x150 SE | 34 | 36 | 0.035956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1002-5_1_3_line_42 | NAYY 4x150 SE | 36 | 45 | 0.039434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1002-5_1_3_line_43 | NAYY 4x150 SE | 36 | 46 | 0.03902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1002-5_1_3_line_44 | NAYY 4x150 SE | 37 | 38 | 0.028749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1002-5_1_3_line_45 | NAYY 4x150 SE | 37 | 39 | 0.021744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1002-5_1_3_line_46 | NAYY 4x150 SE | 38 | 40 | 0.068602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1002-5_1_3_line_47 | NAYY 4x150 SE | 39 | 41 | 0.013856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1002-5_1_3_line_48 | NAYY 4x150 SE | 40 | 42 | 0.013548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1002-5_1_3_line_49 | NAYY 4x150 SE | 40 | 43 | 0.0090152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1002-5_1_3_line_50 | NAYY 4x150 SE | 41 | 44 | 0.012569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1002-5_1_3_line_51 | NAYY 4x150 SE | 42 | 97 | 0.019316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1002-5_1_3_line_52 | NAYY 4x150 SE | 43 | 72 | 0.031405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1002-5_1_3_line_53 | NAYY 4x150 SE | 44 | 54 | 0.0022194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1002-5_1_3_line_54 | NAYY 4x150 SE | 46 | 47 | 0.010431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1002-5_1_3_line_55 | NAYY 4x150 SE | 47 | 77 | 0.022213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1002-5_1_3_line_56 | NAYY 4x150 SE | 48 | 49 | 0.032498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1002-5_1_3_line_57 | NAYY 4x150 SE | 48 | 50 | 0.23408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1002-5_1_3_line_58 | NAYY 4x150 SE | 49 | 51 | 0.0016234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1002-5_1_3_line_59 | NAYY 4x150 SE | 50 | 52 | 0.18749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1002-5_1_3_line_60 | NAYY 4x150 SE | 51 | 53 | 0.0017324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1002-5_1_3_line_61 | NAYY 4x150 SE | 52 | 55 | 0.070023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1002-5_1_3_line_62 | NAYY 4x150 SE | 53 | 65 | 0.30382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_1002-5_1_3_line_63 | NAYY 4x150 SE | 55 | 93 | 0.20967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1002-5_1_3_line_64 | NAYY 4x150 SE | 56 | 57 | 0.018668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1002-5_1_3_line_65 | NAYY 4x150 SE | 56 | 58 | 0.050218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1002-5_1_3_line_66 | NAYY 4x150 SE | 57 | 59 | 0.012109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1002-5_1_3_line_67 | NAYY 4x150 SE | 58 | 60 | 0.017295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1002-5_1_3_line_68 | NAYY 4x150 SE | 58 | 61 | 0.029119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1002-5_1_3_line_69 | NAYY 4x150 SE | 59 | 62 | 0.0085345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1002-5_1_3_line_70 | NAYY 4x150 SE | 60 | 63 | 0.15373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1002-5_1_3_line_71 | NAYY 4x150 SE | 61 | 64 | 0.026457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1002-5_1_3_line_72 | NAYY 4x150 SE | 62 | 71 | 0.085653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1002-5_1_3_line_73 | NAYY 4x150 SE | 64 | 91 | 0.032794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1002-5_1_3_line_74 | NAYY 4x150 SE | 65 | 66 | 0.25561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1002-5_1_3_line_75 | NAYY 4x150 SE | 65 | 67 | 0.18181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1002-5_1_3_line_76 | NAYY 4x150 SE | 66 | 68 | 0.029254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1002-5_1_3_line_77 | NAYY 4x150 SE | 67 | 69 | 0.021357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1002-5_1_3_line_78 | NAYY 4x150 SE | 68 | 113 | 0.108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1002-5_1_3_line_79 | NAYY 4x150 SE | 69 | 89 | 0.10134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1002-5_1_3_line_80 | NAYY 4x150 SE | 70 | 71 | 0.028437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1002-5_1_3_line_81 | NAYY 4x150 SE | 72 | 73 | 0.014902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1002-5_1_3_line_82 | NAYY 4x150 SE | 73 | 74 | 0.016606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1002-5_1_3_line_83 | NAYY 4x150 SE | 73 | 75 | 0.012567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1002-5_1_3_line_84 | NAYY 4x150 SE | 74 | 76 | 0.00065447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1002-5_1_3_line_85 | NAYY 4x150 SE | 75 | 77 | 0.029617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1002-5_1_3_line_86 | NAYY 4x150 SE | 78 | 79 | 0.023557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1002-5_1_3_line_87 | NAYY 4x150 SE | 78 | 80 | 0.030653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1002-5_1_3_line_88 | NAYY 4x150 SE | 80 | 81 | 0.004407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1002-5_1_3_line_89 | NAYY 4x150 SE | 80 | 82 | 0.015263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1002-5_1_3_line_90 | NAYY 4x150 SE | 80 | 83 | 0.04235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1002-5_1_3_line_91 | NAYY 4x150 SE | 81 | 84 | 0.083775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1002-5_1_3_line_92 | NAYY 4x150 SE | 82 | 85 | 0.0072626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1002-5_1_3_line_93 | NAYY 4x150 SE | 83 | 86 | 0.053021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1002-5_1_3_line_94 | NAYY 4x150 SE | 84 | 87 | 0.020541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1002-5_1_3_line_95 | NAYY 4x150 SE | 85 | 94 | 0.01752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1002-5_1_3_line_96 | NAYY 4x150 SE | 86 | 88 | 0.012538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1002-5_1_3_line_97 | NAYY 4x150 SE | 88 | 90 | 0.010471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1002-5_1_3_line_98 | NAYY 4x150 SE | 89 | 90 | 0.079224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1002-5_1_3_line_99 | NAYY 4x150 SE | 89 | 91 | 0.021215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1002-5_1_3_line_100 | NAYY 4x150 SE | 92 | 93 | 0.043297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1002-5_1_3_line_101 | NAYY 4x150 SE | 97 | 107 | 0.019057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1002-5_1_3_line_102 | NAYY 4x150 SE | 98 | 99 | 0.014052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1002-5_1_3_line_103 | NAYY 4x150 SE | 101 | 102 | 0.043286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1002-5_1_3_line_104 | NAYY 4x150 SE | 102 | 103 | 0.012229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1002-5_1_3_line_105 | NAYY 4x150 SE | 103 | 104 | 0.0044813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1002-5_1_3_line_106 | NAYY 4x150 SE | 104 | 105 | 0.021919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1002-5_1_3_line_107 | NAYY 4x150 SE | 105 | 106 | 0.44211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1002-5_1_3_line_108 | NAYY 4x150 SE | 106 | 109 | 0.11803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1002-5_1_3_line_109 | NAYY 4x150 SE | 109 | 110 | 0.027017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1002-5_1_3_line_110 | NAYY 4x150 SE | 110 | 111 | 0.019232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1002-5_1_3_line_111 | NAYY 4x150 SE | 111 | 112 | 0.099833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1002-5_1_3_line_112 | NAYY 4x150 SE | 112 | 113 | 0.019055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1002-5_1_3_line_113 | NAYY 4x150 SE | 113 | 114 | 0.084772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1002-5_1_3_line_114 | NAYY 4x150 SE | 114 | 115 | 0.0227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1002-5_1_3_line_115 | NAYY 4x150 SE | 115 | 116 | 0.030035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1002-5_1_3_trafo_8 | 0.25 MVA 20/0.4 kV | 117 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32
0 | 2648649.8852 | 1208097.1806 | 2648651.2577 | 1208097.9563
1 | 2648629.7917 | 1208085.7499 | 2648635.8454 | 1208089.2456 | 2648649.8852 | 1208097.1806
2 | 2648672.1108 | 1208109.7419 | 2648651.2577 | 1208097.9563
3 | 2648629.7917 | 1208085.7499 | 2648628.9242 | 1208082.1074 | 2648628.0411 | 1208079.4542 | 2648619.3541 | 1208063.8358
4 | 2648629.7917 | 1208085.7499 | 2648626.448 | 1208084.622 | 2648623.9723 | 1208084.2794 | 2648621.1671 | 1208084.2566 | 2648617.5061 | 1208084.7493 | 2648611.7283 | 1208086.5811 | 2648608.7431 | 1208087.6544
5 | 2648617.8862 | 1208061.1966 | 2648619.3541 | 1208063.8358
6 | 2648598.8356 | 1208091.2165 | 2648608.7431 | 1208087.6544
7 | 2648617.8862 | 1208061.1966 | 2648616.8165 | 1208059.2733 | 2648615.2327 | 1208055.825 | 2648614.0851 | 1208052.0468 | 2648611.393 | 1208038.1996
8 | 2648571.1194 | 1208104.6279 | 2648590.7135 | 1208094.1367 | 2648598.8356 | 1208091.2165
9 | 2648643.5332 | 1208235.565 | 2648648.6604 | 1208243.5733 | 2648666.3216 | 1208271.4662
10 | 2648666.3216 | 1208271.4662 | 2648667.3127 | 1208273.0313 | 2648681.7031 | 1208311.3932 | 2648688.1276 | 1208343.0418 | 2648689.6594 | 1208365.8898 | 2648689.6129 | 1208371.5835
11 | 2648689.6129 | 1208371.5835 | 2648689.5278 | 1208382.0173
12 | 2648510.85 | 1208075.9103 | 2648512.3227 | 1208073.3763 | 2648514.4601 | 1208071.3814 | 2648518.1288 | 1208068.9987 | 2648537.7834 | 1208059.4862 | 2648538.852 | 1208058.9723
13 | 2648542.8066 | 1208056.9588 | 2648538.852 | 1208058.9723
14 | 2648538.852 | 1208058.9723 | 2648530.8165 | 1208044.6072
15 | 2648510.85 | 1208075.9103 | 2648510.1842 | 1208078.3174 | 2648509.9502 | 1208081.8509 | 2648510.2692 | 1208085.6334 | 2648517.6609 | 1208120.0246 | 2648520.0892 | 1208133.6745 | 2648521.4691 | 1208143.5026 | 2648522.3429 | 1208151.0474 | 2648522.3734 | 1208155.7059 | 2648522.2132 | 1208160.4518 | 2648521.323 | 1208168.0157 | 2648519.631 | 1208176.9516 | 2648517.2142 | 1208189.9506 | 2648513.6921 | 1208207.0431 | 2648512.1842 | 1208212.9676 | 2648510.3876 | 1208218.8787 | 2648507.813 | 1208226.0286 | 2648500.8777 | 1208244.0161 | 2648500.1187 | 1208248.5459 | 2648499.9238 | 1208253.8141 | 2648500.608 | 1208258.5002 | 2648502.2819 | 1208263.0164 | 2648504.6475 | 1208267.5382 | 2648508.2799 | 1208271.4811 | 2648512.6096 | 1208274.7515 | 2648522.7409 | 1208280.7262 | 2648525.8817 | 1208283.4089 | 2648527.0143 | 1208285.2969 | 2648527.8784 | 1208287.4941 | 2648529.0724 | 1208291.1838 | 2648529.7989 | 1208294.3915 | 2648529.6842 | 1208299.1489 | 2648529.6842 | 1208299.1489
16 | 2648510.85 | 1208075.9103 | 2648506.8625 | 1208076.3559 | 2648503.7709 | 1208076.9534 | 2648500.5918 | 1208078.0282 | 2648493.3141 | 1208081.9936 | 2648465.1083 | 1208099.7195 | 2648459.767 | 1208103.9786 | 2648456.9202 | 1208107.2018 | 2648455.0091 | 1208110.3659 | 2648453.6187 | 1208113.9901 | 2648452.6543 | 1208118.5405 | 2648452.3563 | 1208125.2753 | 2648452.0806 | 1208130.2093 | 2648451.4963 | 1208132.8839 | 2648450.1574 | 1208135.7858 | 2648448.3232 | 1208137.9055 | 2648445.586 | 1208139.8067 | 2648442.8346 | 1208140.6404 | 2648440.0806 | 1208140.8737 | 2648436.7031 | 1208140.1682 | 2648424.9044 | 1208134.3911
17 | 2648542.8066 | 1208056.9588 | 2648534.7921 | 1208043.0828
18 | 2648543.2785 | 1208057.7523 | 2648542.8066 | 1208056.9588
19 | 2648516.1382 | 1208018.5675 | 2648519.098 | 1208023.6579 | 2648530.8165 | 1208044.6072
20 | 2648683.0361 | 1208434.1312 | 2648689.4825 | 1208387.5788 | 2648689.5278 | 1208382.0173
21 | 2648529.6842 | 1208299.1489 | 2648529.0722 | 1208302.4236 | 2648527.8243 | 1208305.3708
22 | 2648556.6095 | 1208080.1711 | 2648543.2785 | 1208057.7523
23 | 2648505.0715 | 1207999.534 | 2648516.1382 | 1208018.5675
24 | 2648429.226 | 1207796.1154 | 2648435.239 | 1207793.0653 | 2648440.3265 | 1207789.1932 | 2648440.7293 | 1207785.4609 | 2648438.5383 | 1207782.4434
25 | 2648470.0879 | 1207699.916 | 2648475.284 | 1207702.3373 | 2648477.1271 | 1207705.7098 | 2648475.964 | 1207711.2925 | 2648433.5837 | 1207766.5587 | 2648433.1627 | 1207772.5254 | 2648435.5487 | 1207778.3259 | 2648438.5383 | 1207782.4434
26 | 2648457.3761 | 1207711.0415 | 2648462.4675 | 1207713.2619 | 2648466.0454 | 1207707.0985 | 2648470.0879 | 1207699.916
27 | 2648470.0879 | 1207699.916 | 2648607.1379 | 1207623.4625
28 | 2648457.3761 | 1207711.0415 | 2648443.9278 | 1207705.1846 | 2648425.5605 | 1207702.1117 | 2648363.4554 | 1207695.1136
29 | 2648457.3761 | 1207711.0415 | 2648442.2551 | 1207729.5519 | 2648407.5727 | 1207769.4272 | 2648397.8925 | 1207785.536 | 2648391.4496 | 1207802.7938 | 2648388.6052 | 1207824.4723 | 2648394.3333 | 1207847.5432 | 2648403.3508 | 1207866.2716 | 2648416.1987 | 1207882.3629 | 2648429.6033 | 1207894.5698
30 | 2648607.1379 | 1207623.4625 | 2648612.9931 | 1207623.1548 | 2648643.9644 | 1207636.2313
31 | 2648227.5563 | 1207699.1652 | 2648237.237 | 1207695.2839 | 2648314.8218 | 1207689.5298 | 2648327.8736 | 1207689.9023 | 2648359.5407 | 1207694.6725 | 2648363.4554 | 1207695.1136
32 | 2648461.2014 | 1207927.2873 | 2648442.35 | 1207906.1777 | 2648429.6033 | 1207894.5698
33 | 2648461.2014 | 1207927.2873 | 2648468.9341 | 1207937.5338 | 2648475.0292 | 1207946.2661 | 2648480.9638 | 1207956.0311
34 | 2648461.2014 | 1207927.2873 | 2648457.7567 | 1207932.0399 | 2648455.7242 | 1207936.0925
35 | 2648480.9638 | 1207956.0311 | 2648484.8843 | 1207953.5504 | 2648489.9196 | 1207962.641 | 2648492.6619 | 1207961.0623 | 2648513.2406 | 1207949.2003 | 2648515.9934 | 1207947.266 | 2648516.757 | 1207945.927
36 | 2648480.9638 | 1207956.0311 | 2648484.8843 | 1207953.5504 | 2648489.9196 | 1207962.641 | 2648500.539 | 1207982.5277
37 | 2648455.7242 | 1207936.0925 | 2648454.4927 | 1207939.818 | 2648453.8563 | 1207944.2265 | 2648452.0481 | 1207950.6155 | 2648449.8367 | 1207955.1669 | 2648444.6283 | 1207963.6518 | 2648444.136 | 1207965.2933 | 2648444.1334 | 1207967.2323
38 | 2648516.757 | 1207945.927 | 2648517.0663 | 1207944.3508 | 2648516.8604 | 1207942.5592 | 2648511.8864 | 1207934.3473
39 | 2648500.539 | 1207982.5277 | 2648513.8019 | 1207976.642
40 | 2648500.539 | 1207982.5277 | 2648515.2408 | 1208008.8716
41 | 2648547.2407 | 1207964.2075 | 2648543.7826 | 1207966.8587 | 2648540.7912 | 1207968.213 | 2648535.088 | 1207970.2123 | 2648527.6297 | 1207972.0638 | 2648521.3738 | 1207973.7696 | 2648515.7923 | 1207975.7587 | 2648513.8019 | 1207976.642
42 | 2648547.2407 | 1207964.2075 | 2648549.5605 | 1207967.8396 | 2648555.2315 | 1207988.4977 | 2648562.0915 | 1208000.3715
43 | 2648547.2407 | 1207964.2075 | 2648549.1252 | 1207962.4663 | 2648556.44 | 1207954.888 | 2648559.6724 | 1207951.9459 | 2648562.398 | 1207950.545 | 2648565.7365 | 1207949.516 | 2648568.5049 | 1207949.4051 | 2648571.5877 | 1207949.8971 | 2648574.4595 | 1207951.0878 | 2648576.8537 | 1207953.0529 | 2648578.2701 | 1207955.577
44 | 2648673.3576 | 1207938.9679 | 2648670.7101 | 1207931.8602 | 2648668.7936 | 1207929.1318 | 2648666.8694 | 1207927.3485 | 2648664.0233 | 1207925.791 | 2648661.4115 | 1207925.3473 | 2648658.3464 | 1207925.489 | 2648652.3046 | 1207927.0681
45 | 2648680.9473 | 1207959.3443 | 2648673.3576 | 1207938.9679
46 | 2648639.7584 | 1207985.9729 | 2648640.1576 | 1207980.8398 | 2648641.4547 | 1207973.7351 | 2648641.7682 | 1207970.7248 | 2648641.6339 | 1207967.6108 | 2648637.3474 | 1207943.1616 | 2648637.0256 | 1207939.7237 | 2648637.5316 | 1207936.4148 | 2648638.5779 | 1207933.9663 | 2648640.3209 | 1207931.8682 | 2648642.5933 | 1207930.119 | 2648645.3937 | 1207928.8744 | 2648652.3046 | 1207927.0681
47 | 2648680.9473 | 1207959.3443 | 2648685.7837 | 1207972.3288
48 | 2648639.7584 | 1207985.9729 | 2648637.4142 | 1207980.6841 | 2648635.408 | 1207974.9644 | 2648634.9872 | 1207973.3156
49 | 2648639.7584 | 1207985.9729 | 2648640.4722 | 1207993.5498 | 2648640.3727 | 1207994.9511
50 | 2648697.6145 | 1207968.0861 | 2648685.7837 | 1207972.3288 | 2648685.7837 | 1207972.3288
51 | 2648634.9872 | 1207973.3156 | 2648630.2102 | 1207954.5993
52 | 2648623.0394 | 1208018.5639 | 2648627.7765 | 1208016.7377 | 2648630.7488 | 1208014.9275 | 2648633.3911 | 1208012.5588 | 2648635.5448 | 1208009.4967 | 2648637.8656 | 1208005.5244 | 2648639.4879 | 1208001.4464 | 2648640.163 | 1207997.9054 | 2648640.3727 | 1207994.9511
53 | 2648697.6145 | 1207968.0861 | 2648699.7036 | 1207967.3369
54 | 2648578.2701 | 1207955.577 | 2648579.3946 | 1207959.3995 | 2648580.2455 | 1207963.2197 | 2648580.5175 | 1207965.7377
55 | 2648583.5981 | 1207987.707 | 2648583.1243 | 1207985.9786 | 2648582.1474 | 1207980.8232 | 2648580.5175 | 1207965.7377
56 | 2648942.6962 | 1207991.4307 | 2648950.288 | 1207983.6862 | 2648948.2497 | 1207970.7953 | 2648947.0619 | 1207962.2762
57 | 2648986.4754 | 1207735.6939 | 2648984.7384 | 1207749.0874 | 2648982.909 | 1207759.8342 | 2648980.4239 | 1207766.1842 | 2648976.7956 | 1207772.8695 | 2648970.2341 | 1207783.0549 | 2648965.5712 | 1207790.7323 | 2648961.0881 | 1207800.5902 | 2648957.1224 | 1207811.3306 | 2648952.2441 | 1207831.369 | 2648950.1932 | 1207845.9718 | 2648948.4053 | 1207870.2157 | 2648946.9915 | 1207899.8436 | 2648945.7491 | 1207950.2962 | 2648946.1314 | 1207955.6024 | 2648947.0619 | 1207962.2762
58 | 2648941.5598 | 1207992.59 | 2648942.6962 | 1207991.4307
59 | 2648986.4754 | 1207735.6939 | 2648986.9627 | 1207726.3369 | 2648982.2266 | 1207706.7866 | 2648983.1973 | 1207691.3411 | 2648985.5518 | 1207660.1423 | 2648985.8169 | 1207655.6418 | 2648985.6521 | 1207651.627 | 2648985.1121 | 1207648.8654 | 2648983.7393 | 1207645.6745 | 2648981.5864 | 1207643.0331 | 2648978.5484 | 1207640.7736 | 2648973.5361 | 1207638.1976 | 2648958.362 | 1207633.2926 | 2648954.7678 | 1207631.173 | 2648951.1764 | 1207627.7749 | 2648947.803 | 1207622.8333 | 2648939.9353 | 1207604.069 | 2648933.3445 | 1207587.2052 | 2648930.5429 | 1207577.4321 | 2648930.032 | 1207573.534
60 | 2648940.4371 | 1207993.9059 | 2648941.0875 | 1207993.0718 | 2648941.5598 | 1207992.59
61 | 2648953.3712 | 1207510.3357 | 2648950.3722 | 1207512.5791 | 2648941.554 | 1207526.2592 | 2648934.7584 | 1207539.011 | 2648931.3598 | 1207546.4208 | 2648929.8501 | 1207552.5008 | 2648928.962 | 1207559.7311 | 2648929.5554 | 1207569.8974 | 2648930.032 | 1207573.534
62 | 2648983.1325 | 1208282.0295 | 2648982.6872 | 1208263.1148 | 2648979.1679 | 1208246.3428 | 2648961.5459 | 1208213.8127 | 2648931.6525 | 1208163.7051 | 2648926.711 | 1208143.2749 | 2648925.4363 | 1208120.6958 | 2648934.2757 | 1208021.7772 | 2648935.1828 | 1208003.863 | 2648935.5481 | 1208001.0422 | 2648936.5388 | 1207998.9046 | 2648940.4371 | 1207993.9059
63 | 2648953.3712 | 1207510.3357 | 2648962.892 | 1207511.1141 | 2648980.7525 | 1207513.9178 | 2649001.4976 | 1207521.0031 | 2649030.7569 | 1207533.8507 | 2649051.636 | 1207549.598 | 2649074.1508 | 1207564.2915 | 2649091.9165 | 1207585.9945 | 2649101.0253 | 1207594.3187 | 2649118.6645 | 1207607.3491 | 2649126.9565 | 1207617.1158
64 | 2648633.7887 | 1208212.7276 | 2648624.2926 | 1208196.6549
65 | 2648661.9689 | 1208254.2769 | 2648646.7486 | 1208232.8181 | 2648634.9675 | 1208214.7228 | 2648633.7887 | 1208212.7276
66 | 2648624.2926 | 1208196.6549 | 2648618.133 | 1208186.2295
67 | 2648661.9689 | 1208254.2769 | 2648674.5388 | 1208242.3977
68 | 2648661.9689 | 1208254.2769 | 2648668.6123 | 1208265.6154 | 2648674.123 | 1208276.9447 | 2648675.2734 | 1208280.1215
69 | 2648618.133 | 1208186.2295 | 2648613.7917 | 1208178.8817
70 | 2648751.3842 | 1208185.9081 | 2648742.4703 | 1208182.8694 | 2648733.678 | 1208186.0996 | 2648726.7402 | 1208193.1359 | 2648722.8638 | 1208203.2658 | 2648722.8097 | 1208209.8914 | 2648734.304 | 1208241.6593 | 2648734.7227 | 1208244.3865 | 2648734.6001 | 1208247.2983 | 2648734.1311 | 1208248.8732 | 2648733.3895 | 1208250.3013 | 2648731.9284 | 1208251.4123 | 2648729.6833 | 1208252.628 | 2648726.3847 | 1208253.446 | 2648719.1028 | 1208253.2754 | 2648714.6678 | 1208252.6833 | 2648710.4457 | 1208251.148 | 2648703.7837 | 1208247.6805 | 2648689.8453 | 1208239.64 | 2648686.408 | 1208237.8887 | 2648684.3052 | 1208237.5047 | 2648681.5964 | 1208237.7827 | 2648679.5604 | 1208238.5332 | 2648676.0816 | 1208240.9396 | 2648674.5388 | 1208242.3977
71 | 2648675.2734 | 1208280.1215 | 2648683.4987 | 1208302.8362 | 2648684.0882 | 1208305.0578
72 | 2648571.1194 | 1208104.6279 | 2648585.792 | 1208130.8736 | 2648599.9725 | 1208154.9808 | 2648601.6557 | 1208158.3409 | 2648613.7917 | 1208178.8817
73 | 2648684.0882 | 1208305.0578 | 2648692.2021 | 1208335.6374 | 2648692.3153 | 1208336.7882
74 | 2648983.1325 | 1208282.0295 | 2649000.0268 | 1208280.9341 | 2649005.5094 | 1208279.8673 | 2649010.2919 | 1208277.9499 | 2649015.701 | 1208274.7257 | 2649031.7733 | 1208262.6284 | 2649036.5607 | 1208260.1329 | 2649040.7607 | 1208258.7888 | 2649045.4115 | 1208258.1044 | 2649052.0333 | 1208258.1143 | 2649090.624 | 1208264.5796 | 2649095.2103 | 1208266.196 | 2649097.9798 | 1208268.698 | 2649100.282 | 1208272.5637 | 2649101.4462 | 1208277.0647 | 2649102.195 | 1208283.0744 | 2649101.0827 | 1208287.9792 | 2649098.4747 | 1208292.6494 | 2649094.446 | 1208297.1856 | 2649087.0374 | 1208303.1949 | 2649059.0386 | 1208323.3877 | 2649054.2126 | 1208327.8174 | 2649051.5133 | 1208330.6413 | 2649048.9846 | 1208333.9891 | 2649046.7366 | 1208338.3288 | 2649045.3637 | 1208342.5755 | 2649044.7033 | 1208347.9955 | 2649044.9306 | 1208352.7223 | 2649045.599 | 1208357.4195 | 2649047.1456 | 1208361.6457 | 2649049.2215 | 1208366.221 | 2649053.9183 | 1208373.8085
75 | 2648983.1325 | 1208282.0295 | 2648950.6457 | 1208284.031 | 2648934.6989 | 1208285.4789 | 2648927.8715 | 1208286.4346 | 2648922.6993 | 1208287.6708 | 2648902.157 | 1208295.118 | 2648828.1705 | 1208323.7738 | 2648816.8874 | 1208327.6172 | 2648809.1348 | 1208329.2437 | 2648809.1348 | 1208329.2437
76 | 2649053.9183 | 1208373.8085 | 2649069.7993 | 1208398.3761
77 | 2648809.1348 | 1208329.2437 | 2648799.8435 | 1208330.3017 | 2648787.8388 | 1208330.441
78 | 2649142.1723 | 1208476.6162 | 2649103.4924 | 1208446.9697 | 2649099.0662 | 1208442.5529 | 2649094.906 | 1208437.2156 | 2649069.7993 | 1208398.3761
79 | 2648694.3924 | 1208357.9016 | 2648706.1847 | 1208354.996 | 2648712.7185 | 1208352.7258 | 2648716.9404 | 1208350.5589 | 2648720.4962 | 1208348.0198 | 2648724.5725 | 1208344.1285 | 2648731.3653 | 1208337.1466 | 2648733.5919 | 1208335.397 | 2648736.0047 | 1208334.1271 | 2648739.9539 | 1208332.7585 | 2648749.1896 | 1208331.0551 | 2648758.2464 | 1208330.7845 | 2648787.8388 | 1208330.441
80 | 2648571.1194 | 1208104.6279 | 2648569.8373 | 1208102.4162 | 2648556.6095 | 1208080.1711
81 | 2648608.4973 | 1208021.1945 | 2648613.136 | 1208021.0766 | 2648615.9371 | 1208020.6881 | 2648619.532 | 1208019.9058 | 2648622.0716 | 1208018.937 | 2648623.0394 | 1208018.5639
82 | 2648608.4973 | 1208021.1945 | 2648609.1449 | 1208026.6362 | 2648611.2681 | 1208037.5571
83 | 2648608.4973 | 1208021.1945 | 2648606.651 | 1208018.2444 | 2648603.5409 | 1208014.5836 | 2648600.6153 | 1208011.4549
84 | 2648611.393 | 1208038.1996 | 2648611.2681 | 1208037.5571
85 | 2648583.5981 | 1207987.707 | 2648584.3278 | 1207990.3688 | 2648585.9467 | 1207994.173 | 2648587.8456 | 1207997.2014 | 2648591.2325 | 1208001.4203 | 2648600.6153 | 1208011.4549
86 | 2648654.7081 | 1208577.063 | 2648645.7944 | 1208595.2329 | 2648643.9769 | 1208598.0092
87 | 2648665.4554 | 1208548.388 | 2648657.0501 | 1208572.289 | 2648654.7081 | 1208577.063
88 | 2648669.6714 | 1208549.712 | 2648665.4554 | 1208548.388
89 | 2648665.4554 | 1208548.388 | 2648663.7508 | 1208547.6625 | 2648651.4096 | 1208542.4145
90 | 2648665.4554 | 1208548.388 | 2648673.4211 | 1208507.529 | 2648673.5163 | 1208506.8135
91 | 2648669.6714 | 1208549.712 | 2648672.5162 | 1208551.3806 | 2648736.0406 | 1208588.5648 | 2648742.2583 | 1208591.4858
92 | 2648644.5431 | 1208544.482 | 2648644.5431 | 1208544.482 | 2648647.886 | 1208542.8749 | 2648651.4096 | 1208542.4145
93 | 2648680.5076 | 1208454.2557 | 2648673.5163 | 1208506.8135
94 | 2648742.2583 | 1208591.4858 | 2648760.8501 | 1208600.2203
95 | 2648644.5431 | 1208544.482 | 2648636.9098 | 1208560.2515
96 | 2648680.5076 | 1208454.2557 | 2648677.4321 | 1208449.1721 | 2648678.349 | 1208442.6398
97 | 2648683.0361 | 1208434.1312 | 2648679.1109 | 1208437.2121 | 2648678.349 | 1208442.6398
98 | 2648694.3924 | 1208357.9016 | 2648694.938 | 1208374.8937 | 2648693.7768 | 1208392.3611 | 2648692.4109 | 1208402.3002 | 2648688.717 | 1208429.2302 | 2648683.0361 | 1208434.1312
99 | 2648694.3924 | 1208357.9016 | 2648692.3153 | 1208336.7882
100 | 2649160.9843 | 1207640.1028 | 2649157.546 | 1207639.0318 | 2649147.4312 | 1207637.4588 | 2649143.4889 | 1207636.07 | 2649140.3596 | 1207633.8207 | 2649136.7817 | 1207629.7334 | 2649128.1604 | 1207618.5337 | 2649126.9565 | 1207617.1158
101 | 2648625.4972 | 1207936.1342 | 2648630.2102 | 1207954.5993
102 | 2648214.5132 | 1207704.3946 | 2648227.5563 | 1207699.1652
103 | 2649838.4994 | 1208641.2606 | 2649838.707 | 1208663.7421 | 2649839.3325 | 1208673.4975 | 2649841.3425 | 1208684.3412
104 | 2649838.4994 | 1208641.2606 | 2649838.4994 | 1208641.2606 | 2649839.6795 | 1208633.766 | 2649839.1281 | 1208629.1565
105 | 2649838.5959 | 1208624.7069 | 2649839.1281 | 1208629.1565
106 | 2649835.5329 | 1208603.0209 | 2649836.5528 | 1208607.6247 | 2649838.5959 | 1208624.7069
107 | 2649397.767 | 1208541.207 | 2649835.5329 | 1208603.0209
108 | 2649397.767 | 1208541.207 | 2649384.6822 | 1208554.2398 | 2649378.5794 | 1208559.5368 | 2649372.6999 | 1208562.6567 | 2649366.6835 | 1208564.8638 | 2649361.2037 | 1208565.619 | 2649352.8881 | 1208564.5496 | 2649311.7622 | 1208554.1928 | 2649299.9041 | 1208551.2709 | 2649290.5247 | 1208548.1681
109 | 2649290.5247 | 1208548.1681 | 2649288.3574 | 1208547.4512 | 2649265.755 | 1208537.4057
110 | 2649265.755 | 1208537.4057 | 2649248.1804 | 1208529.5948
111 | 2649157.4654 | 1208488.0265 | 2649163.6007 | 1208491.6903 | 2649180.1106 | 1208499.3418 | 2649248.1804 | 1208529.5948
112 | 2649142.1723 | 1208476.6162 | 2649156.1793 | 1208487.2599 | 2649157.4654 | 1208488.0265
113 | 2649142.1723 | 1208476.6162 | 2649154.5573 | 1208472.8271 | 2649166.2085 | 1208470.4327 | 2649174.9885 | 1208469.5934 | 2649180.2657 | 1208469.4478 | 2649185.3554 | 1208469.9122 | 2649189.977 | 1208470.9064 | 2649195.4753 | 1208472.5305 | 2649199.3687 | 1208473.3297 | 2649202.3897 | 1208472.9877 | 2649205.4088 | 1208471.9453 | 2649207.8933 | 1208470.2759 | 2649209.4173 | 1208467.9982 | 2649210.1124 | 1208464.8354 | 2649209.9166 | 1208461.8432 | 2649208.4918 | 1208456.6951 | 2649207.0593 | 1208454.3666
114 | 2649207.0593 | 1208454.3666 | 2649206.5188 | 1208453.4881 | 2649191.7802 | 1208437.6042
115 | 2649171.351 | 1208415.5874 | 2649191.7802 | 1208437.6042

## bus_geodata
| x | y | coords
0 | 2648649.8852 | 1208097.1806
1 | 2648651.2577 | 1208097.9563
2 | 2648629.7917 | 1208085.7499
3 | 2648672.1108 | 1208109.7419
4 | 2648619.3541 | 1208063.8358
5 | 2648608.7431 | 1208087.6544
6 | 2648617.8862 | 1208061.1966
7 | 2648598.8356 | 1208091.2165
8 | 2648643.5332 | 1208235.565
9 | 2648666.3216 | 1208271.4662
10 | 2648689.6129 | 1208371.5835
11 | 2648538.852 | 1208058.9723
12 | 2648510.85 | 1208075.9103
13 | 2648542.8066 | 1208056.9588
14 | 2648530.8165 | 1208044.6072
15 | 2648689.5278 | 1208382.0173
16 | 2648529.6842 | 1208299.1489
17 | 2648424.9044 | 1208134.3911
18 | 2648534.7921 | 1208043.0828
19 | 2648543.2785 | 1208057.7523
20 | 2648516.1382 | 1208018.5675
21 | 2648438.5383 | 1207782.4434
22 | 2648429.226 | 1207796.1154
23 | 2648470.0879 | 1207699.916
24 | 2648457.3761 | 1207711.0415
25 | 2648607.1379 | 1207623.4625
26 | 2648363.4554 | 1207695.1136
27 | 2648429.6033 | 1207894.5698
28 | 2648461.2014 | 1207927.2873
29 | 2648480.9638 | 1207956.0311
30 | 2648455.7242 | 1207936.0925
31 | 2648516.757 | 1207945.927
32 | 2648511.8864 | 1207934.3473
33 | 2648500.539 | 1207982.5277
34 | 2648513.8019 | 1207976.642
35 | 2648515.2408 | 1208008.8716
36 | 2648547.2407 | 1207964.2075
37 | 2648673.3576 | 1207938.9679
38 | 2648652.3046 | 1207927.0681
39 | 2648680.9473 | 1207959.3443
40 | 2648639.7584 | 1207985.9729
41 | 2648685.7837 | 1207972.3288
42 | 2648634.9872 | 1207973.3156
43 | 2648640.3727 | 1207994.9511
44 | 2648697.6145 | 1207968.0861
45 | 2648562.0915 | 1208000.3715
46 | 2648578.2701 | 1207955.577
47 | 2648580.5175 | 1207965.7377
48 | 2648947.0619 | 1207962.2762
49 | 2648942.6962 | 1207991.4307
50 | 2648986.4754 | 1207735.6939
51 | 2648941.5598 | 1207992.59
52 | 2648930.032 | 1207573.5341
53 | 2648940.4371 | 1207993.9059
54 | 2648699.7036 | 1207967.3369
55 | 2648953.3712 | 1207510.3357
56 | 2648633.7887 | 1208212.7276
57 | 2648624.2926 | 1208196.6549
58 | 2648661.9689 | 1208254.2769
59 | 2648618.133 | 1208186.2295
60 | 2648674.5388 | 1208242.3977
61 | 2648675.2734 | 1208280.1215
62 | 2648613.7917 | 1208178.8817
63 | 2648751.3842 | 1208185.9081
64 | 2648684.0882 | 1208305.0578
65 | 2648983.1325 | 1208282.0295
66 | 2649053.9183 | 1208373.8085
67 | 2648809.1348 | 1208329.2437
68 | 2649069.7993 | 1208398.3761
69 | 2648787.8388 | 1208330.441
70 | 2648556.6095 | 1208080.1711
71 | 2648571.1194 | 1208104.6279
72 | 2648623.0394 | 1208018.5639
73 | 2648608.4973 | 1208021.1945
74 | 2648611.2681 | 1208037.5571
75 | 2648600.6153 | 1208011.4549
76 | 2648611.393 | 1208038.1996
77 | 2648583.5981 | 1207987.707
78 | 2648654.7081 | 1208577.063
79 | 2648643.9769 | 1208598.0092
80 | 2648665.4554 | 1208548.388
81 | 2648669.6714 | 1208549.712
82 | 2648651.4096 | 1208542.4145
83 | 2648673.5163 | 1208506.8135
84 | 2648742.2583 | 1208591.4858
85 | 2648644.5431 | 1208544.482
86 | 2648680.5076 | 1208454.2557
87 | 2648760.8501 | 1208600.2203
88 | 2648678.349 | 1208442.6398
89 | 2648694.3924 | 1208357.9016
90 | 2648683.0361 | 1208434.1312
91 | 2648692.3153 | 1208336.7882
92 | 2649160.9843 | 1207640.1028
93 | 2649126.9565 | 1207617.1158
94 | 2648636.9098 | 1208560.2515
95 | 2648444.1334 | 1207967.2323
96 | 2648527.8243 | 1208305.3708
97 | 2648630.2102 | 1207954.5993
98 | 2648227.5563 | 1207699.1652
99 | 2648214.5132 | 1207704.3946
100 | 2648505.0715 | 1207999.534
101 | 2649841.3425 | 1208684.3412
102 | 2649838.4994 | 1208641.2606
103 | 2649839.1281 | 1208629.1565
104 | 2649838.5959 | 1208624.7069
105 | 2649835.5329 | 1208603.0209
106 | 2649397.767 | 1208541.207
107 | 2648625.4972 | 1207936.1342
108 | 2648643.9644 | 1207636.2313
109 | 2649290.5247 | 1208548.1681
110 | 2649265.755 | 1208537.4057
111 | 2649248.1804 | 1208529.5948
112 | 2649157.4654 | 1208488.0265
113 | 2649142.1723 | 1208476.6162
114 | 2649207.0593 | 1208454.3666
115 | 2649191.7802 | 1208437.6042
116 | 2649171.351 | 1208415.5874
117 | 2648629.7917 | 1208085.7499

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99806 | -0.013488 | 0.0064653 | 0.0016204
1 | 0.99818 | -0.012662 | 0.00172 | 0.00043106
2 | 0.99639 | -0.02512 | 0 | 0
3 | 1 | 0 | -0.16093 | -0.040337
4 | 0.99442 | -0.03887 | 0.001755 | 0.00043984
5 | 0.9954 | -0.032016 | 0.0071654 | 0.0017958
6 | 0.99419 | -0.040521 | 0.00099364 | 0.00024903
7 | 0.99496 | -0.035104 | 0.0016442 | 0.00041207
8 | 0.97927 | -0.14611 | 0.0080901 | 0.0020276
9 | 0.97977 | -0.14253 | 0.00046274 | 0.00011597
10 | 0.98106 | -0.13332 | 0.00038141 | 9.5592e-05
11 | 0.99228 | -0.054007 | 0 | 0
12 | 0.99215 | -0.054875 | 0 | 0
13 | 0.99234 | -0.053564 | 0 | 0
14 | 0.9921 | -0.055223 | 0.0018332 | 0.00045943
15 | 0.9812 | -0.13235 | 0.00037378 | 9.3677e-05
16 | 0.99192 | -0.056562 | 0.00020521 | 5.1429e-05
17 | 0.99183 | -0.057177 | 0.0018626 | 0.00046681
18 | 0.9923 | -0.053807 | 0.0014966 | 0.00037509
19 | 0.99235 | -0.053458 | 0.0053091 | 0.0013306
20 | 0.99187 | -0.056876 | 0.0045508 | 0.0011405
21 | 0.97886 | -0.14937 | 0.00061639 | 0.00015448
22 | 0.97882 | -0.14962 | 0.0011529 | 0.00028895
23 | 0.97912 | -0.14748 | 0 | 0
24 | 0.97927 | -0.14636 | 0 | 0
25 | 0.97836 | -0.15293 | 0.0024965 | 0.00062569
26 | 0.97881 | -0.14972 | 0.0004568 | 0.00011449
27 | 0.98197 | -0.12703 | 0.0010545 | 0.00026427
28 | 0.9826 | -0.12252 | 0 | 0
29 | 0.98329 | -0.11754 | 0 | 0
30 | 0.98253 | -0.12298 | 0.0018861 | 0.00047269
31 | 0.98308 | -0.11907 | 0 | 0
32 | 0.98302 | -0.11949 | 0.003158 | 0.00079146
33 | 0.98421 | -0.11096 | 0 | 0
34 | 0.9846 | -0.10821 | 0.0048802 | 0.0012231
35 | 0.98415 | -0.11139 | 0.0013871 | 0.00034765
36 | 0.98581 | -0.099607 | 0 | 0
37 | 0.98962 | -0.072639 | 0.00079613 | 0.00019953
38 | 0.9898 | -0.071391 | 0.0010787 | 0.00027034
39 | 0.98952 | -0.073407 | 0.00083446 | 0.00020913
40 | 0.99033 | -0.067658 | 0 | 0
41 | 0.98946 | -0.073778 | 0.00069486 | 0.00017415
42 | 0.99028 | -0.068016 | 0.00088223 | 0.00022111
43 | 0.99043 | -0.066929 | 0.0013163 | 0.00032989
44 | 0.98943 | -0.074025 | 0.0011949 | 0.00029948
45 | 0.98575 | -0.10007 | 0.0011301 | 0.00028323
46 | 0.98719 | -0.089841 | 0.0030122 | 0.00075493
47 | 0.9876 | -0.086913 | 0.006672 | 0.0016722
48 | 0.97784 | -0.15673 | 0.0014382 | 0.00036044
49 | 0.97809 | -0.15488 | 0.0094398 | 0.0023658
50 | 0.97649 | -0.16652 | 0 | 0
51 | 0.97813 | -0.15463 | 0.00059861 | 0.00015003
52 | 0.97541 | -0.17434 | 0.00080933 | 0.00020284
53 | 0.97817 | -0.15435 | 0.0011064 | 0.00027728
54 | 0.98943 | -0.074042 | 0.00073466 | 0.00018412
55 | 0.97509 | -0.17667 | 0 | 0
56 | 0.98967 | -0.072269 | 0.0032995 | 0.00082692
57 | 0.99024 | -0.068252 | 0.00079892 | 0.00020023
58 | 0.98822 | -0.08253 | 0 | 0
59 | 0.99061 | -0.065616 | 0.002015 | 0.000505
60 | 0.98811 | -0.083291 | 0.0029763 | 0.00074594
61 | 0.98744 | -0.088065 | 0.00039984 | 0.00010021
62 | 0.99089 | -0.063701 | 0.0018642 | 0.0004672
63 | 0.98782 | -0.085364 | 0.0013116 | 0.00032871
64 | 0.98673 | -0.093065 | 0.000473 | 0.00011854
65 | 0.98183 | -0.1281 | 0 | 0
66 | 0.9794 | -0.14565 | 0.0004289 | 0.00010749
67 | 0.98386 | -0.1135 | 0.00052533 | 0.00013166
68 | 0.97915 | -0.14753 | 0.00019338 | 4.8465e-05
69 | 0.98411 | -0.11175 | 0.00082233 | 0.00020609
70 | 0.99298 | -0.049051 | 0.00088344 | 0.00022141
71 | 0.99369 | -0.043999 | 0 | 0
72 | 0.99085 | -0.063971 | 0.0013627 | 0.00034152
73 | 0.99108 | -0.062361 | 0 | 0
74 | 0.99229 | -0.053801 | 0.0011133 | 0.00027902
75 | 0.99035 | -0.067494 | 0.0014786 | 0.00037057
76 | 0.99234 | -0.053457 | 0.0012557 | 0.0003147
77 | 0.98869 | -0.079173 | 0.0045909 | 0.0011506
78 | 0.97854 | -0.15136 | 0.00071123 | 0.00017825
79 | 0.97847 | -0.1518 | 0.0017862 | 0.00044767
80 | 0.97865 | -0.15057 | 0 | 0
81 | 0.97862 | -0.15075 | 0 | 0
82 | 0.9784 | -0.15233 | 0.0032559 | 0.00081601
83 | 0.97974 | -0.14275 | 0.0017963 | 0.0004502
84 | 0.97812 | -0.15434 | 0.0022595 | 0.00056629
85 | 0.97832 | -0.15293 | 0.00091854 | 0.00023021
86 | 0.98125 | -0.132 | 0 | 0
87 | 0.97807 | -0.15474 | 0.0018438 | 0.00046209
88 | 0.9816 | -0.12946 | 0.00063125 | 0.00015821
89 | 0.98531 | -0.10316 | 0 | 0
90 | 0.98191 | -0.12727 | 0 | 0
91 | 0.98586 | -0.099219 | 0.00062978 | 0.00015784
92 | 0.97405 | -0.18412 | 0.00113 | 0.00028321
93 | 0.97413 | -0.1836 | 0.0020044 | 0.00050234
94 | 0.97814 | -0.1542 | 0.0069381 | 0.0017389
95 | 0.98242 | -0.1238 | 0.0023632 | 0.00059228
96 | 0.99191 | -0.056594 | 0.00047565 | 0.00011921
97 | 0.99023 | -0.068352 | 0.00085741 | 0.00021489
98 | 0.97823 | -0.15386 | 0.00069946 | 0.0001753
99 | 0.97819 | -0.15418 | 0.0021876 | 0.00054827
100 | 0.99184 | -0.057077 | 0.00089782 | 0.00022502
101 | 0.97505 | -0.1773 | 0.00037287 | 9.345e-05
102 | 0.97507 | -0.17713 | 0.00087935 | 0.00022039
103 | 0.97509 | -0.17696 | 0.00013221 | 3.3134e-05
104 | 0.9751 | -0.1769 | 0.00080602 | 0.00020201
105 | 0.97517 | -0.17639 | 0.00026213 | 6.5695e-05
106 | 0.97676 | -0.1649 | 0 | 0
107 | 0.99021 | -0.068518 | 0.00085138 | 0.00021337
108 | 0.97831 | -0.15327 | 0.00082575 | 0.00020695
109 | 0.97718 | -0.16181 | 0.00055534 | 0.00013918
110 | 0.9773 | -0.16094 | 0.0001232 | 3.0876e-05
111 | 0.97739 | -0.1603 | 0.0016669 | 0.00041778
112 | 0.97809 | -0.15523 | 0 | 0
113 | 0.97822 | -0.15426 | 0 | 0
114 | 0.97808 | -0.15522 | 0.00029604 | 7.4195e-05
115 | 0.97806 | -0.15541 | 0.00040258 | 0.0001009
116 | 0.97804 | -0.15553 | 0.00038577 | 9.6683e-05
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.15811 | -0.039791 | 0.15813 | 0.039798 | 1.8231e-05 | 6.9503e-06 | 0.23579 | 0.23579 | 0.23579 | 0.99806 | -0.013488 | 0.99818 | -0.012662 | 29.1096
1 | 0.15165 | 0.038171 | -0.1514 | -0.038077 | 0.00024592 | 9.368e-05 | 0.22615 | 0.22615 | 0.22615 | 0.99806 | -0.013488 | 0.99639 | -0.02512 | 27.9197
2 | -0.15985 | -0.040229 | 0.16013 | 0.040337 | 0.00028305 | 0.00010792 | 0.23835 | 0.23835 | 0.23835 | 0.99818 | -0.012662 | 1 | 0 | 29.4262
3 | 0.056329 | 0.014172 | -0.056222 | -0.014131 | 0.00010785 | 4.1164e-05 | 0.084142 | 0.084142 | 0.084142 | 0.99639 | -0.02512 | 0.99442 | -0.03887 | 31.1638
4 | 0.095071 | 0.023905 | -0.094979 | -0.023871 | 9.1277e-05 | 3.4257e-05 | 0.14201 | 0.14201 | 0.14201 | 0.99639 | -0.02512 | 0.9954 | -0.032016 | 17.5318
5 | 0.054467 | 0.013691 | -0.054454 | -0.013687 | 1.2522e-05 | 4.7769e-06 | 0.081516 | 0.081516 | 0.081516 | 0.99442 | -0.03887 | 0.99419 | -0.040521 | 30.1912
6 | 0.087814 | 0.022075 | -0.087776 | -0.022061 | 3.7751e-05 | 1.4109e-05 | 0.1313 | 0.1313 | 0.1313 | 0.9954 | -0.032016 | 0.99496 | -0.035104 | 16.2094
7 | 0.05346 | 0.013438 | -0.053364 | -0.013401 | 9.6118e-05 | 3.6657e-05 | 0.080029 | 0.080029 | 0.080029 | 0.99419 | -0.040521 | 0.99234 | -0.053457 | 29.6404
8 | 0.086132 | 0.021649 | -0.086026 | -0.021609 | 0.00010654 | 3.9775e-05 | 0.12884 | 0.12884 | 0.12884 | 0.99496 | -0.035104 | 0.99369 | -0.043999 | 15.9059
9 | -0.0080901 | -0.0020276 | 0.0080941 | 0.0020286 | 4.0097e-06 | 1.0069e-06 | 0.012293 | 0.012293 | 0.012293 | 0.97927 | -0.14611 | 0.97977 | -0.14253 | 4.5529
10 | -0.0085568 | -0.0021445 | 0.0085677 | 0.0021474 | 1.0929e-05 | 2.8956e-06 | 0.012996 | 0.012995 | 0.012996 | 0.97977 | -0.14253 | 0.98106 | -0.13332 | 4.8132
11 | -0.0089491 | -0.002243 | 0.0089503 | 0.0022434 | 1.1996e-06 | 3.296e-07 | 0.013574 | 0.013574 | 0.013574 | 0.98106 | -0.13332 | 0.9812 | -0.13235 | 5.0272
12 | 0.0025445 | 0.00063268 | -0.0025442 | -0.00063299 | 3.0121e-07 | -3.1273e-07 | 0.003814 | 0.0038141 | 0.0038141 | 0.99228 | -0.054007 | 0.99215 | -0.054875 | 1.4126
13 | -0.0098288 | -0.0024577 | 0.0098294 | 0.0024579 | 6.001e-07 | 1.7361e-07 | 0.014737 | 0.014737 | 0.014737 | 0.99228 | -0.054007 | 0.99234 | -0.053564 | 5.4582
14 | 0.0072843 | 0.0018251 | -0.007283 | -0.0018248 | 1.2255e-06 | 2.5877e-07 | 0.010923 | 0.010923 | 0.010923 | 0.99228 | -0.054007 | 0.9921 | -0.055223 | 4.0457
15 | 0.00068102 | 0.00016752 | -0.00068086 | -0.00017056 | 1.5609e-07 | -3.0392e-06 | 0.0010203 | 0.0010214 | 0.0010214 | 0.99215 | -0.054875 | 0.99192 | -0.056562 | 0.37828
16 | 0.0018632 | 0.00046547 | -0.0018626 | -0.00046681 | 5.9171e-07 | -1.3404e-06 | 0.0027939 | 0.0027944 | 0.0027944 | 0.99215 | -0.054875 | 0.99183 | -0.057177 | 1.035
17 | 0.0014967 | 0.00037491 | -0.0014966 | -0.00037509 | 5.0363e-08 | -1.8764e-07 | 0.0022442 | 0.0022443 | 0.0022443 | 0.99234 | -0.053564 | 0.9923 | -0.053807 | 0.83122
18 | -0.011326 | -0.0028328 | 0.011326 | 0.0028329 | 1.6612e-07 | 5.1966e-08 | 0.016981 | 0.016981 | 0.016981 | 0.99234 | -0.053564 | 0.99235 | -0.053458 | 6.2894
19 | 0.0054499 | 0.0013654 | -0.0054486 | -0.0013653 | 1.2463e-06 | 9.3424e-08 | 0.0081739 | 0.008174 | 0.008174 | 0.9921 | -0.055223 | 0.99187 | -0.056876 | 3.0274
20 | -0.0093241 | -0.002337 | 0.0093307 | 0.0023389 | 6.5575e-06 | 1.8578e-06 | 0.01414 | 0.01414 | 0.01414 | 0.9812 | -0.13235 | 0.98191 | -0.12727 | 5.2372
21 | 0.00047566 | 0.00011913 | -0.00047565 | -0.00011921 | 2.0752e-09 | -8.3516e-08 | 0.00071352 | 0.00071355 | 0.00071355 | 0.99192 | -0.056562 | 0.99191 | -0.056594 | 0.26428
22 | -0.016635 | -0.0041635 | 0.016645 | 0.004167 | 1.0125e-05 | 3.5572e-06 | 0.024942 | 0.024942 | 0.024942 | 0.99235 | -0.053458 | 0.99298 | -0.049051 | 9.2379
23 | 0.00089785 | 0.00022474 | -0.00089782 | -0.00022502 | 2.4924e-08 | -2.7457e-07 | 0.0013469 | 0.001347 | 0.001347 | 0.99187 | -0.056876 | 0.99184 | -0.057077 | 0.49888
24 | 0.001153 | 0.0002887 | -0.0011529 | -0.00028895 | 3.9521e-08 | -2.4398e-07 | 0.0017526 | 0.0017527 | 0.0017527 | 0.97886 | -0.14937 | 0.97882 | -0.14962 | 0.64914
25 | -0.0017693 | -0.00044319 | 0.0017698 | 0.00044208 | 4.6155e-07 | -1.1083e-06 | 0.0026896 | 0.0026891 | 0.0026896 | 0.97886 | -0.14937 | 0.97912 | -0.14748 | 0.99615
26 | -0.0050946 | -0.0012732 | 0.0050954 | 0.0012733 | 7.824e-07 | 3.7727e-08 | 0.0077412 | 0.0077412 | 0.0077412 | 0.97912 | -0.14748 | 0.97927 | -0.14636 | 2.8671
27 | 0.0033248 | 0.00083115 | -0.0033223 | -0.00083216 | 2.4998e-06 | -1.0108e-06 | 0.0050521 | 0.0050528 | 0.0050528 | 0.97912 | -0.14748 | 0.97836 | -0.15293 | 1.8714
28 | 0.0033472 | 0.00083622 | -0.0033457 | -0.00083683 | 1.5458e-06 | -6.1003e-07 | 0.0050851 | 0.0050856 | 0.0050856 | 0.97927 | -0.14636 | 0.97881 | -0.14972 | 1.8835
29 | -0.0084426 | -0.0021095 | 0.0084651 | 0.0021154 | 2.2491e-05 | 5.8862e-06 | 0.012826 | 0.012825 | 0.012826 | 0.97927 | -0.14636 | 0.98197 | -0.12703 | 4.7505
30 | 0.00082579 | 0.00020647 | -0.00082575 | -0.00020695 | 3.8858e-08 | -4.8083e-07 | 0.0012558 | 0.001256 | 0.001256 | 0.97836 | -0.15293 | 0.97831 | -0.15327 | 0.46517
31 | 0.0028888 | 0.00072235 | -0.0028872 | -0.00072344 | 1.6516e-06 | -1.0888e-06 | 0.0043911 | 0.0043917 | 0.0043917 | 0.97881 | -0.14972 | 0.97823 | -0.15386 | 1.6266
32 | -0.0095195 | -0.0023796 | 0.0095255 | 0.0023813 | 5.9117e-06 | 1.6972e-06 | 0.014423 | 0.014423 | 0.014423 | 0.98197 | -0.12703 | 0.9826 | -0.12252 | 5.3419
33 | -0.013775 | -0.003446 | 0.013785 | 0.0034492 | 9.4706e-06 | 3.2004e-06 | 0.020859 | 0.020858 | 0.020859 | 0.9826 | -0.12252 | 0.98329 | -0.11754 | 7.7254
34 | 0.0042498 | 0.0010646 | -0.0042495 | -0.0010646 | 2.6887e-07 | -2.8355e-08 | 0.0064356 | 0.0064357 | 0.0064357 | 0.9826 | -0.12252 | 0.98253 | -0.12298 | 2.3836
35 | 0.0031588 | 0.00079103 | -0.0031581 | -0.00079137 | 6.6805e-07 | -3.3725e-07 | 0.00478 | 0.0047802 | 0.0047802 | 0.98329 | -0.11754 | 0.98308 | -0.11907 | 1.7705
36 | -0.016944 | -0.0042402 | 0.016959 | 0.0042456 | 1.5413e-05 | 5.4508e-06 | 0.025638 | 0.025638 | 0.025638 | 0.98329 | -0.11754 | 0.98421 | -0.11096 | 9.4957
37 | 0.0023635 | 0.00059195 | -0.0023632 | -0.00059228 | 2.6931e-07 | -3.2301e-07 | 0.0035793 | 0.0035794 | 0.0035794 | 0.98253 | -0.12298 | 0.98242 | -0.1238 | 1.3257
38 | 0.0031581 | 0.00079137 | -0.003158 | -0.00079146 | 1.8544e-07 | -9.3559e-08 | 0.0047802 | 0.0047803 | 0.0047803 | 0.98308 | -0.11907 | 0.98302 | -0.11949 | 1.7705
39 | -0.018346 | -0.0045929 | 0.018353 | 0.0045954 | 6.9651e-06 | 2.4944e-06 | 0.027735 | 0.027735 | 0.027735 | 0.98421 | -0.11096 | 0.9846 | -0.10821 | 10.2724
40 | 0.0013872 | 0.00034729 | -0.0013871 | -0.00034765 | 8.28e-08 | -3.5152e-07 | 0.0020972 | 0.0020973 | 0.0020973 | 0.98421 | -0.11096 | 0.98415 | -0.11139 | 0.77677
41 | -0.023233 | -0.0058185 | 0.023261 | 0.0058287 | 2.7659e-05 | 1.018e-05 | 0.035111 | 0.035111 | 0.035111 | 0.9846 | -0.10821 | 0.98581 | -0.099607 | 13.004
42 | 0.0011302 | 0.00028276 | -0.0011301 | -0.00028323 | 7.1605e-08 | -4.7519e-07 | 0.0017058 | 0.0017059 | 0.0017059 | 0.98581 | -0.099607 | 0.98575 | -0.10007 | 0.63183
43 | -0.024391 | -0.0061115 | 0.024424 | 0.0061237 | 3.3003e-05 | 1.2195e-05 | 0.036816 | 0.036816 | 0.036816 | 0.98581 | -0.099607 | 0.98719 | -0.089841 | 13.6357
44 | -0.0042556 | -0.001066 | 0.0042563 | 0.0010659 | 7.3447e-07 | -8.6961e-08 | 0.0063986 | 0.0063985 | 0.0063986 | 0.98962 | -0.072639 | 0.9898 | -0.071391 | 2.3699
45 | 0.0034595 | 0.00086646 | -0.0034591 | -0.0008666 | 3.6711e-07 | -1.3815e-07 | 0.0052015 | 0.0052016 | 0.0052016 | 0.98962 | -0.072639 | 0.98952 | -0.073407 | 1.9265
46 | -0.005335 | -0.0013362 | 0.0053378 | 0.0013364 | 2.7534e-06 | 1.7678e-07 | 0.0080201 | 0.0080198 | 0.0080201 | 0.9898 | -0.071391 | 0.99033 | -0.067658 | 2.9704
47 | 0.0026247 | 0.00065746 | -0.0026245 | -0.00065759 | 1.3469e-07 | -1.2618e-07 | 0.0039468 | 0.0039469 | 0.0039469 | 0.98952 | -0.073407 | 0.98946 | -0.073778 | 1.4618
48 | 0.0025912 | 0.00064879 | -0.0025911 | -0.00064891 | 1.2814e-07 | -1.2503e-07 | 0.0038932 | 0.0038933 | 0.0038933 | 0.99033 | -0.067658 | 0.99028 | -0.068016 | 1.442
49 | -0.007929 | -0.0019852 | 0.0079298 | 0.0019854 | 7.9837e-07 | 1.9106e-07 | 0.011913 | 0.011913 | 0.011913 | 0.99033 | -0.067658 | 0.99043 | -0.066929 | 4.4122
50 | 0.0019297 | 0.00048344 | -0.0019296 | -0.00048358 | 6.6045e-08 | -1.3603e-07 | 0.0029019 | 0.0029019 | 0.0029019 | 0.98946 | -0.073778 | 0.98943 | -0.074025 | 1.0748
51 | 0.0017089 | 0.00042781 | -0.0017088 | -0.00042802 | 7.9468e-08 | -2.1794e-07 | 0.0025676 | 0.0025677 | 0.0025677 | 0.99028 | -0.068016 | 0.99023 | -0.068352 | 0.95101
52 | -0.0092461 | -0.0023153 | 0.0092499 | 0.0023163 | 3.7811e-06 | 1.0499e-06 | 0.013891 | 0.01389 | 0.013891 | 0.99043 | -0.066929 | 0.99085 | -0.063971 | 5.1447
53 | 0.00073466 | 0.00018409 | -0.00073466 | -0.00018412 | 1.6906e-09 | -2.7854e-08 | 0.0011049 | 0.0011049 | 0.0011049 | 0.98943 | -0.074025 | 0.98943 | -0.074042 | 0.40921
54 | -0.027436 | -0.0068786 | 0.027448 | 0.0068827 | 1.1133e-05 | 4.1484e-06 | 0.041357 | 0.041357 | 0.041357 | 0.98719 | -0.089841 | 0.9876 | -0.086913 | 15.3173
55 | -0.03412 | -0.0085549 | 0.034156 | 0.0085687 | 3.6632e-05 | 1.3805e-05 | 0.051409 | 0.051409 | 0.051409 | 0.9876 | -0.086913 | 0.98869 | -0.079173 | 19.0405
56 | -0.0053955 | -0.0013448 | 0.0053969 | 0.0013449 | 1.3661e-06 | 1.1767e-07 | 0.0082079 | 0.0082077 | 0.0082079 | 0.97784 | -0.15673 | 0.97809 | -0.15488 | 3.04
57 | 0.0039573 | 0.00098432 | -0.003952 | -0.00098522 | 5.2932e-06 | -8.9641e-07 | 0.0060194 | 0.0060204 | 0.0060204 | 0.97784 | -0.15673 | 0.97649 | -0.16652 | 2.2298
58 | -0.014837 | -0.0037107 | 0.014837 | 0.0037109 | 5.1598e-07 | 1.7808e-07 | 0.022569 | 0.022569 | 0.022569 | 0.97809 | -0.15488 | 0.97813 | -0.15463 | 8.3589
59 | 0.003952 | 0.00098522 | -0.0039478 | -0.00098593 | 4.2411e-06 | -7.1166e-07 | 0.0060204 | 0.0060212 | 0.0060212 | 0.97649 | -0.16652 | 0.97541 | -0.17434 | 2.2301
60 | -0.015436 | -0.0038609 | 0.015436 | 0.0038611 | 5.9595e-07 | 2.0747e-07 | 0.02348 | 0.02348 | 0.02348 | 0.97813 | -0.15463 | 0.97817 | -0.15435 | 8.6961
61 | 0.0031385 | 0.00078309 | -0.0031375 | -0.00078358 | 1.0012e-06 | -4.8868e-07 | 0.0047866 | 0.0047869 | 0.0047869 | 0.97541 | -0.17434 | 0.97509 | -0.17667 | 1.7729
62 | -0.016543 | -0.0041384 | 0.016603 | 0.0041538 | 6.0013e-05 | 1.5426e-05 | 0.025163 | 0.02516 | 0.025163 | 0.97817 | -0.15435 | 0.98183 | -0.1281 | 4.6597
63 | 0.0031375 | 0.00078358 | -0.0031345 | -0.00078504 | 2.9986e-06 | -1.4595e-06 | 0.0047869 | 0.0047878 | 0.0047878 | 0.97509 | -0.17667 | 0.97413 | -0.1836 | 1.7733
64 | -0.063542 | -0.015947 | 0.063578 | 0.01596 | 3.5449e-05 | 1.2914e-05 | 0.095546 | 0.095546 | 0.095546 | 0.98967 | -0.072269 | 0.99024 | -0.068252 | 11.7959
65 | 0.060243 | 0.01512 | -0.060157 | -0.015089 | 8.5713e-05 | 3.1034e-05 | 0.090586 | 0.090586 | 0.090586 | 0.98967 | -0.072269 | 0.98822 | -0.08253 | 11.1835
66 | -0.064377 | -0.01616 | 0.0644 | 0.016169 | 2.3574e-05 | 8.5996e-06 | 0.096747 | 0.096747 | 0.096747 | 0.99024 | -0.068252 | 0.99061 | -0.065616 | 11.944
67 | 0.0042887 | 0.0010728 | -0.0042883 | -0.0010728 | 4.4997e-07 | -4.8494e-08 | 0.0064571 | 0.0064571 | 0.0064571 | 0.98822 | -0.08253 | 0.98811 | -0.083291 | 2.3915
68 | 0.055868 | 0.014016 | -0.055825 | -0.014001 | 4.2868e-05 | 1.5369e-05 | 0.084129 | 0.08413 | 0.08413 | 0.98822 | -0.08253 | 0.98744 | -0.088065 | 10.3864
69 | -0.066415 | -0.016674 | 0.066433 | 0.01668 | 1.7671e-05 | 6.4669e-06 | 0.099773 | 0.099773 | 0.099773 | 0.99061 | -0.065616 | 0.99089 | -0.063701 | 12.3177
70 | 0.001312 | 0.00032689 | -0.0013116 | -0.00032871 | 3.7431e-07 | -1.8246e-06 | 0.001975 | 0.0019757 | 0.0019757 | 0.98811 | -0.083291 | 0.98782 | -0.085364 | 0.73175
71 | 0.055426 | 0.013901 | -0.055387 | -0.013887 | 3.8393e-05 | 1.3752e-05 | 0.083527 | 0.083527 | 0.083527 | 0.98744 | -0.088065 | 0.98673 | -0.093065 | 10.312
72 | -0.068297 | -0.017147 | 0.068484 | 0.017216 | 0.00018744 | 6.8774e-05 | 0.10257 | 0.10257 | 0.10257 | 0.99089 | -0.063701 | 0.99369 | -0.043999 | 12.6633
73 | 0.054914 | 0.013768 | -0.054867 | -0.013752 | 4.6781e-05 | 1.6737e-05 | 0.082814 | 0.082815 | 0.082815 | 0.98673 | -0.093065 | 0.98586 | -0.099219 | 10.224
74 | 0.0065372 | 0.001626 | -0.0065216 | -0.0016232 | 1.5644e-05 | 2.7922e-06 | 0.0099031 | 0.0099042 | 0.0099042 | 0.98183 | -0.1281 | 0.9794 | -0.14565 | 3.6682
75 | -0.02314 | -0.0057798 | 0.023186 | 0.0057908 | 4.6488e-05 | 1.0968e-05 | 0.035063 | 0.03506 | 0.035063 | 0.98183 | -0.1281 | 0.98386 | -0.1135 | 4.3288
76 | 0.0060926 | 0.0015157 | -0.0060911 | -0.0015154 | 1.5628e-06 | 2.3302e-07 | 0.0092526 | 0.0092527 | 0.0092527 | 0.9794 | -0.14565 | 0.97915 | -0.14753 | 3.4269
77 | -0.023712 | -0.0059224 | 0.023718 | 0.0059238 | 5.7108e-06 | 1.3826e-06 | 0.035855 | 0.035855 | 0.035855 | 0.98386 | -0.1135 | 0.98411 | -0.11175 | 4.4265
78 | 0.0058977 | 0.001467 | -0.0058923 | -0.0014662 | 5.4093e-06 | 7.2336e-07 | 0.0089588 | 0.0089593 | 0.0089593 | 0.97915 | -0.14753 | 0.97822 | -0.15426 | 3.3183
79 | -0.02454 | -0.0061299 | 0.024569 | 0.0061372 | 2.9008e-05 | 7.2896e-06 | 0.037098 | 0.037097 | 0.037098 | 0.98411 | -0.11175 | 0.98531 | -0.10316 | 4.58
80 | -0.017529 | -0.0043884 | 0.017541 | 0.0043928 | 1.2242e-05 | 4.3405e-06 | 0.026266 | 0.026266 | 0.026266 | 0.99298 | -0.049051 | 0.99369 | -0.043999 | 9.7282
81 | -0.010613 | -0.0026579 | 0.010615 | 0.0026586 | 2.3618e-06 | 7.164e-07 | 0.015937 | 0.015937 | 0.015937 | 0.99085 | -0.063971 | 0.99108 | -0.062361 | 5.9025
82 | -0.050932 | -0.012783 | 0.050993 | 0.012806 | 6.0603e-05 | 2.3095e-05 | 0.076477 | 0.076477 | 0.076477 | 0.99108 | -0.062361 | 0.99229 | -0.053801 | 28.3248
83 | 0.040317 | 0.010125 | -0.040289 | -0.010114 | 2.8742e-05 | 1.0893e-05 | 0.06054 | 0.06054 | 0.06054 | 0.99108 | -0.062361 | 0.99035 | -0.067494 | 22.4223
84 | -0.052106 | -0.013085 | 0.052109 | 0.013086 | 2.494e-06 | 9.5076e-07 | 0.078146 | 0.078146 | 0.078146 | 0.99229 | -0.053801 | 0.99234 | -0.053457 | 28.9431
85 | 0.03881 | 0.0097431 | -0.038747 | -0.0097193 | 6.2855e-05 | 2.3794e-05 | 0.058319 | 0.058319 | 0.058319 | 0.99035 | -0.067494 | 0.98869 | -0.079173 | 21.5995
86 | 0.0017863 | 0.00044742 | -0.0017862 | -0.00044767 | 1.0846e-07 | -2.5419e-07 | 0.0027163 | 0.0027164 | 0.0027164 | 0.97854 | -0.15136 | 0.97847 | -0.1518 | 1.0061
87 | -0.0024976 | -0.00062567 | 0.0024978 | 0.00062539 | 2.7588e-07 | -2.7901e-07 | 0.0037978 | 0.0037977 | 0.0037978 | 0.97854 | -0.15136 | 0.97865 | -0.15057 | 1.4066
88 | 0.0041056 | 0.0010279 | -0.0041055 | -0.0010279 | 1.0715e-07 | -1.4162e-08 | 0.0062421 | 0.0062421 | 0.0062421 | 0.97865 | -0.15057 | 0.97862 | -0.15075 | 2.3119
89 | 0.011117 | 0.0027863 | -0.011114 | -0.0027855 | 2.7214e-06 | 8.5494e-07 | 0.016903 | 0.016904 | 0.016904 | 0.97865 | -0.15057 | 0.9784 | -0.15233 | 6.2606
90 | -0.017721 | -0.0044396 | 0.01774 | 0.0044465 | 1.9184e-05 | 6.8456e-06 | 0.026943 | 0.026943 | 0.026943 | 0.97865 | -0.15057 | 0.97974 | -0.14275 | 9.979
91 | 0.0041055 | 0.0010279 | -0.0041034 | -0.0010282 | 2.037e-06 | -2.6859e-07 | 0.0062421 | 0.0062424 | 0.0062424 | 0.97862 | -0.15075 | 0.97812 | -0.15434 | 2.312
92 | 0.0078585 | 0.0019695 | -0.0078579 | -0.0019693 | 6.4735e-07 | 1.5778e-07 | 0.011952 | 0.011952 | 0.011952 | 0.9784 | -0.15233 | 0.97832 | -0.15293 | 4.4266
93 | -0.019536 | -0.0048967 | 0.019565 | 0.0049072 | 2.9127e-05 | 1.0534e-05 | 0.029671 | 0.029671 | 0.029671 | 0.97974 | -0.14275 | 0.98125 | -0.132 | 10.9893
94 | 0.0018439 | 0.00046188 | -0.0018438 | -0.00046209 | 1.0085e-07 | -2.1902e-07 | 0.002805 | 0.0028051 | 0.0028051 | 0.97812 | -0.15434 | 0.97807 | -0.15474 | 1.0389
95 | 0.0069393 | 0.0017391 | -0.0069381 | -0.0017389 | 1.2179e-06 | 2.4847e-07 | 0.010555 | 0.010555 | 0.010555 | 0.97832 | -0.15293 | 0.97814 | -0.1542 | 3.9092
96 | -0.019565 | -0.0049072 | 0.019572 | 0.0049097 | 6.8877e-06 | 2.4907e-06 | 0.029671 | 0.029671 | 0.029671 | 0.98125 | -0.132 | 0.9816 | -0.12946 | 10.9893
97 | -0.020203 | -0.0050679 | 0.020209 | 0.0050701 | 6.129e-06 | 2.2249e-06 | 0.030628 | 0.030628 | 0.030628 | 0.9816 | -0.12946 | 0.98191 | -0.12727 | 11.3437
98 | 0.029639 | 0.0074461 | -0.02954 | -0.007409 | 9.9077e-05 | 3.7101e-05 | 0.044768 | 0.044768 | 0.044768 | 0.98531 | -0.10316 | 0.98191 | -0.12727 | 16.5807
99 | -0.054208 | -0.013583 | 0.054238 | 0.013594 | 2.9573e-05 | 1.0563e-05 | 0.081864 | 0.081864 | 0.081864 | 0.98531 | -0.10316 | 0.98586 | -0.099219 | 10.1067
100 | -0.00113 | -0.00028321 | 0.0011301 | 0.0002827 | 8.0505e-08 | -5.0801e-07 | 0.0017263 | 0.0017261 | 0.0017263 | 0.97405 | -0.18412 | 0.97413 | -0.1836 | 0.63937
101 | 0.0008514 | 0.00021314 | -0.00085138 | -0.00021337 | 1.9463e-08 | -2.3766e-07 | 0.0012793 | 0.0012794 | 0.0012794 | 0.99023 | -0.068352 | 0.99021 | -0.068518 | 0.47385
102 | 0.0021877 | 0.00054813 | -0.0021876 | -0.00054827 | 9.7107e-08 | -1.3906e-07 | 0.0033278 | 0.0033278 | 0.0033278 | 0.97823 | -0.15386 | 0.97819 | -0.15418 | 1.2325
103 | -0.00037287 | -9.345e-05 | 0.00037288 | 9.2913e-05 | 8.7431e-09 | -5.3655e-07 | 0.00056904 | 0.00056884 | 0.00056904 | 0.97505 | -0.1773 | 0.97507 | -0.17713 | 0.21075
104 | -0.0012522 | -0.0003133 | 0.0012523 | 0.00031316 | 2.7861e-08 | -1.4183e-07 | 0.0019108 | 0.0019107 | 0.0019108 | 0.97507 | -0.17713 | 0.97509 | -0.17696 | 0.7077
105 | -0.0013845 | -0.00034629 | 0.0013845 | 0.00034624 | 1.2479e-08 | -5.1101e-08 | 0.0021125 | 0.0021125 | 0.0021125 | 0.97509 | -0.17696 | 0.9751 | -0.1769 | 0.7824
106 | -0.0021905 | -0.00054825 | 0.0021906 | 0.00054803 | 1.528e-07 | -2.1467e-07 | 0.0033424 | 0.0033423 | 0.0033424 | 0.9751 | -0.1769 | 0.97517 | -0.17639 | 1.2379
107 | -0.0024528 | -0.00061373 | 0.0024566 | 0.00060969 | 3.8616e-06 | -4.0395e-06 | 0.0037423 | 0.0037403 | 0.0037423 | 0.97517 | -0.17639 | 0.97676 | -0.1649 | 1.386
108 | -0.0024566 | -0.00060969 | 0.0024577 | 0.00060861 | 1.0303e-06 | -1.0817e-06 | 0.0037403 | 0.0037398 | 0.0037403 | 0.97676 | -0.1649 | 0.97718 | -0.16181 | 1.3853
109 | -0.003013 | -0.00074779 | 0.0030134 | 0.00074758 | 3.5447e-07 | -2.0216e-07 | 0.0045855 | 0.0045853 | 0.0045855 | 0.97718 | -0.16181 | 0.9773 | -0.16094 | 1.6983
110 | -0.0031366 | -0.00077846 | 0.0031368 | 0.00077832 | 2.7338e-07 | -1.3586e-07 | 0.0047729 | 0.0047728 | 0.0047729 | 0.9773 | -0.16094 | 0.97739 | -0.1603 | 1.7678
111 | -0.0048038 | -0.0011961 | 0.0048071 | 0.0011961 | 3.3292e-06 | 2.8413e-08 | 0.0073107 | 0.0073102 | 0.0073107 | 0.97739 | -0.1603 | 0.97809 | -0.15523 | 2.7077
112 | -0.0048071 | -0.0011961 | 0.0048077 | 0.0011961 | 6.354e-07 | 5.2019e-09 | 0.0073102 | 0.0073101 | 0.0073102 | 0.97809 | -0.15523 | 0.97822 | -0.15426 | 2.7075
113 | 0.0010846 | 0.00027011 | -0.0010844 | -0.00027112 | 1.439e-07 | -1.0087e-06 | 0.0016492 | 0.0016496 | 0.0016496 | 0.97822 | -0.15426 | 0.97808 | -0.15522 | 0.61095
114 | 0.00078838 | 0.00019693 | -0.00078836 | -0.0001972 | 2.0371e-08 | -2.7705e-07 | 0.0011992 | 0.0011993 | 0.0011993 | 0.97808 | -0.15522 | 0.97806 | -0.15541 | 0.44417
115 | 0.00038578 | 9.6309e-05 | -0.00038577 | -9.6683e-05 | 6.4546e-09 | -3.7445e-07 | 0.00058679 | 0.00058692 | 0.00058692 | 0.97806 | -0.15541 | 0.97804 | -0.15553 | 0.21738

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16243 | 0.040714

## res_load
| p_mw | q_mvar
0 | 0.0064653 | 0.0016204
1 | 0.00172 | 0.00043106
2 | 0.0015007 | 0.00037611
3 | 0.001755 | 0.00043984
4 | 0.0071654 | 0.0017958
5 | 0.00099364 | 0.00024903
6 | 0.0016442 | 0.00041207
7 | 0.0080901 | 0.0020276
8 | 0.00046274 | 0.00011597
9 | 0.00038141 | 9.5592e-05
10 | 0.0018332 | 0.00045943
11 | 0.00037378 | 9.3677e-05
12 | 0.00020521 | 5.1429e-05
13 | 0.0018626 | 0.00046681
14 | 0.0014966 | 0.00037509
15 | 0.0053091 | 0.0013306
16 | 0.0045508 | 0.0011405
17 | 0.00061639 | 0.00015448
18 | 0.0011529 | 0.00028895
19 | 0.0024965 | 0.00062569
20 | 0.0004568 | 0.00011449
21 | 0.0010545 | 0.00026427
22 | 0.0018861 | 0.00047269
23 | 0.003158 | 0.00079146
24 | 0.0048802 | 0.0012231
25 | 0.0013871 | 0.00034765
26 | 0.00079613 | 0.00019953
27 | 0.0010787 | 0.00027034
28 | 0.00083446 | 0.00020913
29 | 0.00069486 | 0.00017415
30 | 0.00088223 | 0.00022111
31 | 0.0013163 | 0.00032989
32 | 0.0011949 | 0.00029948
33 | 0.0011301 | 0.00028323
34 | 0.0030122 | 0.00075493
35 | 0.006672 | 0.0016722
36 | 0.0014382 | 0.00036044
37 | 0.0094398 | 0.0023658
38 | 0.00059861 | 0.00015003
39 | 0.00080933 | 0.00020284
40 | 0.0011064 | 0.00027728
41 | 0.00073466 | 0.00018412
42 | 0.0032995 | 0.00082692
43 | 0.00079892 | 0.00020023
44 | 0.002015 | 0.000505
45 | 0.0029763 | 0.00074594
46 | 0.00039984 | 0.00010021
47 | 0.0018642 | 0.0004672
48 | 0.0013116 | 0.00032871
49 | 0.000473 | 0.00011854
50 | 0.0004289 | 0.00010749
51 | 0.00052533 | 0.00013166
52 | 0.00019338 | 4.8465e-05
53 | 0.00082233 | 0.00020609
54 | 0.00088344 | 0.00022141
55 | 0.0013627 | 0.00034152
56 | 0.0011133 | 0.00027902
57 | 0.0014786 | 0.00037057
58 | 0.0012557 | 0.0003147
59 | 0.0045909 | 0.0011506
60 | 0.00071123 | 0.00017825
61 | 0.0017862 | 0.00044767
62 | 0.0032559 | 0.00081601
63 | 0.0017963 | 0.0004502
64 | 0.0022595 | 0.00056629
65 | 0.00091854 | 0.00023021
66 | 0.0018438 | 0.00046209
67 | 0.00063125 | 0.00015821
68 | 0.00062978 | 0.00015784
69 | 0.00113 | 0.00028321
70 | 0.0020044 | 0.00050234
71 | 0.0069381 | 0.0017389
72 | 0.0023632 | 0.00059228
73 | 0.00047565 | 0.00011921
74 | 0.00085741 | 0.00021489
75 | 0.00069946 | 0.0001753
76 | 0.0021876 | 0.00054827
77 | 0.00089782 | 0.00022502
78 | 0.00037287 | 9.345e-05
79 | 0.00087935 | 0.00022039
80 | 0.00013221 | 3.3134e-05
81 | 0.00080602 | 0.00020201
82 | 0.00026213 | 6.5695e-05
83 | 0.00085138 | 0.00021337
84 | 0.00082575 | 0.00020695
85 | 0.00055534 | 0.00013918
86 | 0.0001232 | 3.0876e-05
87 | 0.0016669 | 0.00041778
88 | 0.00029604 | 7.4195e-05
89 | 0.00040258 | 0.0001009
90 | 0.00038577 | 9.6683e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1