## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1002-7_1_3_node_31 | 0.4 | n |  | TRUE
1 | bus_LV_1002-7_1_3_node_32 | 0.4 | n |  | TRUE
2 | bus_LV_1002-7_1_3_node_33 | 0.4 | n |  | TRUE
3 | bus_LV_1002-7_1_3_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1002-7_1_3_node_35 | 0.4 | n |  | TRUE
5 | bus_LV_1002-7_1_3_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_1002-7_1_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1002-7_1_3_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_1002-7_1_3_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_1002-7_1_3_node_56 | 0.4 | n |  | TRUE
10 | bus_LV_1002-7_1_3_node_54 | 0.4 | n |  | TRUE
11 | bus_LV_1002-7_1_3_node_52 | 0.4 | n |  | TRUE
12 | bus_LV_1002-7_1_3_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_1002-7_1_3_node_51 | 0.4 | n |  | TRUE
14 | bus_LV_1002-7_1_3_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_1002-7_1_3_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_1002-7_1_3_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_1002-7_1_3_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_1002-7_1_3_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_1002-7_1_3_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_1002-7_1_3_node_47 | 0.4 | n |  | TRUE
21 | bus_LV_1002-7_1_3_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1002-7_1_3_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_1002-7_1_3_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_1002-7_1_3_node_53 | 0.4 | n |  | TRUE
25 | bus_LV_1002-7_1_3_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_1002-7_1_3_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_1002-7_1_3_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_1002-7_1_3_node_58 | 0.4 | n |  | TRUE
29 | bus_LV_1002-7_1_3_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_1002-7_1_3_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_1002-7_1_3_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_1002-7_1_3_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_1002-7_1_3_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_1002-7_1_3_node_65 | 0.4 | n |  | TRUE
35 | bus_LV_1002-7_1_3_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_1002-7_1_3_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_1002-7_1_3_node_112 | 0.4 | n |  | TRUE
38 | bus_LV_1002-7_1_3_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_1002-7_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1002-7_1_3_node_70 | 0.4 | n |  | TRUE
41 | bus_MV_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1002-7_1_3_load_31 | 0 | 0.0045134 | 0.0011312 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1002-7_1_3_load_33 | 2 | 0.0021569 | 0.00054058 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1002-7_1_3_load_34 | 3 | 0.0066873 | 0.001676 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1002-7_1_3_load_35 | 4 | 0.0015783 | 0.00039556 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1002-7_1_3_load_36 | 5 | 0.001352 | 0.00033884 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1002-7_1_3_load_56 | 9 | 0.0026092 | 0.00065394 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1002-7_1_3_load_54 | 10 | 0.0006439 | 0.00016138 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1002-7_1_3_load_52 | 11 | 0.00082362 | 0.00020642 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1002-7_1_3_load_51 | 13 | 0.001348 | 0.00033785 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1002-7_1_3_load_40 | 14 | 0.00090781 | 0.00022752 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1002-7_1_3_load_41 | 15 | 0.00086486 | 0.00021675 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1002-7_1_3_load_42 | 16 | 0.00074421 | 0.00018652 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1002-7_1_3_load_44 | 17 | 0.00077202 | 0.00019349 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1002-7_1_3_load_45 | 18 | 0.00081837 | 0.0002051 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1002-7_1_3_load_46 | 19 | 0.0011553 | 0.00028955 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1002-7_1_3_load_47 | 20 | 0.00091357 | 0.00022896 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1002-7_1_3_load_48 | 21 | 0.0012687 | 0.00031796 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1002-7_1_3_load_49 | 22 | 0.00094014 | 0.00023562 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1002-7_1_3_load_50 | 23 | 0.0011342 | 0.00028426 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1002-7_1_3_load_53 | 24 | 0.0011637 | 0.00029165 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1002-7_1_3_load_55 | 25 | 0.0018371 | 0.00046043 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1002-7_1_3_load_57 | 26 | 0.0012001 | 0.00030076 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1002-7_1_3_load_59 | 27 | 0.00021734 | 5.4471e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1002-7_1_3_load_58 | 28 | 0.0001404 | 3.5187e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1002-7_1_3_load_62 | 29 | 8.9562e-05 | 2.2446e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1002-7_1_3_load_60 | 30 | 0.0015023 | 0.00037652 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1002-7_1_3_load_61 | 31 | 0.00029817 | 7.473e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1002-7_1_3_load_66 | 36 | 0.00049972 | 0.00012524 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1002-7_1_3_load_112 | 37 | 9.2739e-05 | 2.3243e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1002-7_1_3_load_67 | 38 | 0.00015103 | 3.7851e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1002-7_1_3_load_70 | 40 | 0.00049178 | 0.00012325 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1002-7_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1002-7_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.060201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1002-7_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.070154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1002-7_1_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.00093077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1002-7_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1002-7_1_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.08467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1002-7_1_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.021208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1002-7_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.074709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1002-7_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.033916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1002-7_1_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.042559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1002-7_1_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.021407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1002-7_1_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.07624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1002-7_1_3_line_12 | NAYY 4x150 SE | 8 | 13 | 0.0042241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1002-7_1_3_line_13 | NAYY 4x150 SE | 9 | 26 | 0.12514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1002-7_1_3_line_14 | NAYY 4x150 SE | 10 | 24 | 0.012857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1002-7_1_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.010575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1002-7_1_3_line_16 | NAYY 4x150 SE | 13 | 23 | 0.031202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1002-7_1_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.0050866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1002-7_1_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.020589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1002-7_1_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.015223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1002-7_1_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.00083831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1002-7_1_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.0256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1002-7_1_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0039439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1002-7_1_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.014795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1002-7_1_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0073575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1002-7_1_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.021019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1002-7_1_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.12986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1002-7_1_3_line_27 | NAYY 4x150 SE | 27 | 29 | 0.14512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1002-7_1_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.16361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1002-7_1_3_line_29 | NAYY 4x150 SE | 29 | 33 | 0.011798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1002-7_1_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0062026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1002-7_1_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.012341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1002-7_1_3_line_32 | NAYY 4x150 SE | 32 | 34 | 0.011054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1002-7_1_3_line_33 | NAYY 4x150 SE | 33 | 35 | 0.020501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1002-7_1_3_line_34 | NAYY 4x150 SE | 34 | 36 | 0.0072004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1002-7_1_3_line_35 | NAYY 4x150 SE | 34 | 37 | 0.36838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1002-7_1_3_line_36 | NAYY 4x150 SE | 35 | 40 | 0.017734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1002-7_1_3_line_37 | NAYY 4x150 SE | 35 | 39 | 0.021019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1002-7_1_3_line_38 | NAYY 4x150 SE | 36 | 38 | 0.015377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1002-7_1_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.011195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1002-7_1_3_trafo_37 | 0.25 MVA 20/0.4 kV | 41 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2648100.7416 | 1204714.8471 | 2648090.8378 | 1204713.8335 | 2648086.4321 | 1204713.9759 | 2648082.5352 | 1204715.1786 | 2648080.7133 | 1204716.6269
1 | 2648072.9778 | 1204772.2457 | 2648079.6078 | 1204750.9312 | 2648080.0346 | 1204747.9885 | 2648080.1942 | 1204745.177 | 2648079.8298 | 1204742.2502 | 2648078.5895 | 1204739.4608 | 2648075.5774 | 1204733.7444 | 2648074.4391 | 1204730.5667 | 2648073.9626 | 1204727.3944 | 2648074.6563 | 1204724.376 | 2648076.4329 | 1204721.0217 | 2648079.5723 | 1204717.5339 | 2648080.7133 | 1204716.6269
2 | 2648100.7416 | 1204714.8471 | 2648101.2916 | 1204704.1787 | 2648102.2217 | 1204696.3706 | 2648103.7071 | 1204689.5008 | 2648106.2182 | 1204681.85 | 2648110.2833 | 1204671.1098 | 2648115.7649 | 1204657.3349 | 2648120.3874 | 1204648.2224
3 | 2648120.3874 | 1204648.2224 | 2648120.9101 | 1204647.4523
4 | 2648120.9101 | 1204647.4523 | 2648123.9672 | 1204642.9482 | 2648127.6594 | 1204638.8311 | 2648132.0419 | 1204634.8417
5 | 2648165.2692 | 1204568.0823 | 2648167.5687 | 1204569.7128 | 2648169.2277 | 1204572.4611 | 2648171.1253 | 1204576.7678 | 2648172.3228 | 1204581.091 | 2648172.3554 | 1204585.5383 | 2648171.5373 | 1204589.812 | 2648169.5937 | 1204594.9993 | 2648167.3911 | 1204599.284 | 2648162.9281 | 1204605.585 | 2648156.3742 | 1204612.6918 | 2648132.0419 | 1204634.8417
6 | 2648165.2692 | 1204568.0823 | 2648172.7817 | 1204562.862 | 2648174.9743 | 1204560.7674 | 2648175.8452 | 1204559.3625 | 2648179.3666 | 1204552.8538
7 | 2648110.7673 | 1204539.2378 | 2648110.0512 | 1204543.1454 | 2648106.8557 | 1204552.6362 | 2648123.0148 | 1204559.1034 | 2648136.4488 | 1204562.936 | 2648147.8423 | 1204565.0845 | 2648161.1042 | 1204566.6812 | 2648165.2692 | 1204568.0823
8 | 2648179.3666 | 1204552.8538 | 2648184.371 | 1204551.1153 | 2648199.9776 | 1204548.7287 | 2648208.2885 | 1204546.3833 | 2648211.9851 | 1204544.3999
9 | 2648179.3666 | 1204552.8538 | 2648182.8931 | 1204541.9537 | 2648184.5399 | 1204533.9513 | 2648184.7323 | 1204529.906 | 2648184.1025 | 1204525.932 | 2648182.698 | 1204522.7522 | 2648180.7075 | 1204520.546 | 2648174.6346 | 1204516.1056 | 2648173.9645 | 1204515.5217
10 | 2648110.7673 | 1204539.2378 | 2648103.6086 | 1204537.3791 | 2648090.6117 | 1204532.1447
11 | 2648045.8794 | 1204544.6189 | 2648058.2387 | 1204543.0395 | 2648070.8326 | 1204543.5189 | 2648083.5246 | 1204545.9779 | 2648106.8557 | 1204552.6362 | 2648110.0512 | 1204543.1454 | 2648110.7673 | 1204539.2378
12 | 2648110.7673 | 1204539.2378 | 2648111.5463 | 1204535.0861
13 | 2648211.9851 | 1204544.3999 | 2648306.2823 | 1204462.1371
14 | 2648166.6092 | 1204505.4492 | 2648166.9383 | 1204507.3274 | 2648169.2258 | 1204511.3926 | 2648173.9645 | 1204515.5217
15 | 2648045.8794 | 1204544.6189 | 2648045.1098 | 1204534.0721
16 | 2648111.5463 | 1204535.0861 | 2648110.4816 | 1204528.4292 | 2648108.4069 | 1204522.498 | 2648104.7713 | 1204516.7543 | 2648100.1402 | 1204511.8031 | 2648096.0048 | 1204509.7891
17 | 2648044.7395 | 1204528.999 | 2648045.1098 | 1204534.0721
18 | 2648044.7395 | 1204528.999 | 2648044.2006 | 1204521.6143 | 2648043.5464 | 1204516.8841 | 2648042.2695 | 1204512.9605 | 2648039.0515 | 1204510.133
19 | 2648042.3047 | 1204473.4589 | 2648051.7201 | 1204485.4207
20 | 2648042.3047 | 1204473.4589 | 2648041.7862 | 1204472.8002
21 | 2648071.4246 | 1204501.1 | 2648066.7635 | 1204498.9827 | 2648061.6087 | 1204495.7728 | 2648056.9072 | 1204492.0106 | 2648051.7201 | 1204485.4207
22 | 2648071.4246 | 1204501.1 | 2648075.0154 | 1204502.7311
23 | 2648089.0305 | 1204507.4541 | 2648075.9576 | 1204503.1591 | 2648075.0154 | 1204502.7311
24 | 2648089.0305 | 1204507.4541 | 2648095.7301 | 1204509.6552 | 2648096.0048 | 1204509.7891
25 | 2648174.5586 | 1204486.8548 | 2648171.2451 | 1204490.2189 | 2648168.6969 | 1204494.9011 | 2648166.8008 | 1204499.8553 | 2648166.2692 | 1204503.5087 | 2648166.6092 | 1204505.4492
26 | 2648306.2823 | 1204462.1371 | 2648422.1146 | 1204520.8402
27 | 2648548.1951 | 1204592.6944 | 2648422.1146 | 1204520.8402
28 | 2648422.1146 | 1204520.8402 | 2648468.8332 | 1204364.0416
29 | 2648556.3726 | 1204584.1897 | 2648548.1951 | 1204592.6944
30 | 2648536.2983 | 1204612.1205 | 2648536.2983 | 1204612.1205 | 2648537.7384 | 1204615.5786 | 2648539.2455 | 1204617.5185
31 | 2648548.1364 | 1204626.0024 | 2648541.337 | 1204620.2105 | 2648539.2455 | 1204617.5185
32 | 2648548.1364 | 1204626.0024 | 2648554.3621 | 1204629.3772 | 2648558.1476 | 1204630.6642
33 | 2648556.3726 | 1204584.1897 | 2648558.796 | 1204586.4662 | 2648566.4876 | 1204591.0536 | 2648570.1207 | 1204592.3839 | 2648574.4426 | 1204593.1973
34 | 2648558.1476 | 1204630.6642 | 2648560.4766 | 1204630.5164 | 2648564.2077 | 1204629.1348 | 2648564.9602 | 1204628.6632
35 | 2648558.1476 | 1204630.6642 | 2648444.8291 | 1204981.1814
36 | 2648574.4426 | 1204593.1973 | 2648579.1212 | 1204592.2459 | 2648582.4807 | 1204590.7279 | 2648585.9351 | 1204587.8432 | 2648589.0303 | 1204584.2107
37 | 2648574.4426 | 1204593.1973 | 2648578.9464 | 1204601.5832 | 2648584.6159 | 1204611.6017
38 | 2648564.9602 | 1204628.6632 | 2648568.7954 | 1204626.2593 | 2648577.5976 | 1204619.9143
39 | 2648584.6159 | 1204611.6017 | 2648583.4452 | 1204614.3048 | 2648581.8958 | 1204616.8159 | 2648577.5976 | 1204619.9143

## bus_geodata
| x | y | coords
0 | 2648080.7133 | 1204716.6269
1 | 2648100.7416 | 1204714.8471
2 | 2648072.9778 | 1204772.2457
3 | 2648120.3874 | 1204648.2224
4 | 2648120.9101 | 1204647.4523
5 | 2648132.0419 | 1204634.8417
6 | 2648165.2692 | 1204568.0823
7 | 2648179.3666 | 1204552.8538
8 | 2648110.7673 | 1204539.2378
9 | 2648211.9851 | 1204544.3999
10 | 2648173.9645 | 1204515.5217
11 | 2648090.6117 | 1204532.1447
12 | 2648045.8794 | 1204544.6189
13 | 2648111.5463 | 1204535.0861
14 | 2648044.7395 | 1204528.999
15 | 2648045.1098 | 1204534.0721
16 | 2648039.0515 | 1204510.133
17 | 2648042.3047 | 1204473.4589
18 | 2648051.7201 | 1204485.4207
19 | 2648041.7862 | 1204472.8002
20 | 2648071.4246 | 1204501.1
21 | 2648075.0154 | 1204502.7311
22 | 2648089.0305 | 1204507.4541
23 | 2648096.0048 | 1204509.7891
24 | 2648166.6092 | 1204505.4492
25 | 2648174.5586 | 1204486.8548
26 | 2648306.2823 | 1204462.1371
27 | 2648422.1146 | 1204520.8402
28 | 2648468.8332 | 1204364.0416
29 | 2648548.1951 | 1204592.6944
30 | 2648536.2983 | 1204612.1205
31 | 2648539.2455 | 1204617.5185
32 | 2648548.1364 | 1204626.0024
33 | 2648556.3726 | 1204584.1897
34 | 2648558.1476 | 1204630.6642
35 | 2648574.4426 | 1204593.1973
36 | 2648564.9602 | 1204628.6632
37 | 2648444.8291 | 1204981.1814
38 | 2648577.5976 | 1204619.9143
39 | 2648584.6159 | 1204611.6017
40 | 2648589.0303 | 1204584.2107
41 | 2648165.2692 | 1204568.0823

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99678 | -0.022562 | 0.0045134 | 0.0011312
1 | 0.99698 | -0.021169 | 0 | 0
2 | 0.9966 | -0.023869 | 0.0021569 | 0.00054058
3 | 0.99765 | -0.016466 | 0.0066873 | 0.001676
4 | 0.99767 | -0.016341 | 0.0015783 | 0.00039556
5 | 0.99803 | -0.013808 | 0.001352 | 0.00033884
6 | 1 | 0 | -0.039793 | -0.0097601
7 | 0.99967 | -0.0023402 | 0 | 0
8 | 0.99875 | -0.0087478 | 0 | 0
9 | 0.99932 | -0.004847 | 0.0026092 | 0.00065394
10 | 0.99945 | -0.003892 | 0.0006439 | 0.00016138
11 | 0.99873 | -0.0089244 | 0.00082362 | 0.00020642
12 | 0.99848 | -0.010674 | 0 | 0
13 | 0.9987 | -0.0091011 | 0.001348 | 0.00033785
14 | 0.99843 | -0.011025 | 0.00090781 | 0.00022752
15 | 0.99844 | -0.01094 | 0.00086486 | 0.00021675
16 | 0.99841 | -0.011178 | 0.00074421 | 0.00018652
17 | 0.99806 | -0.013598 | 0.00077202 | 0.00019349
18 | 0.9981 | -0.013304 | 0.00081837 | 0.0002051
19 | 0.99806 | -0.013608 | 0.0011553 | 0.00028955
20 | 0.9982 | -0.012599 | 0.00091357 | 0.00022896
21 | 0.99823 | -0.012454 | 0.0012687 | 0.00031796
22 | 0.99833 | -0.011723 | 0.00094014 | 0.00023562
23 | 0.99839 | -0.011291 | 0.0011342 | 0.00028426
24 | 0.99939 | -0.0042779 | 0.0011637 | 0.00029165
25 | 0.99934 | -0.004664 | 0.0018371 | 0.00046043
26 | 0.99848 | -0.010831 | 0.0012001 | 0.00030076
27 | 0.99783 | -0.015473 | 0.00021734 | 5.4471e-05
28 | 0.9978 | -0.015716 | 0.0001404 | 3.5187e-05
29 | 0.99719 | -0.020103 | 8.9562e-05 | 2.2446e-05
30 | 0.99678 | -0.022972 | 0.0015023 | 0.00037652
31 | 0.9968 | -0.022879 | 0.00029817 | 7.473e-05
32 | 0.99683 | -0.022655 | 0 | 0
33 | 0.99713 | -0.020469 | 0 | 0
34 | 0.99686 | -0.022455 | 0 | 0
35 | 0.99705 | -0.021103 | 0 | 0
36 | 0.99688 | -0.022315 | 0.00049972 | 0.00012524
37 | 0.99681 | -0.022865 | 9.2739e-05 | 2.3243e-05
38 | 0.99693 | -0.02194 | 0.00015103 | 3.7851e-05
39 | 0.99697 | -0.021649 | 0 | 0
40 | 0.99703 | -0.021191 | 0.00049178 | 0.00012325
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0066708 | -0.0016711 | 0.0066721 | 0.0016713 | 1.2851e-06 | 2.235e-07 | 0.009958 | 0.0099579 | 0.009958 | 0.99678 | -0.022562 | 0.99698 | -0.021169 | 3.6881
1 | 0.0021573 | 0.00053995 | -0.0021569 | -0.00054058 | 3.8959e-07 | -6.3474e-07 | 0.0032203 | 0.0032205 | 0.0032205 | 0.99678 | -0.022562 | 0.9966 | -0.023869 | 1.1928
2 | -0.0066721 | -0.0016713 | 0.0066764 | 0.0016721 | 4.3407e-06 | 7.5406e-07 | 0.0099579 | 0.0099576 | 0.0099579 | 0.99698 | -0.021169 | 0.99765 | -0.016466 | 3.6881
3 | -0.013364 | -0.0033481 | 0.013364 | 0.0033482 | 2.3074e-07 | 7.6591e-08 | 0.019932 | 0.019932 | 0.019932 | 0.99765 | -0.016466 | 0.99767 | -0.016341 | 7.3821
4 | -0.014942 | -0.0037437 | 0.014947 | 0.0037455 | 5.2376e-06 | 1.7937e-06 | 0.022286 | 0.022286 | 0.022286 | 0.99767 | -0.016341 | 0.99803 | -0.013808 | 8.254
5 | -0.016299 | -0.0040844 | 0.016331 | 0.0040952 | 3.1201e-05 | 1.0892e-05 | 0.024301 | 0.024301 | 0.024301 | 0.99803 | -0.013808 | 1 | 0 | 9.0005
6 | 0.010953 | 0.0027316 | -0.01095 | -0.0027305 | 3.5134e-06 | 1.0732e-06 | 0.016294 | 0.016294 | 0.016294 | 1 | 0 | 0.99967 | -0.0023402 | 6.0347
7 | 0.01171 | 0.0029331 | -0.011695 | -0.0029287 | 1.4153e-05 | 4.4644e-06 | 0.017424 | 0.017424 | 0.017424 | 1 | 0 | 0.99875 | -0.0087478 | 6.4533
8 | 0.0073038 | 0.0018177 | -0.0073013 | -0.0018172 | 2.4995e-06 | 5.1682e-07 | 0.010867 | 0.010867 | 0.010867 | 0.99967 | -0.0023402 | 0.99932 | -0.004847 | 4.025
9 | 0.0036458 | 0.00091285 | -0.003645 | -0.00091311 | 7.8204e-07 | -2.5707e-07 | 0.0054265 | 0.0054267 | 0.0054267 | 0.99967 | -0.0023402 | 0.99945 | -0.003892 | 2.0099
10 | 0.00082364 | 0.00020615 | -0.00082362 | -0.00020642 | 2.0113e-08 | -2.7241e-07 | 0.001227 | 0.0012271 | 0.0012271 | 0.99875 | -0.0087478 | 0.99873 | -0.0089244 | 0.45449
11 | 0.0025177 | 0.00062963 | -0.002517 | -0.00063037 | 6.6927e-07 | -7.4004e-07 | 0.0037505 | 0.0037509 | 0.0037509 | 0.99875 | -0.0087478 | 0.99848 | -0.010674 | 1.3892
12 | 0.0083542 | 0.0020929 | -0.0083538 | -0.0020928 | 4.0832e-07 | 1.0177e-07 | 0.012446 | 0.012446 | 0.012446 | 0.99875 | -0.0087478 | 0.9987 | -0.0091011 | 4.6098
13 | 0.0046921 | 0.0011632 | -0.0046883 | -0.0011634 | 3.8071e-06 | -1.7382e-07 | 0.0069822 | 0.0069828 | 0.0069828 | 0.99932 | -0.004847 | 0.99848 | -0.010831 | 2.5862
14 | 0.0030011 | 0.00075174 | -0.0030009 | -0.00075184 | 1.6016e-07 | -1.0688e-07 | 0.004468 | 0.0044681 | 0.0044681 | 0.99945 | -0.003892 | 0.99939 | -0.0042779 | 1.6548
15 | 0.002517 | 0.00063037 | -0.0025169 | -0.00063047 | 9.2839e-08 | -1.026e-07 | 0.0037509 | 0.0037509 | 0.0037509 | 0.99848 | -0.010674 | 0.99844 | -0.01094 | 1.3892
16 | 0.0070057 | 0.001755 | -0.0070036 | -0.0017545 | 2.1213e-06 | 4.0771e-07 | 0.010438 | 0.010438 | 0.010438 | 0.9987 | -0.0091011 | 0.99839 | -0.011291 | 3.8659
17 | -0.001652 | -0.00041377 | 0.0016521 | 0.00041371 | 1.924e-08 | -5.9124e-08 | 0.002462 | 0.002462 | 0.002462 | 0.99843 | -0.011025 | 0.99844 | -0.01094 | 0.91186
18 | 0.00074423 | 0.00018625 | -0.00074421 | -0.00018652 | 1.5805e-08 | -2.6319e-07 | 0.0011091 | 0.0011092 | 0.0011092 | 0.99843 | -0.011025 | 0.99841 | -0.011178 | 0.4108
19 | -0.0019273 | -0.00048303 | 0.0019274 | 0.00048286 | 7.8431e-08 | -1.6878e-07 | 0.0028735 | 0.0028734 | 0.0028735 | 0.99806 | -0.013598 | 0.9981 | -0.013304 | 1.0643
20 | 0.0011553 | 0.00028954 | -0.0011553 | -0.00028955 | 1.5519e-09 | -1.0358e-08 | 0.0017225 | 0.0017225 | 0.0017225 | 0.99806 | -0.013598 | 0.99806 | -0.013608 | 0.63795
21 | -0.0027458 | -0.00068796 | 0.0027461 | 0.00068773 | 2.6767e-07 | -2.3167e-07 | 0.0040935 | 0.0040934 | 0.0040935 | 0.9981 | -0.013304 | 0.9982 | -0.012599 | 1.5161
22 | -0.0036596 | -0.00091669 | 0.0036597 | 0.00091667 | 7.3238e-08 | -2.3389e-08 | 0.0054552 | 0.0054552 | 0.0054552 | 0.9982 | -0.012599 | 0.99823 | -0.012454 | 2.0204
23 | -0.0049284 | -0.0012346 | 0.0049289 | 0.0012346 | 4.9825e-07 | -1.7991e-09 | 0.0073464 | 0.0073463 | 0.0073464 | 0.99823 | -0.012454 | 0.99833 | -0.011723 | 2.7209
24 | -0.005869 | -0.0014703 | 0.0058694 | 0.0014703 | 3.5131e-07 | 3.8911e-08 | 0.0087476 | 0.0087476 | 0.0087476 | 0.99833 | -0.011723 | 0.99839 | -0.011291 | 3.2399
25 | 0.0018372 | 0.00046019 | -0.0018371 | -0.00046043 | 9.8141e-08 | -2.3766e-07 | 0.0027354 | 0.0027355 | 0.0027355 | 0.99939 | -0.0042779 | 0.99934 | -0.004664 | 1.0131
26 | 0.0034882 | 0.00086264 | -0.003486 | -0.00086349 | 2.1866e-06 | -8.5637e-07 | 0.0051944 | 0.005195 | 0.005195 | 0.99848 | -0.010831 | 0.99783 | -0.015473 | 1.9241
27 | 0.0031283 | 0.00077597 | -0.0031263 | -0.00077711 | 1.9686e-06 | -1.1372e-06 | 0.0046622 | 0.0046629 | 0.0046629 | 0.99783 | -0.015473 | 0.99719 | -0.020103 | 1.727
28 | 0.0001404 | 3.3051e-05 | -0.0001404 | -3.5187e-05 | 4.4596e-09 | -2.1354e-06 | 0.00020864 | 0.00020937 | 0.00020937 | 0.99783 | -0.015473 | 0.9978 | -0.015716 | 0.077546
29 | 0.0030368 | 0.00075466 | -0.0030366 | -0.00075476 | 1.5103e-07 | -9.5819e-08 | 0.0045293 | 0.0045293 | 0.0045293 | 0.99719 | -0.020103 | 0.99713 | -0.020469 | 1.6775
30 | -0.0015023 | -0.00037652 | 0.0015023 | 0.00037644 | 1.9467e-08 | -7.3365e-08 | 0.0022427 | 0.0022427 | 0.0022427 | 0.99678 | -0.022972 | 0.9968 | -0.022879 | 0.83063
31 | -0.0018005 | -0.00045117 | 0.0018006 | 0.00045103 | 5.563e-08 | -1.3948e-07 | 0.0026878 | 0.0026877 | 0.0026878 | 0.9968 | -0.022879 | 0.99683 | -0.022655 | 0.99548
32 | -0.0018006 | -0.00045103 | 0.0018006 | 0.00045091 | 4.9827e-08 | -1.2494e-07 | 0.0026877 | 0.0026877 | 0.0026877 | 0.99683 | -0.022655 | 0.99686 | -0.022455 | 0.99545
33 | 0.0030366 | 0.00075476 | -0.0030363 | -0.00075493 | 2.6244e-07 | -1.6646e-07 | 0.0045293 | 0.0045294 | 0.0045294 | 0.99713 | -0.020469 | 0.99705 | -0.021103 | 1.6776
34 | -0.0018934 | -0.00046935 | 0.0018934 | 0.00046927 | 3.5843e-08 | -8.0088e-08 | 0.0028244 | 0.0028244 | 0.0028244 | 0.99686 | -0.022455 | 0.99688 | -0.022315 | 1.0461
35 | 9.2744e-05 | 1.8442e-05 | -9.2739e-05 | -2.3243e-05 | 4.3545e-09 | -4.8006e-06 | 0.00013692 | 0.00013844 | 0.00013844 | 0.99686 | -0.022455 | 0.99681 | -0.022865 | 0.051274
36 | 0.00049178 | 0.00012302 | -0.00049178 | -0.00012325 | 5.9603e-09 | -2.2899e-07 | 0.00073387 | 0.00073395 | 0.00073395 | 0.99705 | -0.021103 | 0.99703 | -0.021191 | 0.27183
37 | 0.0025446 | 0.0006319 | -0.0025444 | -0.0006321 | 1.8895e-07 | -2.0143e-07 | 0.0037955 | 0.0037956 | 0.0037956 | 0.99705 | -0.021103 | 0.99697 | -0.021649 | 1.4058
38 | -0.0023931 | -0.00059451 | 0.0023932 | 0.00059436 | 1.2231e-07 | -1.5345e-07 | 0.0035703 | 0.0035703 | 0.0035703 | 0.99688 | -0.022315 | 0.99693 | -0.02194 | 1.3223
39 | -0.0025443 | -0.00063221 | 0.0025444 | 0.0006321 | 1.0064e-07 | -1.0727e-07 | 0.0037957 | 0.0037956 | 0.0037957 | 0.99693 | -0.02194 | 0.99697 | -0.021649 | 1.4058

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.039793 | 0.0097601

## res_load
| p_mw | q_mvar
0 | 0.0045134 | 0.0011312
1 | 0.0021569 | 0.00054058
2 | 0.0066873 | 0.001676
3 | 0.0015783 | 0.00039556
4 | 0.001352 | 0.00033884
5 | 0.0026092 | 0.00065394
6 | 0.0006439 | 0.00016138
7 | 0.00082362 | 0.00020642
8 | 0.001348 | 0.00033785
9 | 0.00090781 | 0.00022752
10 | 0.00086486 | 0.00021675
11 | 0.00074421 | 0.00018652
12 | 0.00077202 | 0.00019349
13 | 0.00081837 | 0.0002051
14 | 0.0011553 | 0.00028955
15 | 0.00091357 | 0.00022896
16 | 0.0012687 | 0.00031796
17 | 0.00094014 | 0.00023562
18 | 0.0011342 | 0.00028426
19 | 0.0011637 | 0.00029165
20 | 0.0018371 | 0.00046043
21 | 0.0012001 | 0.00030076
22 | 0.00021734 | 5.4471e-05
23 | 0.0001404 | 3.5187e-05
24 | 8.9562e-05 | 2.2446e-05
25 | 0.0015023 | 0.00037652
26 | 0.00029817 | 7.473e-05
27 | 0.00049972 | 0.00012524
28 | 9.2739e-05 | 2.3243e-05
29 | 0.00015103 | 3.7851e-05
30 | 0.00049178 | 0.00012325

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1