## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1004-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1004-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1004-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1004-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1004-12_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1004-12_0_3_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_1004-12_0_3_node_49 | 0.4 | n |  | TRUE
7 | bus_LV_1004-12_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1004-12_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1004-12_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1004-12_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1004-12_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1004-12_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1004-12_0_3_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1004-12_0_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1004-12_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1004-12_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1004-12_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1004-12_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1004-12_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1004-12_0_3_node_54 | 0.4 | n |  | TRUE
21 | bus_LV_1004-12_0_3_node_81 | 0.4 | n |  | TRUE
22 | bus_LV_1004-12_0_3_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_1004-12_0_3_node_79 | 0.4 | n |  | TRUE
24 | bus_LV_1004-12_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1004-12_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1004-12_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1004-12_0_3_node_86 | 0.4 | n |  | TRUE
28 | bus_LV_1004-12_0_3_node_84 | 0.4 | n |  | TRUE
29 | bus_LV_1004-12_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1004-12_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1004-12_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1004-12_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_1004-12_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1004-12_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1004-12_0_3_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_1004-12_0_3_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1004-12_0_3_node_62 | 0.4 | n |  | TRUE
38 | bus_LV_1004-12_0_3_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_1004-12_0_3_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_1004-12_0_3_node_114 | 0.4 | n |  | TRUE
41 | bus_LV_1004-12_0_3_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_1004-12_0_3_node_115 | 0.4 | n |  | TRUE
43 | bus_LV_1004-12_0_3_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_1004-12_0_3_node_106 | 0.4 | n |  | TRUE
45 | bus_LV_1004-12_0_3_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_1004-12_0_3_node_119 | 0.4 | n |  | TRUE
47 | bus_LV_1004-12_0_3_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_1004-12_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1004-12_0_3_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_1004-12_0_3_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_1004-12_0_3_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_1004-12_0_3_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_1004-12_0_3_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_1004-12_0_3_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_1004-12_0_3_node_107 | 0.4 | n |  | TRUE
56 | bus_LV_1004-12_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1004-12_0_3_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_1004-12_0_3_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_1004-12_0_3_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_1004-12_0_3_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_1004-12_0_3_node_113 | 0.4 | n |  | TRUE
62 | bus_LV_1004-12_0_3_node_95 | 0.4 | n |  | TRUE
63 | bus_LV_1004-12_0_3_node_111 | 0.4 | n |  | TRUE
64 | bus_LV_1004-12_0_3_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1004-12_0_3_node_74 | 0.4 | n |  | TRUE
66 | bus_LV_1004-12_0_3_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_1004-12_0_3_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1004-12_0_3_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1004-12_0_3_node_102 | 0.4 | n |  | TRUE
70 | bus_LV_1004-12_0_3_node_76 | 0.4 | n |  | TRUE
71 | bus_LV_1004-12_0_3_node_108 | 0.4 | n |  | TRUE
72 | bus_LV_1004-12_0_3_node_75 | 0.4 | n |  | TRUE
73 | bus_LV_1004-12_0_3_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1004-12_0_3_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_1004-12_0_3_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1004-12_0_3_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_1004-12_0_3_node_96 | 0.4 | n |  | TRUE
78 | bus_LV_1004-12_0_3_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_1004-12_0_3_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_1004-12_0_3_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_1004-12_0_3_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_1004-12_0_3_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_1004-12_0_3_node_67 | 0.4 | n |  | TRUE
84 | bus_LV_1004-12_0_3_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_1004-12_0_3_node_109 | 0.4 | n |  | TRUE
86 | bus_LV_1004-12_0_3_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_1004-12_0_3_node_100 | 0.4 | n |  | TRUE
88 | bus_LV_1004-12_0_3_node_112 | 0.4 | n |  | TRUE
89 | bus_LV_1004-12_0_3_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_1004-12_0_3_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_1004-12_0_3_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_1004-12_0_3_node_110 | 0.4 | n |  | TRUE
93 | bus_LV_1004-12_0_3_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_1004-12_0_3_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_1004-12_0_3_node_71 | 0.4 | n |  | TRUE
96 | bus_LV_1004-12_0_3_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_1004-12_0_3_node_105 | 0.4 | n |  | TRUE
98 | bus_LV_1004-12_0_3_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1004-12_0_3_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_1004-12_0_3_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_1004-12_0_3_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1004-12_0_3_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_1004-12_0_3_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_1004-12_0_3_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_1004-12_0_3_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_1004-12_0_3_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_1004-12_0_3_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_1004-12_0_3_node_89 | 0.4 | n |  | TRUE
109 | bus_LV_1004-12_0_3_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_1004-12_0_3_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_1004-12_0_3_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_1004-12_0_3_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_1004-12_0_3_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_1004-12_0_3_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_1004-12_0_3_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_1004-12_0_3_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_1004-12_0_3_node_117 | 0.4 | n |  | TRUE
118 | bus_MV_82_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1004-12_0_3_load_0 | 0 | 0.00052306 | 0.00013109 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1004-12_0_3_load_1 | 1 | 0.00043607 | 0.00010929 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1004-12_0_3_load_3 | 3 | 0.00068336 | 0.00017127 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1004-12_0_3_load_4 | 4 | 0.00097174 | 0.00024354 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1004-12_0_3_load_49 | 6 | 0.0018686 | 0.00046831 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1004-12_0_3_load_5 | 8 | 0.0019601 | 0.00049124 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1004-12_0_3_load_6 | 9 | 0.0018017 | 0.00045154 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1004-12_0_3_load_7 | 10 | 0.0019239 | 0.00048217 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1004-12_0_3_load_8 | 11 | 0.001294 | 0.00032432 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1004-12_0_3_load_9 | 12 | 0.0019525 | 0.00048935 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1004-12_0_3_load_19 | 13 | 0.0010502 | 0.00026321 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1004-12_0_3_load_17 | 14 | 0.0046468 | 0.0011646 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1004-12_0_3_load_10 | 15 | 0.0020271 | 0.00050803 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1004-12_0_3_load_11 | 16 | 0.0014338 | 0.00035935 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1004-12_0_3_load_12 | 17 | 0.0023076 | 0.00057834 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1004-12_0_3_load_13 | 18 | 0.0016056 | 0.00040241 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1004-12_0_3_load_14 | 19 | 0.0018662 | 0.00046771 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1004-12_0_3_load_54 | 20 | 0.0014259 | 0.00035737 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1004-12_0_3_load_81 | 21 | 0.0011964 | 0.00029984 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1004-12_0_3_load_55 | 22 | 0.0016229 | 0.00040675 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1004-12_0_3_load_79 | 23 | 0.0013059 | 0.00032728 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1004-12_0_3_load_15 | 24 | 0.0031496 | 0.00078936 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1004-12_0_3_load_16 | 25 | 0.0046762 | 0.001172 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1004-12_0_3_load_20 | 26 | 0.0018373 | 0.00046046 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1004-12_0_3_load_86 | 27 | 0.00060449 | 0.0001515 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1004-12_0_3_load_84 | 28 | 0.0024491 | 0.00061381 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1004-12_0_3_load_21 | 29 | 0.00091729 | 0.00022989 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1004-12_0_3_load_24 | 31 | 0.00092119 | 0.00023087 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1004-12_0_3_load_25 | 32 | 0.0012376 | 0.00031016 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1004-12_0_3_load_26 | 33 | 0.0014754 | 0.00036977 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1004-12_0_3_load_27 | 34 | 0.0030752 | 0.00077072 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1004-12_0_3_load_56 | 35 | 0.002769 | 0.00069397 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1004-12_0_3_load_61 | 38 | 0.001108 | 0.00027769 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1004-12_0_3_load_52 | 39 | 0.0017384 | 0.00043569 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1004-12_0_3_load_114 | 40 | 0.002471 | 0.00061929 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1004-12_0_3_load_50 | 41 | 0.0023622 | 0.00059201 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1004-12_0_3_load_115 | 42 | 0.0027142 | 0.00068024 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1004-12_0_3_load_106 | 44 | 0.0013376 | 0.00033525 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1004-12_0_3_load_39 | 45 | 0.00081589 | 0.00020448 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1004-12_0_3_load_119 | 46 | 0.0021664 | 0.00054295 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1004-12_0_3_load_31 | 48 | 0.0010067 | 0.00025229 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1004-12_0_3_load_32 | 49 | 0.0014177 | 0.00035532 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1004-12_0_3_load_33 | 50 | 0.0014874 | 0.00037277 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1004-12_0_3_load_34 | 51 | 0.0012821 | 0.00032131 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1004-12_0_3_load_35 | 52 | 0.0014362 | 0.00035994 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1004-12_0_3_load_42 | 53 | 0.0013188 | 0.00033052 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1004-12_0_3_load_46 | 54 | 0.0012234 | 0.0003066 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1004-12_0_3_load_107 | 55 | 0.0018302 | 0.00045869 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1004-12_0_3_load_44 | 56 | 0.0022227 | 0.00055705 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1004-12_0_3_load_36 | 57 | 0.00085544 | 0.00021439 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1004-12_0_3_load_40 | 59 | 0.0017729 | 0.00044434 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1004-12_0_3_load_41 | 60 | 0.00081863 | 0.00020517 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1004-12_0_3_load_113 | 61 | 0.0012482 | 0.00031282 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1004-12_0_3_load_95 | 62 | 0.00091883 | 0.00023028 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1004-12_0_3_load_111 | 63 | 0.0039856 | 0.00099888 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1004-12_0_3_load_60 | 64 | 0.001024 | 0.00025664 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1004-12_0_3_load_74 | 65 | 0.00097599 | 0.0002446 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1004-12_0_3_load_43 | 66 | 0.0021211 | 0.0005316 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1004-12_0_3_load_45 | 67 | 0.0013849 | 0.00034709 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1004-12_0_3_load_102 | 69 | 0.0014524 | 0.000364 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1004-12_0_3_load_76 | 70 | 0.0014779 | 0.00037039 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1004-12_0_3_load_108 | 71 | 0.0014784 | 0.00037052 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1004-12_0_3_load_75 | 72 | 0.0014706 | 0.00036856 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1004-12_0_3_load_51 | 73 | 0.0013652 | 0.00034216 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1004-12_0_3_load_53 | 74 | 0.0020703 | 0.00051888 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1004-12_0_3_load_57 | 75 | 0.002855 | 0.00071553 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1004-12_0_3_load_96 | 77 | 0.0020393 | 0.0005111 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1004-12_0_3_load_59 | 78 | 0.0011168 | 0.00027989 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1004-12_0_3_load_63 | 79 | 0.0012478 | 0.00031272 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1004-12_0_3_load_64 | 80 | 0.0010355 | 0.00025952 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1004-12_0_3_load_67 | 83 | 0.0020612 | 0.00051659 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1004-12_0_3_load_68 | 84 | 0.0018361 | 0.00046017 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1004-12_0_3_load_109 | 85 | 0.0023275 | 0.00058333 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1004-12_0_3_load_100 | 87 | 0.0017422 | 0.00043665 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1004-12_0_3_load_112 | 88 | 0.0014507 | 0.00036357 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1004-12_0_3_load_72 | 89 | 0.00131 | 0.00032831 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1004-12_0_3_load_88 | 90 | 0.00058085 | 0.00014558 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1004-12_0_3_load_101 | 91 | 0.001256 | 0.00031478 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1004-12_0_3_load_110 | 92 | 0.00093281 | 0.00023378 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1004-12_0_3_load_69 | 93 | 0.0010716 | 0.00026856 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1004-12_0_3_load_70 | 94 | 0.0010982 | 0.00027523 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1004-12_0_3_load_73 | 96 | 0.0010729 | 0.0002689 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1004-12_0_3_load_105 | 97 | 0.0021926 | 0.00054951 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1004-12_0_3_load_94 | 98 | 0.00054789 | 0.00013731 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1004-12_0_3_load_77 | 99 | 0.0026828 | 0.00067236 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1004-12_0_3_load_78 | 100 | 0.0016985 | 0.00042569 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1004-12_0_3_load_80 | 101 | 0.0014588 | 0.0003656 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1004-12_0_3_load_82 | 102 | 0.00063109 | 0.00015817 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1004-12_0_3_load_83 | 105 | 0.0017641 | 0.00044212 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1004-12_0_3_load_85 | 106 | 0.00060477 | 0.00015157 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1004-12_0_3_load_87 | 107 | 0.0018838 | 0.00047213 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1004-12_0_3_load_89 | 108 | 0.00084938 | 0.00021288 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1004-12_0_3_load_91 | 109 | 0.0010968 | 0.00027489 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1004-12_0_3_load_92 | 110 | 0.001386 | 0.00034737 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1004-12_0_3_load_93 | 111 | 0.00090764 | 0.00022748 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1004-12_0_3_load_97 | 112 | 0.0015984 | 0.00040059 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1004-12_0_3_load_99 | 114 | 0.0015511 | 0.00038873 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1004-12_0_3_load_118 | 115 | 0.0022211 | 0.00055665 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1004-12_0_3_load_116 | 116 | 0.0035296 | 0.0008846 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1004-12_0_3_load_117 | 117 | 0.0018132 | 0.00045443 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 107 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1004-12_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0053421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1004-12_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.052427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1004-12_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.044691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1004-12_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1004-12_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.016416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1004-12_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.020562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1004-12_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.012056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1004-12_0_3_line_7 | NAYY 4x150 SE | 6 | 12 | 0.0094113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1004-12_0_3_line_8 | NAYY 4x150 SE | 7 | 25 | 0.014612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1004-12_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.010456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1004-12_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.0094778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1004-12_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.0053515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1004-12_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.010479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1004-12_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0035067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1004-12_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.021412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1004-12_0_3_line_15 | NAYY 4x150 SE | 14 | 26 | 0.015311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1004-12_0_3_line_16 | NAYY 4x150 SE | 14 | 24 | 0.024406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1004-12_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.027881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1004-12_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.01016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1004-12_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.0032626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1004-12_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.016521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1004-12_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.017935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1004-12_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.01127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1004-12_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.013091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1004-12_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.028213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1004-12_0_3_line_25 | NAYY 4x150 SE | 22 | 77 | 0.0079772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1004-12_0_3_line_26 | NAYY 4x150 SE | 23 | 101 | 0.0087323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1004-12_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.016982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1004-12_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 6.5554e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1004-12_0_3_line_29 | NAYY 4x150 SE | 28 | 105 | 0.0064627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1004-12_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.052073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1004-12_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0082717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1004-12_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.017036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1004-12_0_3_line_33 | NAYY 4x150 SE | 31 | 35 | 0.011868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1004-12_0_3_line_34 | NAYY 4x150 SE | 32 | 37 | 0.029891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1004-12_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.006064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1004-12_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.047846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1004-12_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.033299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1004-12_0_3_line_38 | NAYY 4x150 SE | 36 | 39 | 0.02332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1004-12_0_3_line_39 | NAYY 4x150 SE | 36 | 40 | 0.0038377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1004-12_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.053066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1004-12_0_3_line_41 | NAYY 4x150 SE | 39 | 41 | 0.021938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1004-12_0_3_line_42 | NAYY 4x150 SE | 40 | 42 | 0.023819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1004-12_0_3_line_43 | NAYY 4x150 SE | 41 | 73 | 0.013668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1004-12_0_3_line_44 | NAYY 4x150 SE | 42 | 116 | 0.0027053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1004-12_0_3_line_45 | NAYY 4x150 SE | 43 | 44 | 0.016201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1004-12_0_3_line_46 | NAYY 4x150 SE | 43 | 45 | 0.046044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1004-12_0_3_line_47 | NAYY 4x150 SE | 44 | 46 | 0.034335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1004-12_0_3_line_48 | NAYY 4x150 SE | 45 | 47 | 0.0017814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1004-12_0_3_line_49 | NAYY 4x150 SE | 46 | 115 | 0.025117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1004-12_0_3_line_50 | NAYY 4x150 SE | 47 | 59 | 0.01831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1004-12_0_3_line_51 | NAYY 4x150 SE | 47 | 57 | 0.024336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1004-12_0_3_line_52 | NAYY 4x150 SE | 48 | 49 | 0.015239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1004-12_0_3_line_53 | NAYY 4x150 SE | 48 | 50 | 0.0088173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1004-12_0_3_line_54 | NAYY 4x150 SE | 49 | 51 | 0.0028231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1004-12_0_3_line_55 | NAYY 4x150 SE | 50 | 52 | 0.0093343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1004-12_0_3_line_56 | NAYY 4x150 SE | 51 | 53 | 0.018213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1004-12_0_3_line_57 | NAYY 4x150 SE | 52 | 54 | 0.01609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1004-12_0_3_line_58 | NAYY 4x150 SE | 53 | 55 | 0.019568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1004-12_0_3_line_59 | NAYY 4x150 SE | 54 | 56 | 0.0043045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1004-12_0_3_line_60 | NAYY 4x150 SE | 55 | 65 | 0.0038804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1004-12_0_3_line_61 | NAYY 4x150 SE | 56 | 66 | 0.013701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1004-12_0_3_line_62 | NAYY 4x150 SE | 57 | 58 | 0.0059149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1004-12_0_3_line_63 | NAYY 4x150 SE | 58 | 60 | 0.01999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1004-12_0_3_line_64 | NAYY 4x150 SE | 59 | 61 | 0.0022919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1004-12_0_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.025991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1004-12_0_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.021085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1004-12_0_3_line_67 | NAYY 4x150 SE | 62 | 64 | 0.00020723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1004-12_0_3_line_68 | NAYY 4x150 SE | 63 | 92 | 0.0020996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1004-12_0_3_line_69 | NAYY 4x150 SE | 64 | 76 | 0.013363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1004-12_0_3_line_70 | NAYY 4x150 SE | 65 | 95 | 0.011153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1004-12_0_3_line_71 | NAYY 4x150 SE | 66 | 67 | 0.019557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1004-12_0_3_line_72 | NAYY 4x150 SE | 67 | 68 | 0.011303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1004-12_0_3_line_73 | NAYY 4x150 SE | 68 | 69 | 0.012703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1004-12_0_3_line_74 | NAYY 4x150 SE | 68 | 70 | 0.032199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1004-12_0_3_line_75 | NAYY 4x150 SE | 69 | 71 | 0.023701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1004-12_0_3_line_76 | NAYY 4x150 SE | 70 | 72 | 0.001494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1004-12_0_3_line_77 | NAYY 4x150 SE | 72 | 99 | 0.035403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1004-12_0_3_line_78 | NAYY 4x150 SE | 73 | 74 | 0.010557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1004-12_0_3_line_79 | NAYY 4x150 SE | 74 | 75 | 0.016656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1004-12_0_3_line_80 | NAYY 4x150 SE | 75 | 76 | 0.014576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1004-12_0_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.030539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1004-12_0_3_line_82 | NAYY 4x150 SE | 77 | 78 | 0.0077576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1004-12_0_3_line_83 | NAYY 4x150 SE | 79 | 80 | 0.0074857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_1004-12_0_3_line_84 | NAYY 4x150 SE | 79 | 81 | 0.01267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_1004-12_0_3_line_85 | NAYY 4x150 SE | 80 | 82 | 0.014471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_1004-12_0_3_line_86 | NAYY 4x150 SE | 81 | 83 | 0.00079725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1004-12_0_3_line_87 | NAYY 4x150 SE | 81 | 84 | 0.032627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_1004-12_0_3_line_88 | NAYY 4x150 SE | 82 | 85 | 0.016829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1004-12_0_3_line_89 | NAYY 4x150 SE | 82 | 86 | 0.006145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_1004-12_0_3_line_90 | NAYY 4x150 SE | 83 | 87 | 0.010931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1004-12_0_3_line_91 | NAYY 4x150 SE | 84 | 88 | 0.0021899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1004-12_0_3_line_92 | NAYY 4x150 SE | 86 | 89 | 0.016603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1004-12_0_3_line_93 | NAYY 4x150 SE | 86 | 90 | 0.018682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_1004-12_0_3_line_94 | NAYY 4x150 SE | 87 | 91 | 0.01014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1004-12_0_3_line_95 | NAYY 4x150 SE | 88 | 92 | 0.021577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1004-12_0_3_line_96 | NAYY 4x150 SE | 89 | 94 | 0.016835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1004-12_0_3_line_97 | NAYY 4x150 SE | 90 | 108 | 0.0046502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_1004-12_0_3_line_98 | NAYY 4x150 SE | 91 | 100 | 0.023118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1004-12_0_3_line_99 | NAYY 4x150 SE | 93 | 94 | 0.014087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1004-12_0_3_line_100 | NAYY 4x150 SE | 95 | 96 | 0.012806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1004-12_0_3_line_101 | NAYY 4x150 SE | 96 | 97 | 0.0011308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1004-12_0_3_line_102 | NAYY 4x150 SE | 97 | 98 | 0.013647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1004-12_0_3_line_103 | NAYY 4x150 SE | 98 | 111 | 0.0086937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1004-12_0_3_line_104 | NAYY 4x150 SE | 99 | 100 | 0.0096373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1004-12_0_3_line_105 | NAYY 4x150 SE | 101 | 102 | 0.0032983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1004-12_0_3_line_106 | NAYY 4x150 SE | 102 | 103 | 0.04602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1004-12_0_3_line_107 | NAYY 4x150 SE | 103 | 104 | 0.025942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1004-12_0_3_line_108 | NAYY 4x150 SE | 104 | 114 | 0.013958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1004-12_0_3_line_109 | NAYY 4x150 SE | 105 | 106 | 0.01056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1004-12_0_3_line_110 | NAYY 4x150 SE | 106 | 107 | 0.0092794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1004-12_0_3_line_111 | NAYY 4x150 SE | 107 | 108 | 0.024295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
112 | LV_1004-12_0_3_line_112 | NAYY 4x150 SE | 109 | 110 | 0.024753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1004-12_0_3_line_113 | NAYY 4x150 SE | 109 | 111 | 0.0025485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1004-12_0_3_line_114 | NAYY 4x150 SE | 112 | 113 | 0.0078647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1004-12_0_3_line_115 | NAYY 4x150 SE | 113 | 114 | 0.018451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1004-12_0_3_line_116 | NAYY 4x150 SE | 115 | 117 | 0.010104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1004-12_0_3_trafo_87 | 0.25 MVA 20/0.4 kV | 118 | 107 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2645641.9487 | 1186052.1838 | 2645643.025 | 1186057.4164
1 | 2645607.8413 | 1186018.7838 | 2645618.0975 | 1186021.7523 | 2645629.8374 | 1186026.2886 | 2645633.106 | 1186028.9594 | 2645637.7065 | 1186038.0883 | 2645641.9487 | 1186052.1838 | 2645641.9487 | 1186052.1838
2 | 2645673.5072 | 1186085.9823 | 2645666.5748 | 1186079.0304 | 2645663.4092 | 1186076.8829 | 2645651.7645 | 1186072.8809 | 2645647.0205 | 1186069.5652 | 2645644.7155 | 1186065.6344 | 2645643.025 | 1186057.4164
3 | 2645607.8413 | 1186018.7838 | 2645614.5982 | 1186005.1736
4 | 2645623.0391 | 1185991.1065 | 2645615.8855 | 1186002.5806 | 2645614.5982 | 1186005.1736
5 | 2645623.0391 | 1185991.1065 | 2645626.7114 | 1185992.8688 | 2645632.9414 | 1185994.4504 | 2645635.8013 | 1185994.6723 | 2645641.1514 | 1185991.5558 | 2645641.9722 | 1185990.9827
6 | 2645619.4326 | 1185979.6951 | 2645621.2189 | 1185987.6241 | 2645623.0391 | 1185991.1065
7 | 2645641.9722 | 1185990.9827 | 2645649.6884 | 1185985.5945
8 | 2645619.4326 | 1185979.6951 | 2645631.4634 | 1185971.4023
9 | 2645666.0509 | 1185974.1688 | 2645674.6238 | 1185968.1824
10 | 2645666.0509 | 1185974.1688 | 2645658.2801 | 1185979.595
11 | 2645674.6238 | 1185968.1824 | 2645679.0115 | 1185965.1186
12 | 2645649.6884 | 1185985.5945 | 2645658.2801 | 1185979.595
13 | 2645680.8656 | 1185962.1422 | 2645680.8656 | 1185962.1422 | 2645679.0115 | 1185965.1186 | 2645679.0115 | 1185965.1186
14 | 2645675.0913 | 1185941.8204 | 2645681.0308 | 1185957.4965 | 2645680.8656 | 1185962.1422
15 | 2645675.0913 | 1185941.8204 | 2645689.6502 | 1185937.0792
16 | 2645675.0913 | 1185941.8204 | 2645670.4309 | 1185944.542 | 2645654.7798 | 1185955.3303
17 | 2645637.925 | 1185890.0237 | 2645650.125 | 1185881.4196 | 2645660.3758 | 1185873.5025
18 | 2645637.925 | 1185890.0237 | 2645629.6225 | 1185895.8792
19 | 2645662.958 | 1185871.5082 | 2645660.3758 | 1185873.5025
20 | 2645629.6225 | 1185895.8792 | 2645616.1211 | 1185905.4012
21 | 2645662.958 | 1185871.5082 | 2645677.1522 | 1185860.5455
22 | 2645616.1211 | 1185905.4012 | 2645606.9114 | 1185911.8964
23 | 2645677.1522 | 1185860.5455 | 2645687.5126 | 1185852.5438
24 | 2645583.9475 | 1185928.2857 | 2645592.7982 | 1185921.8498 | 2645606.9114 | 1185911.8964
25 | 2645687.5126 | 1185852.5438 | 2645693.8261 | 1185847.6677
26 | 2645583.9475 | 1185928.2857 | 2645576.8849 | 1185933.4213
27 | 2645689.6502 | 1185937.0792 | 2645689.9016 | 1185936.9973 | 2645693.4552 | 1185935.3235 | 2645704.236 | 1185928.443
28 | 2645704.2913 | 1185928.4077 | 2645704.236 | 1185928.443
29 | 2645709.726 | 1185924.9112 | 2645709.0678 | 1185925.3593 | 2645704.2913 | 1185928.4077
30 | 2645652.8476 | 1185738.4179 | 2645644.1321 | 1185732.4816 | 2645641.1941 | 1185731.4809 | 2645638.1805 | 1185731.3802 | 2645632.8105 | 1185733.0735 | 2645619.7178 | 1185738.7548 | 2645605.8425 | 1185745.6778
31 | 2645652.8476 | 1185738.4179 | 2645651.0985 | 1185742.618 | 2645649.9075 | 1185746.1442
32 | 2645652.8476 | 1185738.4179 | 2645656.6646 | 1185729.2197 | 2645658.3097 | 1185722.3362
33 | 2645646.1097 | 1185757.388 | 2645649.9075 | 1185746.1442
34 | 2645653.0531 | 1185693.406 | 2645657.3816 | 1185705.2232 | 2645659.061 | 1185714.1742 | 2645658.3672 | 1185722.0955 | 2645658.3097 | 1185722.3362
35 | 2645620.2539 | 1185797.6465 | 2645615.8223 | 1185799.3693 | 2645614.8309 | 1185800.2246
36 | 2645620.2539 | 1185797.6465 | 2645646.1097 | 1185757.388
37 | 2645592.3916 | 1185823.8489 | 2645594.4522 | 1185817.8057 | 2645614.8309 | 1185800.2246
38 | 2645592.3916 | 1185823.8489 | 2645615.5654 | 1185821.2428
39 | 2645592.3916 | 1185823.8489 | 2645588.5696 | 1185824.1959
40 | 2645653.0531 | 1185693.406 | 2645667.4726 | 1185708.9021 | 2645676.8844 | 1185715.5885 | 2645686.9711 | 1185718.8338 | 2645693.2629 | 1185718.3593 | 2645696.2089 | 1185716.5681
41 | 2645637.3659 | 1185818.7911 | 2645615.5654 | 1185821.2428
42 | 2645588.5696 | 1185824.1959 | 2645581.4334 | 1185824.8439 | 2645570.5341 | 1185823.1045 | 2645566.1378 | 1185819.6097
43 | 2645637.3659 | 1185818.7911 | 2645650.9481 | 1185817.2637
44 | 2645564.02 | 1185817.9262 | 2645566.1378 | 1185819.6097
45 | 2645819.8176 | 1185761.5375 | 2645831.8434 | 1185772.3932
46 | 2645819.8176 | 1185761.5375 | 2645809.1976 | 1185769.1828 | 2645778.4887 | 1185781.1511
47 | 2645859.6238 | 1185792.5215 | 2645835.1573 | 1185775.3846 | 2645831.8434 | 1185772.3932
48 | 2645776.8289 | 1185781.798 | 2645778.4887 | 1185781.1511
49 | 2645880.196 | 1185806.9307 | 2645859.6238 | 1185792.5215
50 | 2645776.8289 | 1185781.798 | 2645784.2697 | 1185798.5282
51 | 2645776.8289 | 1185781.798 | 2645754.073 | 1185790.4246
52 | 2645818.8021 | 1185940.2934 | 2645806.0019 | 1185948.5625
53 | 2645826.2084 | 1185935.5088 | 2645818.8021 | 1185940.2934
54 | 2645803.6306 | 1185950.0944 | 2645806.0019 | 1185948.5625
55 | 2645826.2084 | 1185935.5088 | 2645833.6487 | 1185930.7022 | 2645834.0567 | 1185930.4562
56 | 2645803.6306 | 1185950.0944 | 2645788.3322 | 1185959.9774
57 | 2645834.0567 | 1185930.4562 | 2645847.8352 | 1185922.1462
58 | 2645771.702 | 1185970.2842 | 2645780.381 | 1185965.114 | 2645788.3322 | 1185959.9774
59 | 2645851.5212 | 1185919.9231 | 2645847.8352 | 1185922.1462
60 | 2645771.702 | 1185970.2842 | 2645768.3683 | 1185972.2702
61 | 2645851.5212 | 1185919.9231 | 2645855.7279 | 1185917.386 | 2645864.0833 | 1185914.6606
62 | 2645748.5422 | 1185792.5213 | 2645754.073 | 1185790.4246
63 | 2645748.5422 | 1185792.5213 | 2645729.7216 | 1185799.2592
64 | 2645784.2697 | 1185798.5282 | 2645785.201 | 1185800.6223
65 | 2645729.7216 | 1185799.2592 | 2645705.2517 | 1185808.0196
66 | 2645785.201 | 1185800.6223 | 2645789.4552 | 1185810.1877 | 2645791.9448 | 1185820.5079
67 | 2645705.2517 | 1185808.0196 | 2645705.0566 | 1185808.0895
68 | 2645792.4371 | 1185822.5489 | 2645791.9448 | 1185820.5079
69 | 2645692.4756 | 1185812.5935 | 2645705.0566 | 1185808.0895
70 | 2645758.7864 | 1185977.9784 | 2645768.3683 | 1185972.2702
71 | 2645882.9932 | 1185909.7878 | 2645876.3368 | 1185911.7183 | 2645868.6489 | 1185913.1714 | 2645864.0833 | 1185914.6606
72 | 2645892.6816 | 1185904.8619 | 2645890.3786 | 1185907.6458 | 2645882.9932 | 1185909.7878
73 | 2645892.6816 | 1185904.8619 | 2645895.963 | 1185905.8431 | 2645904.9665 | 1185903.6023
74 | 2645892.6816 | 1185904.8619 | 2645893.079 | 1185901.7966 | 2645886.458 | 1185873.4521
75 | 2645904.9665 | 1185903.6023 | 2645927.9659 | 1185897.8781
76 | 2645886.1182 | 1185871.9973 | 2645886.458 | 1185873.4521
77 | 2645886.1182 | 1185871.9973 | 2645884.6631 | 1185865.7681 | 2645882.6265 | 1185862.6619 | 2645880.2234 | 1185860.5757 | 2645876.1533 | 1185859.9442 | 2645858.6888 | 1185864.2616
78 | 2645661.4389 | 1185816.0839 | 2645650.9481 | 1185817.2637
79 | 2645677.9909 | 1185814.2225 | 2645661.4389 | 1185816.0839
80 | 2645692.4756 | 1185812.5935 | 2645677.9909 | 1185814.2225
81 | 2645692.4756 | 1185812.5935 | 2645699.4227 | 1185838.2494 | 2645699.2628 | 1185842.2059
82 | 2645699.2628 | 1185842.2059 | 2645696.5204 | 1185845.5868 | 2645693.8261 | 1185847.6677
83 | 2645793.3958 | 1185880.5472 | 2645786.1492 | 1185882.4241
84 | 2645805.6615 | 1185877.3703 | 2645793.3958 | 1185880.5472
85 | 2645772.1406 | 1185886.0524 | 2645786.1492 | 1185882.4241
86 | 2645806.4355 | 1185877.179 | 2645805.6615 | 1185877.3703
87 | 2645805.6615 | 1185877.3703 | 2645798.0105 | 1185845.6532
88 | 2645772.1406 | 1185886.0524 | 2645768.0235 | 1185869.7345
89 | 2645766.4827 | 1185888.4883 | 2645772.1406 | 1185886.0524
90 | 2645806.4355 | 1185877.179 | 2645817.0469 | 1185874.5558
91 | 2645798.0105 | 1185845.6532 | 2645797.497 | 1185843.5244
92 | 2645766.4827 | 1185888.4883 | 2645766.3004 | 1185892.3668 | 2645760.3883 | 1185902.1048 | 2645759.8482 | 1185903.3178
93 | 2645766.4827 | 1185888.4883 | 2645750.4583 | 1185898.0926
94 | 2645826.8907 | 1185872.1223 | 2645817.0469 | 1185874.5558
95 | 2645792.4371 | 1185822.5489 | 2645797.497 | 1185843.5244
96 | 2645759.8482 | 1185903.3178 | 2645756.0715 | 1185911.7993 | 2645754.1727 | 1185919.1074
97 | 2645750.4583 | 1185898.0926 | 2645746.4697 | 1185900.4832
98 | 2645826.8907 | 1185872.1223 | 2645849.3331 | 1185866.5744
99 | 2645751.389 | 1185932.9053 | 2645752.9581 | 1185923.7821 | 2645754.1727 | 1185919.1074
100 | 2645758.7864 | 1185977.9784 | 2645748.0177 | 1185984.9085
101 | 2645748.0177 | 1185984.9085 | 2645747.0668 | 1185985.5204
102 | 2645747.0668 | 1185985.5204 | 2645735.5906 | 1185992.9059
103 | 2645728.28 | 1185997.6106 | 2645735.5906 | 1185992.9059
104 | 2645849.3331 | 1185866.5744 | 2645858.6888 | 1185864.2616
105 | 2645574.2173 | 1185935.361 | 2645576.8849 | 1185933.4213
106 | 2645536.9973 | 1185962.4257 | 2645574.2173 | 1185935.361
107 | 2645536.9973 | 1185962.4257 | 2645522.709 | 1185940.7498
108 | 2645522.709 | 1185940.7498 | 2645515.0282 | 1185929.0951
109 | 2645709.726 | 1185924.9112 | 2645718.4548 | 1185918.9679
110 | 2645726.125 | 1185913.7453 | 2645718.4548 | 1185918.9679
111 | 2645746.4697 | 1185900.4832 | 2645739.2297 | 1185904.8226 | 2645726.125 | 1185913.7453
112 | 2645726.1369 | 1185998.9898 | 2645718.1199 | 1186004.1491 | 2645706.3705 | 1186005.8604 | 2645703.505 | 1186007.5872
113 | 2645726.1369 | 1185998.9898 | 2645728.28 | 1185997.6106
114 | 2645504.8749 | 1185913.6885 | 2645500.3644 | 1185907.2457
115 | 2645504.8749 | 1185913.6885 | 2645515.0282 | 1185929.0951
116 | 2645889.212 | 1185810.8619 | 2645884.9204 | 1185810.2398 | 2645880.196 | 1185806.9307

## bus_geodata
| x | y | coords
0 | 2645641.9487 | 1186052.1838
1 | 2645643.025 | 1186057.4164
2 | 2645607.8413 | 1186018.7838
3 | 2645673.5072 | 1186085.9823
4 | 2645614.5982 | 1186005.1736
5 | 2645623.0391 | 1185991.1065
6 | 2645641.9722 | 1185990.9827
7 | 2645619.4326 | 1185979.6951
8 | 2645666.0509 | 1185974.1688
9 | 2645674.6238 | 1185968.1824
10 | 2645658.2801 | 1185979.595
11 | 2645679.0115 | 1185965.1186
12 | 2645649.6884 | 1185985.5945
13 | 2645680.8656 | 1185962.1422
14 | 2645675.0913 | 1185941.8204
15 | 2645637.925 | 1185890.0237
16 | 2645660.3758 | 1185873.5025
17 | 2645629.6225 | 1185895.8792
18 | 2645662.958 | 1185871.5082
19 | 2645616.1211 | 1185905.4012
20 | 2645677.1522 | 1185860.5455
21 | 2645606.9114 | 1185911.8964
22 | 2645687.5126 | 1185852.5438
23 | 2645583.9475 | 1185928.2857
24 | 2645654.7798 | 1185955.3303
25 | 2645631.4634 | 1185971.4023
26 | 2645689.6502 | 1185937.0792
27 | 2645704.236 | 1185928.443
28 | 2645704.2913 | 1185928.4077
29 | 2645605.8425 | 1185745.6778
30 | 2645652.8476 | 1185738.4179
31 | 2645649.9075 | 1185746.1442
32 | 2645658.3097 | 1185722.3362
33 | 2645620.2539 | 1185797.6465
34 | 2645614.8309 | 1185800.2246
35 | 2645646.1097 | 1185757.388
36 | 2645592.3916 | 1185823.8489
37 | 2645653.0531 | 1185693.406
38 | 2645696.2089 | 1185716.5681
39 | 2645615.5654 | 1185821.2428
40 | 2645588.5696 | 1185824.1959
41 | 2645637.3659 | 1185818.7911
42 | 2645566.1378 | 1185819.6097
43 | 2645819.8176 | 1185761.5375
44 | 2645831.8434 | 1185772.3932
45 | 2645778.4887 | 1185781.1511
46 | 2645859.6238 | 1185792.5215
47 | 2645776.8289 | 1185781.798
48 | 2645818.8021 | 1185940.2934
49 | 2645806.0019 | 1185948.5625
50 | 2645826.2084 | 1185935.5088
51 | 2645803.6306 | 1185950.0944
52 | 2645834.0567 | 1185930.4562
53 | 2645788.3322 | 1185959.9774
54 | 2645847.8352 | 1185922.1462
55 | 2645771.702 | 1185970.2842
56 | 2645851.5212 | 1185919.9231
57 | 2645754.073 | 1185790.4246
58 | 2645748.5422 | 1185792.5213
59 | 2645784.2697 | 1185798.5282
60 | 2645729.7216 | 1185799.2592
61 | 2645785.201 | 1185800.6223
62 | 2645705.2517 | 1185808.0196
63 | 2645791.9448 | 1185820.5079
64 | 2645705.0566 | 1185808.0895
65 | 2645768.3683 | 1185972.2702
66 | 2645864.0833 | 1185914.6606
67 | 2645882.9932 | 1185909.7878
68 | 2645892.6816 | 1185904.8619
69 | 2645904.9665 | 1185903.6023
70 | 2645886.458 | 1185873.4521
71 | 2645927.9659 | 1185897.8781
72 | 2645886.1182 | 1185871.9973
73 | 2645650.9481 | 1185817.2637
74 | 2645661.4389 | 1185816.0839
75 | 2645677.9909 | 1185814.2225
76 | 2645692.4756 | 1185812.5935
77 | 2645693.8261 | 1185847.6677
78 | 2645699.2628 | 1185842.2059
79 | 2645793.3958 | 1185880.5472
80 | 2645786.1492 | 1185882.4241
81 | 2645805.6615 | 1185877.3703
82 | 2645772.1406 | 1185886.0524
83 | 2645806.4355 | 1185877.179
84 | 2645798.0105 | 1185845.6532
85 | 2645768.0235 | 1185869.7345
86 | 2645766.4827 | 1185888.4883
87 | 2645817.0469 | 1185874.5558
88 | 2645797.497 | 1185843.5244
89 | 2645759.8482 | 1185903.3178
90 | 2645750.4583 | 1185898.0926
91 | 2645826.8907 | 1185872.1223
92 | 2645792.4371 | 1185822.5489
93 | 2645751.389 | 1185932.9053
94 | 2645754.1727 | 1185919.1074
95 | 2645758.7864 | 1185977.9784
96 | 2645748.0177 | 1185984.9085
97 | 2645747.0668 | 1185985.5204
98 | 2645735.5906 | 1185992.9059
99 | 2645858.6888 | 1185864.2616
100 | 2645849.3331 | 1185866.5744
101 | 2645576.8849 | 1185933.4213
102 | 2645574.2173 | 1185935.361
103 | 2645536.9973 | 1185962.4257
104 | 2645522.709 | 1185940.7498
105 | 2645709.726 | 1185924.9112
106 | 2645718.4548 | 1185918.9679
107 | 2645726.125 | 1185913.7453
108 | 2645746.4697 | 1185900.4832
109 | 2645726.1369 | 1185998.9898
110 | 2645703.505 | 1186007.5872
111 | 2645728.28 | 1185997.6106
112 | 2645500.3644 | 1185907.2457
113 | 2645504.8749 | 1185913.6885
114 | 2645515.0282 | 1185929.0951
115 | 2645880.196 | 1185806.9307
116 | 2645564.02 | 1185817.9262
117 | 2645889.212 | 1185810.8619
118 | 2645726.125 | 1185913.7453

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99552 | -0.031431 | 0.00052306 | 0.00013109
1 | 0.99551 | -0.031491 | 0.00043607 | 0.00010929
2 | 0.99564 | -0.03056 | 0 | 0
3 | 0.99547 | -0.0318 | 0.00068336 | 0.00017127
4 | 0.99568 | -0.030307 | 0.00097174 | 0.00024354
5 | 0.99574 | -0.029873 | 0 | 0
6 | 0.99596 | -0.028361 | 0.0018686 | 0.00046831
7 | 0.99566 | -0.030441 | 0 | 0
8 | 0.99642 | -0.025075 | 0.0019601 | 0.00049124
9 | 0.99665 | -0.023497 | 0.0018017 | 0.00045154
10 | 0.99625 | -0.026319 | 0.0019239 | 0.00048217
11 | 0.99678 | -0.022593 | 0.001294 | 0.00032432
12 | 0.99608 | -0.027492 | 0.0019525 | 0.00048935
13 | 0.99687 | -0.021955 | 0.0010502 | 0.00026321
14 | 0.99745 | -0.017836 | 0.0046468 | 0.0011646
15 | 0.97303 | -0.18963 | 0.0020271 | 0.00050803
16 | 0.9736 | -0.18553 | 0.0014338 | 0.00035935
17 | 0.97285 | -0.19091 | 0.0023076 | 0.00057834
18 | 0.97367 | -0.185 | 0.0016056 | 0.00040241
19 | 0.97262 | -0.19258 | 0.0018662 | 0.00046771
20 | 0.97412 | -0.18179 | 0.0014259 | 0.00035737
21 | 0.97249 | -0.19351 | 0.0011964 | 0.00029984
22 | 0.97447 | -0.17925 | 0.0016229 | 0.00040675
23 | 0.97222 | -0.19546 | 0.0013059 | 0.00032728
24 | 0.99734 | -0.018607 | 0.0031496 | 0.00078936
25 | 0.99556 | -0.031129 | 0.0046762 | 0.001172
26 | 0.99804 | -0.013697 | 0.0018373 | 0.00046046
27 | 0.99874 | -0.008799 | 0.00060449 | 0.0001515
28 | 0.99874 | -0.0087797 | 0.0024491 | 0.00061381
29 | 0.97107 | -0.20374 | 0.00091729 | 0.00022989
30 | 0.97114 | -0.20323 | 0 | 0
31 | 0.97118 | -0.20294 | 0.00092119 | 0.00023087
32 | 0.97108 | -0.20366 | 0.0012376 | 0.00031016
33 | 0.97174 | -0.19889 | 0.0014754 | 0.00036977
34 | 0.97181 | -0.19835 | 0.0030752 | 0.00077072
35 | 0.97125 | -0.20242 | 0.002769 | 0.00069397
36 | 0.97238 | -0.19429 | 0 | 0
37 | 0.97103 | -0.20401 | 0 | 0
38 | 0.97094 | -0.20463 | 0.001108 | 0.00027769
39 | 0.97307 | -0.18931 | 0.0017384 | 0.00043569
40 | 0.97233 | -0.19465 | 0.002471 | 0.00061929
41 | 0.97377 | -0.18423 | 0.0023622 | 0.00059201
42 | 0.97211 | -0.19622 | 0.0027142 | 0.00068024
43 | 0.98285 | -0.11959 | 0 | 0
44 | 0.98267 | -0.12086 | 0.0013376 | 0.00033525
45 | 0.98335 | -0.116 | 0.00081589 | 0.00020448
46 | 0.98236 | -0.12306 | 0.0021664 | 0.00054295
47 | 0.98338 | -0.11585 | 0 | 0
48 | 0.98388 | -0.11277 | 0.0010067 | 0.00025229
49 | 0.98357 | -0.11498 | 0.0014177 | 0.00035532
50 | 0.98408 | -0.11141 | 0.0014874 | 0.00037277
51 | 0.98352 | -0.11535 | 0.0012821 | 0.00032131
52 | 0.9843 | -0.10982 | 0.0014362 | 0.00035994
53 | 0.98322 | -0.11748 | 0.0013188 | 0.00033052
54 | 0.98472 | -0.10684 | 0.0012234 | 0.0003066
55 | 0.98294 | -0.1195 | 0.0018302 | 0.00045869
56 | 0.98484 | -0.10599 | 0.0022227 | 0.00055705
57 | 0.98133 | -0.13032 | 0.00085544 | 0.00021439
58 | 0.98084 | -0.13379 | 0 | 0
59 | 0.98514 | -0.10343 | 0.0017729 | 0.00044434
60 | 0.97918 | -0.14555 | 0.00081863 | 0.00020517
61 | 0.98536 | -0.10183 | 0.0012482 | 0.00031282
62 | 0.97706 | -0.16068 | 0.00091883 | 0.00023028
63 | 0.98748 | -0.086939 | 0.0039856 | 0.00099888
64 | 0.97704 | -0.1608 | 0.001024 | 0.00025664
65 | 0.98289 | -0.11983 | 0.00097599 | 0.0002446
66 | 0.98526 | -0.10297 | 0.0021211 | 0.0005316
67 | 0.98593 | -0.098238 | 0.0013849 | 0.00034709
68 | 0.98634 | -0.095347 | 0 | 0
69 | 0.98628 | -0.095729 | 0.0014524 | 0.000364
70 | 0.98764 | -0.086154 | 0.0014779 | 0.00037039
71 | 0.98623 | -0.096089 | 0.0014784 | 0.00037052
72 | 0.9877 | -0.085705 | 0.0014706 | 0.00036856
73 | 0.97426 | -0.18073 | 0.0013652 | 0.00034216
74 | 0.97466 | -0.17788 | 0.0020703 | 0.00051888
75 | 0.97534 | -0.17302 | 0.002855 | 0.00071553
76 | 0.97599 | -0.16834 | 0 | 0
77 | 0.9747 | -0.17757 | 0.0020393 | 0.0005111
78 | 0.97495 | -0.17577 | 0.0011168 | 0.00027989
79 | 0.99319 | -0.047138 | 0.0012478 | 0.00031272
80 | 0.99383 | -0.04265 | 0.0010355 | 0.00025952
81 | 0.99211 | -0.054669 | 0 | 0
82 | 0.99509 | -0.033913 | 0 | 0
83 | 0.99206 | -0.054994 | 0.0020612 | 0.00051659
84 | 0.99027 | -0.067444 | 0.0018361 | 0.00046017
85 | 0.99503 | -0.034308 | 0.0023275 | 0.00058333
86 | 0.99563 | -0.030138 | 0 | 0
87 | 0.99146 | -0.059232 | 0.0017422 | 0.00043665
88 | 0.99003 | -0.069122 | 0.0014507 | 0.00036357
89 | 0.99555 | -0.03072 | 0.00131 | 0.00032831
90 | 0.99734 | -0.018359 | 0.00058085 | 0.00014558
91 | 0.99092 | -0.062988 | 0.001256 | 0.00031478
92 | 0.98771 | -0.085373 | 0.00093281 | 0.00023378
93 | 0.99548 | -0.031241 | 0.0010716 | 0.00026856
94 | 0.9955 | -0.031088 | 0.0010982 | 0.00027523
95 | 0.98278 | -0.12066 | 0 | 0
96 | 0.98264 | -0.12162 | 0.0010729 | 0.0002689
97 | 0.98263 | -0.12169 | 0.0021926 | 0.00054951
98 | 0.98255 | -0.12225 | 0.00054789 | 0.00013731
99 | 0.98928 | -0.074561 | 0.0026828 | 0.00067236
100 | 0.98974 | -0.07127 | 0.0016985 | 0.00042569
101 | 0.97215 | -0.19594 | 0.0014588 | 0.0003656
102 | 0.97213 | -0.19608 | 0.00063109 | 0.00015817
103 | 0.97192 | -0.19761 | 0 | 0
104 | 0.9718 | -0.19847 | 0 | 0
105 | 0.99904 | -0.0067202 | 0.0017641 | 0.00044212
106 | 0.99955 | -0.0031715 | 0.00060477 | 0.00015157
107 | 1 | 0 | -0.16426 | -0.041281
108 | 0.99776 | -0.015419 | 0.00084938 | 0.00021288
109 | 0.9825 | -0.12262 | 0.0010968 | 0.00027489
110 | 0.98245 | -0.12297 | 0.001386 | 0.00034737
111 | 0.98251 | -0.12255 | 0.00090764 | 0.00022748
112 | 0.97167 | -0.19938 | 0.0015984 | 0.00040059
113 | 0.97169 | -0.19925 | 0 | 0
114 | 0.97173 | -0.19894 | 0.0015511 | 0.00038873
115 | 0.98222 | -0.12411 | 0.0022211 | 0.00055665
116 | 0.9721 | -0.19632 | 0.0035296 | 0.0008846
117 | 0.98219 | -0.1243 | 0.0018132 | 0.00045443
118 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0011195 | 0.00027992 | -0.0011195 | -0.00027998 | 9.3309e-09 | -6.5869e-08 | 0.001673 | 0.0016731 | 0.0016731 | 0.99552 | -0.031431 | 0.99551 | -0.031491 | 0.61966
1 | -0.0016425 | -0.00041101 | 0.0016427 | 0.0004104 | 1.9713e-07 | -6.0592e-07 | 0.0024549 | 0.0024546 | 0.0024549 | 0.99552 | -0.031431 | 0.99564 | -0.03056 | 0.90921
2 | 0.00068339 | 0.0001707 | -0.00068336 | -0.00017127 | 2.9092e-08 | -5.6985e-07 | 0.0010213 | 0.0010215 | 0.0010215 | 0.99551 | -0.031491 | 0.99547 | -0.0318 | 0.37832
3 | -0.0016427 | -0.0004104 | 0.0016428 | 0.00041023 | 5.7128e-08 | -1.7565e-07 | 0.0024546 | 0.0024546 | 0.0024546 | 0.99564 | -0.03056 | 0.99568 | -0.030307 | 0.90912
4 | -0.0026145 | -0.00065377 | 0.0026147 | 0.00065361 | 1.5635e-07 | -1.5339e-07 | 0.0039068 | 0.0039067 | 0.0039068 | 0.99568 | -0.030307 | 0.99574 | -0.029873 | 1.447
5 | -0.0072917 | -0.0018256 | 0.0072932 | 0.0018259 | 1.5233e-06 | 3.1834e-07 | 0.010896 | 0.010896 | 0.010896 | 0.99574 | -0.029873 | 0.99596 | -0.028361 | 4.0355
6 | 0.004677 | 0.0011719 | -0.0046767 | -0.001172 | 3.6749e-07 | -1.5467e-08 | 0.0069892 | 0.0069892 | 0.0069892 | 0.99574 | -0.029873 | 0.99566 | -0.030441 | 2.5886
7 | -0.0091618 | -0.0022942 | 0.0091629 | 0.0022945 | 1.1002e-06 | 3.0068e-07 | 0.013688 | 0.013688 | 0.013688 | 0.99596 | -0.028361 | 0.99608 | -0.027492 | 5.0695
8 | 0.0046767 | 0.001172 | -0.0046762 | -0.001172 | 4.4541e-07 | -1.8709e-08 | 0.0069892 | 0.0069893 | 0.0069893 | 0.99566 | -0.030441 | 0.99556 | -0.031129 | 2.5886
9 | -0.015003 | -0.0037585 | 0.015007 | 0.0037597 | 3.2752e-06 | 1.1235e-06 | 0.022405 | 0.022405 | 0.022405 | 0.99642 | -0.025075 | 0.99665 | -0.023497 | 8.2981
10 | 0.013043 | 0.0032673 | -0.013041 | -0.0032666 | 2.2437e-06 | 7.3955e-07 | 0.019478 | 0.019478 | 0.019478 | 0.99642 | -0.025075 | 0.99625 | -0.026319 | 7.214
11 | -0.016808 | -0.0042112 | 0.01681 | 0.0042119 | 2.103e-06 | 7.3908e-07 | 0.025095 | 0.025095 | 0.025095 | 0.99665 | -0.023497 | 0.99678 | -0.022593 | 9.2944
12 | 0.011117 | 0.0027844 | -0.011115 | -0.0027838 | 1.8028e-06 | 5.5696e-07 | 0.016604 | 0.016604 | 0.016604 | 0.99625 | -0.026319 | 0.99608 | -0.027492 | 6.1498
13 | -0.018105 | -0.0045363 | 0.018106 | 0.0045368 | 1.5983e-06 | 5.6902e-07 | 0.027027 | 0.027027 | 0.027027 | 0.99678 | -0.022593 | 0.99687 | -0.021955 | 10.0098
14 | -0.019156 | -0.0048 | 0.019167 | 0.004804 | 1.0924e-05 | 3.9224e-06 | 0.028594 | 0.028594 | 0.028594 | 0.99687 | -0.021955 | 0.99745 | -0.017836 | 10.5904
15 | -0.026964 | -0.0067577 | 0.026979 | 0.0067635 | 1.546e-05 | 5.746e-06 | 0.040225 | 0.040225 | 0.040225 | 0.99745 | -0.017836 | 0.99804 | -0.013697 | 14.8983
16 | 0.0031499 | 0.00078917 | -0.0031496 | -0.00078936 | 3.3628e-07 | -1.8918e-07 | 0.004699 | 0.0046991 | 0.0046991 | 0.99745 | -0.017836 | 0.99734 | -0.018607 | 1.7404
17 | -0.013951 | -0.0034953 | 0.013959 | 0.003498 | 7.9189e-06 | 2.6992e-06 | 0.021335 | 0.021335 | 0.021335 | 0.97303 | -0.18963 | 0.9736 | -0.18553 | 7.9017
18 | 0.011924 | 0.0029873 | -0.011922 | -0.0029866 | 2.108e-06 | 6.8459e-07 | 0.018235 | 0.018235 | 0.018235 | 0.97303 | -0.18963 | 0.97285 | -0.19091 | 6.7537
19 | -0.015393 | -0.0038574 | 0.015394 | 0.0038578 | 1.1268e-06 | 3.928e-07 | 0.023526 | 0.023526 | 0.023526 | 0.9736 | -0.18553 | 0.97367 | -0.185 | 8.7133
20 | 0.0096145 | 0.0024083 | -0.0096122 | -0.0024076 | 2.2294e-06 | 6.5236e-07 | 0.014705 | 0.014705 | 0.014705 | 0.97285 | -0.19091 | 0.97262 | -0.19258 | 5.4464
21 | -0.017 | -0.0042602 | 0.017007 | 0.0042629 | 7.5536e-06 | 2.6821e-06 | 0.02598 | 0.02598 | 0.02598 | 0.97367 | -0.185 | 0.97412 | -0.18179 | 9.6222
22 | 0.007746 | 0.0019399 | -0.007745 | -0.0019397 | 9.8753e-07 | 2.3998e-07 | 0.01185 | 0.01185 | 0.01185 | 0.97262 | -0.19258 | 0.97249 | -0.19351 | 4.389
23 | -0.018433 | -0.0046202 | 0.01844 | 0.0046226 | 6.4766e-06 | 2.328e-06 | 0.028158 | 0.028158 | 0.028158 | 0.97412 | -0.18179 | 0.97447 | -0.17925 | 10.4289
24 | 0.0065487 | 0.0016398 | -0.0065469 | -0.0016395 | 1.7675e-06 | 3.2985e-07 | 0.01002 | 0.01002 | 0.01002 | 0.97249 | -0.19351 | 0.97222 | -0.19546 | 3.7111
25 | -0.020063 | -0.0050293 | 0.020067 | 0.005031 | 4.672e-06 | 1.6975e-06 | 0.030636 | 0.030636 | 0.030636 | 0.97447 | -0.17925 | 0.9747 | -0.17757 | 11.3467
26 | 0.005241 | 0.0013122 | -0.0052407 | -0.0013122 | 3.5058e-07 | 2.6562e-08 | 0.0080211 | 0.0080212 | 0.0080212 | 0.97222 | -0.19546 | 0.97215 | -0.19594 | 2.9708
27 | -0.028817 | -0.0072239 | 0.028836 | 0.0072312 | 1.9561e-05 | 7.3013e-06 | 0.042964 | 0.042964 | 0.042964 | 0.99804 | -0.013697 | 0.99874 | -0.008799 | 15.9128
28 | -0.029441 | -0.0073827 | 0.029441 | 0.0073828 | 7.871e-08 | 2.9415e-08 | 0.043865 | 0.043865 | 0.043865 | 0.99874 | -0.008799 | 0.99874 | -0.0087797 | 16.2463
29 | -0.03189 | -0.0079966 | 0.031899 | 0.008 | 9.1041e-06 | 3.417e-06 | 0.047514 | 0.047514 | 0.047514 | 0.99874 | -0.0087797 | 0.99904 | -0.0067202 | 17.5978
30 | -0.00091729 | -0.00022989 | 0.00091735 | 0.00022927 | 6.4188e-08 | -6.1957e-07 | 0.0014056 | 0.0014054 | 0.0014056 | 0.97107 | -0.20374 | 0.97114 | -0.20323 | 0.52059
31 | -0.0032632 | -0.000816 | 0.0032633 | 0.00081595 | 1.29e-07 | -5.2732e-08 | 0.0049993 | 0.0049993 | 0.0049993 | 0.97114 | -0.20323 | 0.97118 | -0.20294 | 1.8516
32 | 0.0023459 | 0.00058673 | -0.0023457 | -0.00058689 | 1.3731e-07 | -1.5796e-07 | 0.003594 | 0.0035941 | 0.0035941 | 0.97114 | -0.20323 | 0.97108 | -0.20366 | 1.3311
33 | -0.0041845 | -0.0010468 | 0.0041848 | 0.0010468 | 3.0435e-07 | -2.9807e-08 | 0.0064107 | 0.0064107 | 0.0064107 | 0.97118 | -0.20294 | 0.97125 | -0.20242 | 2.3743
34 | 0.0011082 | 0.00027673 | -0.0011081 | -0.00027708 | 5.3764e-08 | -3.491e-07 | 0.0016977 | 0.0016978 | 0.0016978 | 0.97108 | -0.20366 | 0.97103 | -0.20401 | 0.62883
35 | -0.0084326 | -0.0021112 | 0.0084332 | 0.0021114 | 6.3086e-07 | 1.6751e-07 | 0.012912 | 0.012912 | 0.012912 | 0.97174 | -0.19889 | 0.97181 | -0.19835 | 4.7822
36 | 0.0069572 | 0.0017415 | -0.0069538 | -0.0017408 | 3.3882e-06 | 7.107e-07 | 0.010653 | 0.010653 | 0.010653 | 0.97174 | -0.19889 | 0.97125 | -0.20242 | 3.9455
37 | -0.011508 | -0.0028821 | 0.011515 | 0.0028842 | 6.4515e-06 | 2.0685e-06 | 0.017621 | 0.017621 | 0.017621 | 0.97181 | -0.19835 | 0.97238 | -0.19429 | 6.5262
38 | -0.020232 | -0.0050687 | 0.020245 | 0.0050737 | 1.3947e-05 | 5.0749e-06 | 0.030959 | 0.030959 | 0.030959 | 0.97238 | -0.19429 | 0.97307 | -0.18931 | 11.4664
39 | 0.0087166 | 0.0021845 | -0.0087162 | -0.0021843 | 4.2609e-07 | 1.1628e-07 | 0.013339 | 0.013339 | 0.013339 | 0.97238 | -0.19429 | 0.97233 | -0.19465 | 4.9403
40 | 0.0011081 | 0.00027708 | -0.001108 | -0.00027769 | 9.5467e-08 | -6.1966e-07 | 0.0016978 | 0.0016981 | 0.0016981 | 0.97103 | -0.20401 | 0.97094 | -0.20463 | 0.62892
41 | -0.021984 | -0.0055094 | 0.021999 | 0.0055151 | 1.5471e-05 | 5.6776e-06 | 0.033618 | 0.033618 | 0.033618 | 0.97307 | -0.18931 | 0.97377 | -0.18423 | 12.451
42 | 0.0062452 | 0.0015651 | -0.0062438 | -0.0015648 | 1.3577e-06 | 2.2681e-07 | 0.0095574 | 0.0095575 | 0.0095575 | 0.97233 | -0.19465 | 0.97211 | -0.19622 | 3.5398
43 | -0.024362 | -0.0061071 | 0.024373 | 0.0061115 | 1.182e-05 | 4.3759e-06 | 0.037227 | 0.037227 | 0.037227 | 0.97377 | -0.18423 | 0.97426 | -0.18073 | 13.7879
44 | 0.0035296 | 0.00088458 | -0.0035296 | -0.0008846 | 4.9277e-08 | -1.4587e-08 | 0.0054028 | 0.0054028 | 0.0054028 | 0.97211 | -0.19622 | 0.9721 | -0.19632 | 2.001
45 | 0.0075421 | 0.0018897 | -0.0075408 | -0.0018894 | 1.3181e-06 | 3.0167e-07 | 0.011418 | 0.011419 | 0.011419 | 0.98285 | -0.11959 | 0.98267 | -0.12086 | 4.2291
46 | -0.0075421 | -0.0018897 | 0.0075459 | 0.0018905 | 3.746e-06 | 8.5694e-07 | 0.011418 | 0.011418 | 0.011418 | 0.98285 | -0.11959 | 0.98335 | -0.116 | 4.2291
47 | 0.0062032 | 0.0015541 | -0.0062013 | -0.0015538 | 1.8903e-06 | 2.9221e-07 | 0.009393 | 0.0093932 | 0.0093932 | 0.98267 | -0.12086 | 0.98236 | -0.12306 | 3.4789
48 | -0.0083618 | -0.002095 | 0.008362 | 0.0020951 | 1.7796e-07 | 4.5846e-08 | 0.012653 | 0.012653 | 0.012653 | 0.98335 | -0.116 | 0.98338 | -0.11585 | 4.6862
49 | 0.0040349 | 0.0010109 | -0.0040343 | -0.001011 | 5.8542e-07 | -9.2782e-08 | 0.0061116 | 0.0061118 | 0.0061118 | 0.98236 | -0.12306 | 0.98222 | -0.12411 | 2.2636
50 | -0.066358 | -0.016698 | 0.066473 | 0.016743 | 0.00011525 | 4.4095e-05 | 0.10043 | 0.10043 | 0.10043 | 0.98338 | -0.11585 | 0.98514 | -0.10343 | 37.198
51 | 0.057996 | 0.014603 | -0.057879 | -0.014559 | 0.00011702 | 4.4698e-05 | 0.087782 | 0.087782 | 0.087782 | 0.98338 | -0.11585 | 0.98133 | -0.13032 | 32.5118
52 | 0.014042 | 0.0035195 | -0.014038 | -0.0035181 | 4.289e-06 | 1.4561e-06 | 0.021238 | 0.021238 | 0.021238 | 0.98388 | -0.11277 | 0.98357 | -0.11498 | 7.8658
53 | -0.015049 | -0.0037718 | 0.015052 | 0.0037728 | 2.8502e-06 | 9.8422e-07 | 0.02276 | 0.02276 | 0.02276 | 0.98388 | -0.11277 | 0.98408 | -0.11141 | 8.4297
54 | 0.01262 | 0.0031627 | -0.01262 | -0.0031625 | 6.4217e-07 | 2.1116e-07 | 0.019093 | 0.019093 | 0.019093 | 0.98357 | -0.11498 | 0.98352 | -0.11535 | 7.0714
55 | -0.016539 | -0.0041455 | 0.016543 | 0.0041468 | 3.643e-06 | 1.2825e-06 | 0.025009 | 0.025009 | 0.025009 | 0.98408 | -0.11141 | 0.9843 | -0.10982 | 9.2626
56 | 0.011338 | 0.0028412 | -0.011334 | -0.0028402 | 3.3439e-06 | 1.0551e-06 | 0.017153 | 0.017153 | 0.017153 | 0.98352 | -0.11535 | 0.98322 | -0.11748 | 6.3531
57 | -0.017979 | -0.0045068 | 0.017987 | 0.0045094 | 7.4175e-06 | 2.6483e-06 | 0.02718 | 0.02718 | 0.02718 | 0.9843 | -0.10982 | 0.98472 | -0.10684 | 10.0667
58 | 0.010016 | 0.0025096 | -0.010013 | -0.0025088 | 2.8054e-06 | 8.3089e-07 | 0.015157 | 0.015158 | 0.015158 | 0.98322 | -0.11748 | 0.98294 | -0.1195 | 5.6139
59 | -0.01921 | -0.004816 | 0.019212 | 0.0048168 | 2.2634e-06 | 8.1578e-07 | 0.029029 | 0.029029 | 0.029029 | 0.98472 | -0.10684 | 0.98484 | -0.10599 | 10.7514
60 | 0.0081825 | 0.0020501 | -0.0081822 | -0.00205 | 3.7152e-07 | 9.371e-08 | 0.012387 | 0.012387 | 0.012387 | 0.98294 | -0.1195 | 0.98289 | -0.11983 | 4.5877
61 | -0.021435 | -0.0053739 | 0.021444 | 0.0053772 | 8.9677e-06 | 3.2747e-06 | 0.032387 | 0.032387 | 0.032387 | 0.98484 | -0.10599 | 0.98526 | -0.10297 | 11.9952
62 | 0.057023 | 0.014344 | -0.056996 | -0.014334 | 2.7607e-05 | 1.0543e-05 | 0.086485 | 0.086485 | 0.086485 | 0.98133 | -0.13032 | 0.98084 | -0.13379 | 32.0314
63 | 0.056996 | 0.014334 | -0.056902 | -0.014298 | 9.3301e-05 | 3.5633e-05 | 0.086485 | 0.086485 | 0.086485 | 0.98084 | -0.13379 | 0.97918 | -0.14555 | 32.0315
64 | -0.068246 | -0.017187 | 0.068261 | 0.017193 | 1.5205e-05 | 5.819e-06 | 0.10311 | 0.10311 | 0.10311 | 0.98514 | -0.10343 | 0.98536 | -0.10183 | 38.1898
65 | 0.056084 | 0.014093 | -0.055966 | -0.014048 | 0.00011784 | 4.4998e-05 | 0.085241 | 0.085241 | 0.085241 | 0.97918 | -0.14555 | 0.97706 | -0.16068 | 31.5708
66 | -0.069509 | -0.017506 | 0.069654 | 0.017561 | 0.00014505 | 5.5519e-05 | 0.105 | 0.105 | 0.105 | 0.98536 | -0.10183 | 0.98748 | -0.086939 | 38.8879
67 | 0.055047 | 0.013818 | -0.055046 | -0.013817 | 9.0898e-07 | 3.4701e-07 | 0.083842 | 0.083842 | 0.083842 | 0.97706 | -0.16068 | 0.97704 | -0.1608 | 31.0525
68 | -0.07364 | -0.01856 | 0.073656 | 0.018566 | 1.6143e-05 | 6.182e-06 | 0.111 | 0.111 | 0.111 | 0.98748 | -0.086939 | 0.98771 | -0.085373 | 41.1123
69 | 0.054022 | 0.013561 | -0.053966 | -0.013539 | 5.6454e-05 | 2.1546e-05 | 0.082282 | 0.082282 | 0.082282 | 0.97704 | -0.1608 | 0.97599 | -0.16834 | 30.4749
70 | 0.0072062 | 0.0018054 | -0.0072054 | -0.0018052 | 8.283e-07 | 1.7723e-07 | 0.010909 | 0.010909 | 0.010909 | 0.98289 | -0.11983 | 0.98278 | -0.12066 | 4.0405
71 | -0.023565 | -0.0059088 | 0.02358 | 0.0059145 | 1.5458e-05 | 5.6962e-06 | 0.03559 | 0.03559 | 0.03559 | 0.98526 | -0.10297 | 0.98593 | -0.098238 | 13.1816
72 | -0.024965 | -0.0062616 | 0.024975 | 0.0062653 | 1.0014e-05 | 3.7073e-06 | 0.037681 | 0.03768 | 0.037681 | 0.98593 | -0.098238 | 0.98634 | -0.095347 | 13.9557
73 | 0.002931 | 0.00073414 | -0.0029308 | -0.00073424 | 1.5498e-07 | -1.0252e-07 | 0.0044216 | 0.0044217 | 0.0044217 | 0.98634 | -0.095347 | 0.98628 | -0.095729 | 1.6377
74 | -0.027906 | -0.0069994 | 0.027942 | 0.0070127 | 3.5614e-05 | 1.3286e-05 | 0.042102 | 0.042102 | 0.042102 | 0.98634 | -0.095347 | 0.98764 | -0.086154 | 15.5934
75 | 0.0014784 | 0.00037024 | -0.0014784 | -0.00037052 | 7.3579e-08 | -2.7415e-07 | 0.0022304 | 0.0022306 | 0.0022306 | 0.98628 | -0.095729 | 0.98623 | -0.096089 | 0.82613
76 | -0.02942 | -0.0073831 | 0.029422 | 0.0073838 | 1.8319e-06 | 6.8545e-07 | 0.044329 | 0.044329 | 0.044329 | 0.98764 | -0.086154 | 0.9877 | -0.085705 | 16.418
77 | -0.030892 | -0.0077523 | 0.03094 | 0.0077703 | 4.7857e-05 | 1.7953e-05 | 0.046544 | 0.046544 | 0.046544 | 0.9877 | -0.085705 | 0.98928 | -0.074561 | 17.2385
78 | -0.025739 | -0.0064537 | 0.025749 | 0.0064574 | 1.0181e-05 | 3.7842e-06 | 0.039312 | 0.039312 | 0.039312 | 0.97426 | -0.18073 | 0.97466 | -0.17788 | 14.5601
79 | -0.027819 | -0.0069763 | 0.027838 | 0.0069833 | 1.875e-05 | 7.0036e-06 | 0.042473 | 0.042473 | 0.042473 | 0.97466 | -0.17788 | 0.97534 | -0.17302 | 15.7308
80 | -0.030693 | -0.0076988 | 0.030713 | 0.0077063 | 1.9946e-05 | 7.4893e-06 | 0.046829 | 0.046829 | 0.046829 | 0.97534 | -0.17302 | 0.97599 | -0.16834 | 17.3439
81 | 0.023253 | 0.0058329 | -0.023229 | -0.005824 | 2.3954e-05 | 8.8317e-06 | 0.035454 | 0.035454 | 0.035454 | 0.97599 | -0.16834 | 0.97495 | -0.17577 | 13.131
82 | -0.022107 | -0.0055421 | 0.022112 | 0.0055441 | 5.5137e-06 | 2.0239e-06 | 0.033749 | 0.033749 | 0.033749 | 0.9747 | -0.17757 | 0.97495 | -0.17577 | 12.4998
83 | -0.12006 | -0.030283 | 0.12013 | 0.030312 | 7.5622e-05 | 2.8892e-05 | 0.17994 | 0.17994 | 0.17994 | 0.99319 | -0.047138 | 0.99383 | -0.04265 | 33.3225
84 | 0.11881 | 0.029971 | -0.11868 | -0.029923 | 0.00012535 | 4.7886e-05 | 0.17807 | 0.17807 | 0.17807 | 0.99319 | -0.047138 | 0.99211 | -0.054669 | 32.9764
85 | -0.12117 | -0.030572 | 0.12132 | 0.030629 | 0.00014872 | 5.6824e-05 | 0.18149 | 0.18149 | 0.18149 | 0.99383 | -0.04265 | 0.99509 | -0.033913 | 33.6096
86 | 0.04048 | 0.010174 | -0.040479 | -0.010173 | 1.8345e-06 | 6.9528e-07 | 0.060725 | 0.060725 | 0.060725 | 0.99211 | -0.054669 | 0.99206 | -0.054994 | 22.4908
87 | 0.078204 | 0.019749 | -0.078064 | -0.019696 | 0.00014018 | 5.3073e-05 | 0.11735 | 0.11735 | 0.11735 | 0.99211 | -0.054669 | 0.99027 | -0.067444 | 21.731
88 | 0.0023276 | 0.00058316 | -0.0023275 | -0.00058333 | 1.2722e-07 | -1.6968e-07 | 0.0034806 | 0.0034807 | 0.0034807 | 0.99509 | -0.033913 | 0.99503 | -0.034308 | 1.2891
89 | -0.12364 | -0.031212 | 0.12371 | 0.031237 | 6.5598e-05 | 2.507e-05 | 0.18497 | 0.18497 | 0.18497 | 0.99509 | -0.033913 | 0.99563 | -0.030138 | 34.2542
90 | 0.038417 | 0.0096567 | -0.038395 | -0.0096481 | 2.2656e-05 | 8.5729e-06 | 0.057633 | 0.057633 | 0.057633 | 0.99206 | -0.054994 | 0.99146 | -0.059232 | 21.3457
91 | 0.076228 | 0.019236 | -0.07621 | -0.019229 | 1.7943e-05 | 6.873e-06 | 0.11459 | 0.11459 | 0.11459 | 0.99027 | -0.067444 | 0.99003 | -0.069122 | 42.4403
92 | 0.0034801 | 0.00087164 | -0.0034798 | -0.00087175 | 2.8025e-07 | -1.0811e-07 | 0.005201 | 0.0052011 | 0.0052011 | 0.99563 | -0.030138 | 0.99555 | -0.03072 | 1.9263
93 | -0.12719 | -0.032108 | 0.1274 | 0.032189 | 0.0002108 | 8.0592e-05 | 0.19017 | 0.19017 | 0.19017 | 0.99563 | -0.030138 | 0.99734 | -0.018359 | 35.2173
94 | 0.036653 | 0.0092115 | -0.036633 | -0.0092043 | 1.9154e-05 | 7.2361e-06 | 0.055019 | 0.055019 | 0.055019 | 0.99146 | -0.059232 | 0.99092 | -0.062988 | 20.3773
95 | 0.074759 | 0.018865 | -0.074589 | -0.0188 | 0.00017013 | 6.5157e-05 | 0.11241 | 0.11241 | 0.11241 | 0.99003 | -0.069122 | 0.98771 | -0.085373 | 41.6328
96 | 0.0021699 | 0.00054344 | -0.0021698 | -0.00054362 | 1.1049e-07 | -1.7639e-07 | 0.0032431 | 0.0032432 | 0.0032432 | 0.99555 | -0.03072 | 0.9955 | -0.031088 | 1.2012
97 | -0.12798 | -0.032335 | 0.12804 | 0.032355 | 5.2951e-05 | 2.0244e-05 | 0.19104 | 0.19104 | 0.19104 | 0.99734 | -0.018359 | 0.99776 | -0.015419 | 35.3777
98 | 0.035377 | 0.0088895 | -0.035337 | -0.0088741 | 4.0725e-05 | 1.5366e-05 | 0.053133 | 0.053133 | 0.053133 | 0.99092 | -0.062988 | 0.98974 | -0.07127 | 19.6788
99 | -0.0010716 | -0.00026856 | 0.0010716 | 0.00026838 | 2.2551e-08 | -1.7448e-07 | 0.0016017 | 0.0016017 | 0.0016017 | 0.99548 | -0.031241 | 0.9955 | -0.031088 | 0.59324
100 | 0.0072054 | 0.0018052 | -0.0072044 | -0.001805 | 9.5103e-07 | 2.0354e-07 | 0.010909 | 0.010909 | 0.010909 | 0.98278 | -0.12066 | 0.98264 | -0.12162 | 4.0405
101 | 0.0061315 | 0.0015361 | -0.0061314 | -0.0015361 | 6.0829e-08 | 9.0711e-09 | 0.0092847 | 0.0092847 | 0.0092847 | 0.98264 | -0.12162 | 0.98263 | -0.12169 | 3.4388
102 | 0.0039389 | 0.00098662 | -0.0039386 | -0.00098668 | 3.0296e-07 | -5.634e-08 | 0.0059645 | 0.0059646 | 0.0059646 | 0.98263 | -0.12169 | 0.98255 | -0.12225 | 2.2091
103 | 0.0033907 | 0.00084936 | -0.0033905 | -0.00084942 | 1.4304e-07 | -5.5092e-08 | 0.0051348 | 0.0051349 | 0.0051349 | 0.98255 | -0.12225 | 0.98251 | -0.12255 | 1.9018
104 | -0.033623 | -0.0084426 | 0.033638 | 0.0084484 | 1.5385e-05 | 5.7933e-06 | 0.050579 | 0.050579 | 0.050579 | 0.98928 | -0.074561 | 0.98974 | -0.07127 | 18.733
105 | 0.0037819 | 0.0009466 | -0.0037819 | -0.00094661 | 6.8957e-08 | -1.4372e-08 | 0.0057883 | 0.0057883 | 0.0057883 | 0.97215 | -0.19594 | 0.97213 | -0.19608 | 2.1438
106 | 0.0031508 | 0.00078844 | -0.0031501 | -0.00078876 | 6.6783e-07 | -3.1358e-07 | 0.0048223 | 0.0048226 | 0.0048226 | 0.97213 | -0.19608 | 0.97192 | -0.19761 | 1.7861
107 | 0.0031501 | 0.00078876 | -0.0031497 | -0.00078893 | 3.7649e-07 | -1.7665e-07 | 0.0048226 | 0.0048227 | 0.0048227 | 0.97192 | -0.19761 | 0.9718 | -0.19847 | 1.7862
108 | 0.0031497 | 0.00078893 | -0.0031495 | -0.00078903 | 2.0258e-07 | -9.5011e-08 | 0.0048227 | 0.0048227 | 0.0048227 | 0.9718 | -0.19847 | 0.97173 | -0.19894 | 1.7862
109 | -0.033663 | -0.0084421 | 0.03368 | 0.0084484 | 1.6567e-05 | 6.2335e-06 | 0.050141 | 0.050141 | 0.050141 | 0.99904 | -0.0067202 | 0.99955 | -0.0031715 | 18.5709
110 | -0.034285 | -0.0085999 | 0.0343 | 0.0086056 | 1.5085e-05 | 5.6804e-06 | 0.051042 | 0.051042 | 0.051042 | 0.99955 | -0.0031715 | 1 | 0 | 18.9043
111 | 0.12916 | 0.032675 | -0.12888 | -0.032568 | 0.00028032 | 0.00010718 | 0.19231 | 0.19231 | 0.19231 | 1 | 0 | 0.99776 | -0.015419 | 35.6123
112 | 0.0013861 | 0.00034708 | -0.001386 | -0.00034737 | 6.8062e-08 | -2.8728e-07 | 0.0020991 | 0.0020992 | 0.0020992 | 0.9825 | -0.12262 | 0.98245 | -0.12297 | 0.77749
113 | -0.0024829 | -0.00062197 | 0.0024829 | 0.00062194 | 2.2486e-08 | -2.3627e-08 | 0.0037603 | 0.0037603 | 0.0037603 | 0.9825 | -0.12262 | 0.98251 | -0.12255 | 1.3927
114 | -0.0015984 | -0.00040059 | 0.0015984 | 0.0004005 | 2.9403e-08 | -8.611e-08 | 0.0024477 | 0.0024477 | 0.0024477 | 0.97167 | -0.19938 | 0.97169 | -0.19925 | 0.90656
115 | -0.0015984 | -0.0004005 | 0.0015985 | 0.0004003 | 6.8978e-08 | -2.0204e-07 | 0.0024477 | 0.0024476 | 0.0024477 | 0.97169 | -0.19925 | 0.97173 | -0.19894 | 0.90655
116 | 0.0018132 | 0.00045432 | -0.0018132 | -0.00045443 | 4.7577e-08 | -1.0959e-07 | 0.0027469 | 0.002747 | 0.002747 | 0.98222 | -0.12411 | 0.98219 | -0.1243 | 1.0174

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16615 | 0.041753

## res_load
| p_mw | q_mvar
0 | 0.00052306 | 0.00013109
1 | 0.00043607 | 0.00010929
2 | 0.00068336 | 0.00017127
3 | 0.00097174 | 0.00024354
4 | 0.0018686 | 0.00046831
5 | 0.0019601 | 0.00049124
6 | 0.0018017 | 0.00045154
7 | 0.0019239 | 0.00048217
8 | 0.001294 | 0.00032432
9 | 0.0019525 | 0.00048935
10 | 0.0010502 | 0.00026321
11 | 0.0046468 | 0.0011646
12 | 0.0020271 | 0.00050803
13 | 0.0014338 | 0.00035935
14 | 0.0023076 | 0.00057834
15 | 0.0016056 | 0.00040241
16 | 0.0018662 | 0.00046771
17 | 0.0014259 | 0.00035737
18 | 0.0011964 | 0.00029984
19 | 0.0016229 | 0.00040675
20 | 0.0013059 | 0.00032728
21 | 0.0031496 | 0.00078936
22 | 0.0046762 | 0.001172
23 | 0.0018373 | 0.00046046
24 | 0.00060449 | 0.0001515
25 | 0.0024491 | 0.00061381
26 | 0.00091729 | 0.00022989
27 | 0.00092119 | 0.00023087
28 | 0.0012376 | 0.00031016
29 | 0.0014754 | 0.00036977
30 | 0.0030752 | 0.00077072
31 | 0.002769 | 0.00069397
32 | 0.001108 | 0.00027769
33 | 0.0017384 | 0.00043569
34 | 0.002471 | 0.00061929
35 | 0.0023622 | 0.00059201
36 | 0.0027142 | 0.00068024
37 | 0.0013376 | 0.00033525
38 | 0.00081589 | 0.00020448
39 | 0.0021664 | 0.00054295
40 | 0.0010067 | 0.00025229
41 | 0.0014177 | 0.00035532
42 | 0.0014874 | 0.00037277
43 | 0.0012821 | 0.00032131
44 | 0.0014362 | 0.00035994
45 | 0.0013188 | 0.00033052
46 | 0.0012234 | 0.0003066
47 | 0.0018302 | 0.00045869
48 | 0.0022227 | 0.00055705
49 | 0.00085544 | 0.00021439
50 | 0.0017729 | 0.00044434
51 | 0.00081863 | 0.00020517
52 | 0.0012482 | 0.00031282
53 | 0.00091883 | 0.00023028
54 | 0.0039856 | 0.00099888
55 | 0.001024 | 0.00025664
56 | 0.00097599 | 0.0002446
57 | 0.0021211 | 0.0005316
58 | 0.0013849 | 0.00034709
59 | 0.0014524 | 0.000364
60 | 0.0014779 | 0.00037039
61 | 0.0014784 | 0.00037052
62 | 0.0014706 | 0.00036856
63 | 0.0013652 | 0.00034216
64 | 0.0020703 | 0.00051888
65 | 0.002855 | 0.00071553
66 | 0.0020393 | 0.0005111
67 | 0.0011168 | 0.00027989
68 | 0.0012478 | 0.00031272
69 | 0.0010355 | 0.00025952
70 | 0.0020612 | 0.00051659
71 | 0.0018361 | 0.00046017
72 | 0.0023275 | 0.00058333
73 | 0.0017422 | 0.00043665
74 | 0.0014507 | 0.00036357
75 | 0.00131 | 0.00032831
76 | 0.00058085 | 0.00014558
77 | 0.001256 | 0.00031478
78 | 0.00093281 | 0.00023378
79 | 0.0010716 | 0.00026856
80 | 0.0010982 | 0.00027523
81 | 0.0010729 | 0.0002689
82 | 0.0021926 | 0.00054951
83 | 0.00054789 | 0.00013731
84 | 0.0026828 | 0.00067236
85 | 0.0016985 | 0.00042569
86 | 0.0014588 | 0.0003656
87 | 0.00063109 | 0.00015817
88 | 0.0017641 | 0.00044212
89 | 0.00060477 | 0.00015157
90 | 0.0018838 | 0.00047213
91 | 0.00084938 | 0.00021288
92 | 0.0010968 | 0.00027489
93 | 0.001386 | 0.00034737
94 | 0.00090764 | 0.00022748
95 | 0.0015984 | 0.00040059
96 | 0.0015511 | 0.00038873
97 | 0.0022211 | 0.00055665
98 | 0.0035296 | 0.0008846
99 | 0.0018132 | 0.00045443

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1