## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1004-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1004-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1004-13_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1004-13_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1004-13_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1004-13_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1004-13_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1004-13_0_3_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_1004-13_0_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1004-13_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1004-13_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1004-13_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1004-13_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1004-13_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1004-13_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1004-13_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1004-13_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1004-13_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1004-13_0_3_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1004-13_0_3_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1004-13_0_3_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_1004-13_0_3_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1004-13_0_3_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_1004-13_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1004-13_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1004-13_0_3_node_48 | 0.4 | n |  | TRUE
26 | bus_LV_1004-13_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1004-13_0_3_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1004-13_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1004-13_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1004-13_0_3_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_1004-13_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_1004-13_0_3_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_1004-13_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_1004-13_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1004-13_0_3_node_47 | 0.4 | n |  | TRUE
36 | bus_LV_1004-13_0_3_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1004-13_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1004-13_0_3_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1004-13_0_3_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1004-13_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1004-13_0_3_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_1004-13_0_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_1004-13_0_3_node_45 | 0.4 | n |  | TRUE
44 | bus_MV_126_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1004-13_0_3_load_0 | 0 | 0.0051349 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1004-13_0_3_load_3 | 3 | 0.0020549 | 0.000515 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1004-13_0_3_load_11 | 6 | 0.0014186 | 0.00035554 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1004-13_0_3_load_41 | 7 | 0.0036072 | 0.00090405 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1004-13_0_3_load_16 | 8 | 0.0023166 | 0.0005806 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1004-13_0_3_load_13 | 10 | 0.005677 | 0.0014228 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1004-13_0_3_load_12 | 12 | 0.0070505 | 0.001767 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1004-13_0_3_load_15 | 13 | 0.059458 | 0.014902 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1004-13_0_3_load_14 | 14 | 0.080506 | 0.020177 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1004-13_0_3_load_18 | 17 | 0.0036687 | 0.00091945 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1004-13_0_3_load_25 | 18 | 0.0037887 | 0.00094954 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1004-13_0_3_load_42 | 20 | 0.0013379 | 0.0003353 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1004-13_0_3_load_21 | 21 | 0.0029572 | 0.00074115 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1004-13_0_3_load_27 | 24 | 0.0017379 | 0.00043555 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1004-13_0_3_load_26 | 26 | 0.0031953 | 0.00080083 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1004-13_0_3_load_43 | 27 | 0.0010661 | 0.00026719 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1004-13_0_3_load_19 | 28 | 0.00089662 | 0.00022472 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1004-13_0_3_load_40 | 30 | 0.0049849 | 0.0012493 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1004-13_0_3_load_37 | 31 | 0.0032529 | 0.00081524 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1004-13_0_3_load_38 | 33 | 0.00050003 | 0.00012532 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1004-13_0_3_load_47 | 35 | 0.004683 | 0.0011737 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1004-13_0_3_load_28 | 36 | 0.0071079 | 0.0017814 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1004-13_0_3_load_32 | 38 | 0.0029263 | 0.0007334 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1004-13_0_3_load_34 | 39 | 0.0014251 | 0.00035715 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1004-13_0_3_load_39 | 41 | 0.0020061 | 0.00050278 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1004-13_0_3_load_44 | 42 | 0.002843 | 0.00071253 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1004-13_0_3_load_45 | 43 | 0.0010077 | 0.00025255 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1004-13_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0089998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1004-13_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1004-13_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.013489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1004-13_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.037488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1004-13_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.005106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1004-13_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.0073965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1004-13_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.033827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1004-13_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.017074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1004-13_0_3_line_8 | NAYY 4x150 SE | 5 | 18 | 0.01253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1004-13_0_3_line_9 | NAYY 4x150 SE | 6 | 19 | 0.034598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1004-13_0_3_line_10 | NAYY 4x150 SE | 7 | 20 | 0.060467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1004-13_0_3_line_11 | NAYY 4x150 SE | 8 | 23 | 0.010769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1004-13_0_3_line_12 | NAYY 4x150 SE | 9 | 10 | 0.047242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1004-13_0_3_line_13 | NAYY 4x150 SE | 9 | 11 | 0.050957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1004-13_0_3_line_14 | NAYY 4x150 SE | 9 | 12 | 0.012555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1004-13_0_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.013038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1004-13_0_3_line_16 | NAYY 4x150 SE | 11 | 14 | 0.034094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1004-13_0_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.021207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1004-13_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.098405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1004-13_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.019803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1004-13_0_3_line_20 | NAYY 4x150 SE | 17 | 23 | 0.020008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1004-13_0_3_line_21 | NAYY 4x150 SE | 18 | 26 | 0.026365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1004-13_0_3_line_22 | NAYY 4x150 SE | 19 | 27 | 0.025859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1004-13_0_3_line_23 | NAYY 4x150 SE | 19 | 25 | 0.010892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1004-13_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.0083921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1004-13_0_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.0081587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1004-13_0_3_line_26 | NAYY 4x150 SE | 22 | 34 | 0.017889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1004-13_0_3_line_27 | NAYY 4x150 SE | 23 | 28 | 0.03557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1004-13_0_3_line_28 | NAYY 4x150 SE | 23 | 29 | 0.071345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1004-13_0_3_line_29 | NAYY 4x150 SE | 24 | 25 | 0.00755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1004-13_0_3_line_30 | NAYY 4x150 SE | 25 | 35 | 0.015412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1004-13_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.045816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1004-13_0_3_line_32 | NAYY 4x150 SE | 29 | 31 | 0.0131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1004-13_0_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.036439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1004-13_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.033224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1004-13_0_3_line_35 | NAYY 4x150 SE | 32 | 40 | 0.0082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1004-13_0_3_line_36 | NAYY 4x150 SE | 33 | 41 | 0.038349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1004-13_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.031773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1004-13_0_3_line_38 | NAYY 4x150 SE | 35 | 43 | 0.044737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1004-13_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.016454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1004-13_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.018371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1004-13_0_3_line_41 | NAYY 4x150 SE | 39 | 40 | 0.027804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1004-13_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.0047218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1004-13_0_3_trafo_7 | 0.25 MVA 20/0.4 kV | 44 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2643983.6641 | 1192727.6682 | 2643982.1059 | 1192736.5321
1 | 2643979.6629 | 1192750.4291 | 2643982.1059 | 1192736.5321
2 | 2643983.6641 | 1192727.6682 | 2643996.7133 | 1192731.0839
3 | 2643983.6641 | 1192727.6682 | 2643986.9952 | 1192712.084 | 2643982.8836 | 1192711.4868 | 2643977.7354 | 1192710.882 | 2643965.587 | 1192709.6255
4 | 2643979.6629 | 1192750.4291 | 2643983.4564 | 1192753.8589
5 | 2643979.6629 | 1192750.4291 | 2643978.3453 | 1192757.7074
6 | 2643996.7133 | 1192731.0839 | 2644000.051 | 1192731.9576 | 2644003.5623 | 1192732.3058 | 2644007.3217 | 1192732.0889 | 2644011.7865 | 1192731.299 | 2644029.4261 | 1192725.563
7 | 2643965.587 | 1192709.6255 | 2643962.2574 | 1192709.4454 | 2643954.6279 | 1192709.3894 | 2643948.5204 | 1192709.2077
8 | 2643983.4564 | 1192753.8589 | 2643984.7285 | 1192755.0133 | 2643987.6054 | 1192765.4357
9 | 2643975.4006 | 1192792.1209 | 2643976.628 | 1192767.1939 | 2643978.3453 | 1192757.7074
10 | 2644029.4261 | 1192725.563 | 2644032.0798 | 1192724.7001 | 2644039.373 | 1192722.8193 | 2644088.618 | 1192713.3641
11 | 2643937.7558 | 1192708.8875 | 2643948.5204 | 1192709.2077
12 | 2644031.76 | 1192596.1712 | 2644038.8695 | 1192597.5131 | 2644068.3748 | 1192599.7425 | 2644078.7045 | 1192601.0888
13 | 2644031.76 | 1192596.1712 | 2644030.5626 | 1192600.4092 | 2644024.5788 | 1192617.0188 | 2644022.3314 | 1192623.0723 | 2644043.3262 | 1192630.9977
14 | 2644031.76 | 1192596.1712 | 2644034.3658 | 1192583.8894
15 | 2644043.3262 | 1192630.9977 | 2644049.1596 | 1192630.6849 | 2644054.0125 | 1192631.0319 | 2644056.313 | 1192631.4048
16 | 2644043.3262 | 1192630.9977 | 2644064.0392 | 1192643.0234 | 2644065.1042 | 1192644.3542 | 2644065.5208 | 1192645.7469 | 2644065.4183 | 1192647.2358 | 2644064.6097 | 1192649.3977 | 2644063.0536 | 1192652.1754
17 | 2644054.1283 | 1192671.2327 | 2644054.6373 | 1192668.3571 | 2644055.5419 | 1192665.5844 | 2644063.0536 | 1192652.1754
18 | 2643974.2295 | 1192697.3377 | 2643977.4456 | 1192697.4058 | 2643981.83 | 1192697.1934 | 2643985.3321 | 1192696.73 | 2643987.5168 | 1192696.0901 | 2643990.191 | 1192695.2204 | 2643992.0581 | 1192694.2336 | 2643993.7986 | 1192692.8345 | 2643995.6205 | 1192690.7356 | 2643998.1141 | 1192687.4743 | 2643999.4438 | 1192684.9383 | 2644001.096 | 1192681.0483 | 2644006.152 | 1192667.2444 | 2644021.5853 | 1192672.6942 | 2644026.0978 | 1192673.728 | 2644032.8446 | 1192673.5775 | 2644054.1283 | 1192671.2327
19 | 2643974.2295 | 1192697.3377 | 2643964.9165 | 1192697.1359 | 2643961.2876 | 1192697.2315 | 2643957.5036 | 1192697.6818 | 2643954.5335 | 1192698.3603
20 | 2643937.7558 | 1192708.8875 | 2643942.1226 | 1192704.8395 | 2643946.0902 | 1192702.2116 | 2643950.4823 | 1192699.9204 | 2643954.5335 | 1192698.3603
21 | 2643987.6054 | 1192765.4357 | 2643990.5493 | 1192776.1011 | 2644002.3771 | 1192785.8082
22 | 2643975.4006 | 1192792.1209 | 2643971.4501 | 1192784.1208 | 2643962.0212 | 1192770.0509
23 | 2643975.4006 | 1192792.1209 | 2643979.1605 | 1192797.0179 | 2643983.8728 | 1192796.7746
24 | 2643957.4792 | 1192763.2734 | 2643955.7075 | 1192760.6256 | 2643955.385 | 1192755.4294
25 | 2643957.4792 | 1192763.2734 | 2643962.0212 | 1192770.0509
26 | 2643957.4792 | 1192763.2734 | 2643947.4504 | 1192767.1464 | 2643948.0629 | 1192769.8968 | 2643948.5063 | 1192771.79 | 2643949.0074 | 1192774.1394
27 | 2643937.7558 | 1192708.8875 | 2643933.0001 | 1192702.5713 | 2643931.1556 | 1192674.9692
28 | 2643890.1479 | 1192760.7226 | 2643891.995 | 1192755.1775 | 2643894.469 | 1192750.4264 | 2643897.2438 | 1192746.2221 | 2643901.1995 | 1192742.1044 | 2643927.1178 | 1192718.8928 | 2643937.7558 | 1192708.8875
29 | 2643983.8728 | 1192796.7746 | 2643983.8117 | 1192794.7174 | 2643983.5493 | 1192789.2317
30 | 2643983.8728 | 1192796.7746 | 2643987.87 | 1192798.4159 | 2643991.4362 | 1192800.6322 | 2643997.3401 | 1192804.1887
31 | 2643890.1479 | 1192760.7226 | 2643889.633 | 1192767.5226 | 2643889.3789 | 1192780.35 | 2643889.87 | 1192791.3375 | 2643890.5452 | 1192806.4907
32 | 2643890.1479 | 1192760.7226 | 2643877.1096 | 1192761.9919
33 | 2643892.1673 | 1192842.8939 | 2643890.5452 | 1192806.4907
34 | 2643877.1096 | 1192761.9919 | 2643868.0581 | 1192762.873 | 2643858.8207 | 1192770.0538 | 2643847.1774 | 1192774.4042
35 | 2643892.1673 | 1192842.8939 | 2643883.99 | 1192843.7678
36 | 2643825.3324 | 1192801.0112 | 2643825.6112 | 1192796.0028 | 2643825.8565 | 1192790.6016 | 2643828.0455 | 1192785.2147 | 2643835.1404 | 1192782.2761 | 2643845.514 | 1192775.0258 | 2643847.1774 | 1192774.4042
37 | 2643949.0074 | 1192774.1394 | 2643955.7833 | 1192772.0991 | 2643957.796 | 1192772.0361 | 2643959.5584 | 1192772.8495 | 2643966.2506 | 1192782.2038 | 2643967.2009 | 1192784.6121 | 2643967.7207 | 1192790.6414 | 2643967.7471 | 1192791.2407
38 | 2643997.3401 | 1192804.1887 | 2643997.3401 | 1192804.1887 | 2643989.6825 | 1192816.2613 | 2643991.0336 | 1192820.1401 | 2643999.0775 | 1192824.9907 | 2644006.5365 | 1192825.4013 | 2644009.9229 | 1192827.1827 | 2644011.8941 | 1192832.4701
39 | 2643968.4721 | 1192807.6786 | 2643967.7471 | 1192791.2407
40 | 2643968.4721 | 1192807.6786 | 2643950.1452 | 1192808.9544
41 | 2643883.99 | 1192843.7678 | 2643867.626 | 1192844.7151 | 2643867.1137 | 1192833.314
42 | 2644013.5436 | 1192836.8945 | 2644011.8941 | 1192832.4701

## bus_geodata
| x | y | coords
0 | 2643982.1059 | 1192736.5321
1 | 2643983.6641 | 1192727.6682
2 | 2643979.6629 | 1192750.4291
3 | 2643996.7133 | 1192731.0839
4 | 2643965.587 | 1192709.6255
5 | 2643983.4564 | 1192753.8589
6 | 2643978.3453 | 1192757.7074
7 | 2644029.4261 | 1192725.563
8 | 2643948.5204 | 1192709.2077
9 | 2644031.76 | 1192596.1712
10 | 2644078.7045 | 1192601.0888
11 | 2644043.3262 | 1192630.9977
12 | 2644034.3658 | 1192583.8894
13 | 2644056.313 | 1192631.4048
14 | 2644063.0536 | 1192652.1754
15 | 2644054.1283 | 1192671.2327
16 | 2643974.2295 | 1192697.3377
17 | 2643954.5335 | 1192698.3603
18 | 2643987.6054 | 1192765.4357
19 | 2643975.4006 | 1192792.1209
20 | 2644088.618 | 1192713.3641
21 | 2643955.385 | 1192755.4294
22 | 2643957.4792 | 1192763.2734
23 | 2643937.7558 | 1192708.8875
24 | 2643983.5493 | 1192789.2317
25 | 2643983.8728 | 1192796.7746
26 | 2644002.3771 | 1192785.8082
27 | 2643962.0212 | 1192770.0509
28 | 2643931.1556 | 1192674.9692
29 | 2643890.1479 | 1192760.7226
30 | 2643890.5452 | 1192806.4907
31 | 2643877.1096 | 1192761.9919
32 | 2643892.1673 | 1192842.8939
33 | 2643847.1774 | 1192774.4042
34 | 2643949.0074 | 1192774.1394
35 | 2643997.3401 | 1192804.1887
36 | 2643967.7471 | 1192791.2407
37 | 2643968.4721 | 1192807.6786
38 | 2643950.1452 | 1192808.9544
39 | 2643867.1137 | 1192833.314
40 | 2643883.99 | 1192843.7678
41 | 2643825.3324 | 1192801.0112
42 | 2644013.5436 | 1192836.8945
43 | 2644011.8941 | 1192832.4701
44 | 2644041.2427 | 1192705.9349

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9825 | -0.12263 | 0.0051349 | 0.0012869
1 | 0.98299 | -0.11911 | 0 | 0
2 | 0.98182 | -0.12742 | 0 | 0
3 | 0.98285 | -0.12009 | 0.0020549 | 0.000515
4 | 0.98544 | -0.10176 | 0 | 0
5 | 0.98177 | -0.12779 | 0 | 0
6 | 0.98155 | -0.12939 | 0.0014186 | 0.00035554
7 | 0.98261 | -0.12182 | 0.0036072 | 0.00090405
8 | 0.98655 | -0.093891 | 0.0023166 | 0.0005806
9 | 0.99322 | -0.047526 | 0 | 0
10 | 0.99283 | -0.050242 | 0.005677 | 0.0014228
11 | 0.99415 | -0.040967 | 0 | 0
12 | 0.99309 | -0.048422 | 0.0070505 | 0.001767
13 | 0.99304 | -0.048804 | 0.059458 | 0.014902
14 | 0.99768 | -0.016198 | 0.080506 | 0.020177
15 | 1 | 0 | -0.21919 | -0.054958
16 | 0.99087 | -0.063436 | 0 | 0
17 | 0.98904 | -0.076342 | 0.0036687 | 0.00091945
18 | 0.98164 | -0.12869 | 0.0037887 | 0.00094954
19 | 0.98032 | -0.13813 | 0 | 0
20 | 0.98249 | -0.12265 | 0.0013379 | 0.0003353
21 | 0.9796 | -0.14327 | 0.0029572 | 0.00074115
22 | 0.97964 | -0.14301 | 0 | 0
23 | 0.98729 | -0.088679 | 0 | 0
24 | 0.98014 | -0.13943 | 0.0017379 | 0.00043555
25 | 0.98016 | -0.13929 | 0 | 0
26 | 0.98152 | -0.12956 | 0.0031953 | 0.00080083
27 | 0.97979 | -0.14191 | 0.0010661 | 0.00026719
28 | 0.98724 | -0.089006 | 0.00089662 | 0.00022472
29 | 0.98603 | -0.097597 | 0 | 0
30 | 0.98561 | -0.10062 | 0.0049849 | 0.0012493
31 | 0.98592 | -0.098372 | 0.0032529 | 0.00081524
32 | 0.98553 | -0.10115 | 0 | 0
33 | 0.9858 | -0.099229 | 0.00050003 | 0.00012532
34 | 0.97938 | -0.14488 | 0 | 0
35 | 0.97997 | -0.14066 | 0.004683 | 0.0011737
36 | 0.97891 | -0.1482 | 0.0071079 | 0.0017814
37 | 0.97884 | -0.1487 | 0 | 0
38 | 0.97876 | -0.14926 | 0.0029263 | 0.0007334
39 | 0.98546 | -0.10168 | 0.0014251 | 0.00035715
40 | 0.98552 | -0.10127 | 0 | 0
41 | 0.98569 | -0.10002 | 0.0020061 | 0.00050278
42 | 0.9797 | -0.14259 | 0.002843 | 0.00071253
43 | 0.97972 | -0.14245 | 0.0010077 | 0.00025255
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.037948 | -0.0095177 | 0.037967 | 0.0095247 | 1.8552e-05 | 7.0213e-06 | 0.057476 | 0.057476 | 0.057476 | 0.9825 | -0.12263 | 0.98299 | -0.11911 | 21.2874
1 | 0.032813 | 0.0082307 | -0.032791 | -0.0082225 | 2.1748e-05 | 8.1859e-06 | 0.049699 | 0.049699 | 0.049699 | 0.9825 | -0.12263 | 0.98182 | -0.12742 | 18.407
2 | 0.0070022 | 0.0017539 | -0.0070013 | -0.0017537 | 9.4562e-07 | 1.9273e-07 | 0.010599 | 0.010599 | 0.010599 | 0.98299 | -0.11911 | 0.98285 | -0.12009 | 3.9257
3 | -0.044969 | -0.011279 | 0.045077 | 0.01132 | 0.00010841 | 4.1218e-05 | 0.068075 | 0.068075 | 0.068075 | 0.98299 | -0.11911 | 0.98544 | -0.10176 | 25.213
4 | 0.0069857 | 0.0017504 | -0.0069853 | -0.0017504 | 3.5713e-07 | 7.2786e-08 | 0.010587 | 0.010587 | 0.010587 | 0.98182 | -0.12742 | 0.98177 | -0.12779 | 3.9212
5 | 0.025806 | 0.0064721 | -0.025799 | -0.0064695 | 7.0604e-06 | 2.622e-06 | 0.039112 | 0.039112 | 0.039112 | 0.98182 | -0.12742 | 0.98155 | -0.12939 | 14.4859
6 | 0.0049464 | 0.0012387 | -0.0049452 | -0.0012386 | 1.1837e-06 | 2.6664e-08 | 0.0074884 | 0.0074885 | 0.0074885 | 0.98285 | -0.12009 | 0.98261 | -0.12182 | 2.7735
7 | -0.045077 | -0.01132 | 0.045127 | 0.011339 | 4.9375e-05 | 1.8772e-05 | 0.068075 | 0.068075 | 0.068075 | 0.98544 | -0.10176 | 0.98655 | -0.093891 | 25.213
8 | 0.0069853 | 0.0017504 | -0.0069845 | -0.0017502 | 8.7638e-07 | 1.7865e-07 | 0.010587 | 0.010587 | 0.010587 | 0.98177 | -0.12779 | 0.98164 | -0.12869 | 3.9212
9 | 0.02438 | 0.0061139 | -0.024351 | -0.006103 | 2.9494e-05 | 1.0907e-05 | 0.036961 | 0.036961 | 0.036961 | 0.98155 | -0.12939 | 0.98032 | -0.13813 | 13.6894
10 | 0.001338 | 0.00033459 | -0.0013379 | -0.0003353 | 1.5489e-07 | -7.0627e-07 | 0.002026 | 0.0020262 | 0.0020262 | 0.98261 | -0.12182 | 0.98249 | -0.12265 | 0.75046
11 | -0.047443 | -0.011919 | 0.047478 | 0.011932 | 3.4421e-05 | 1.3101e-05 | 0.071569 | 0.071569 | 0.071569 | 0.98655 | -0.093891 | 0.98729 | -0.088679 | 26.5071
12 | 0.0056791 | 0.001423 | -0.005677 | -0.0014228 | 2.134e-06 | 2.0962e-07 | 0.0085082 | 0.0085084 | 0.0085084 | 0.99322 | -0.047526 | 0.99283 | -0.050242 | 3.1513
13 | -0.012731 | -0.0031902 | 0.012742 | 0.003194 | 1.1566e-05 | 3.7885e-06 | 0.019072 | 0.019072 | 0.019072 | 0.99322 | -0.047526 | 0.99415 | -0.040967 | 7.0639
14 | 0.0070514 | 0.0017672 | -0.0070505 | -0.001767 | 8.7435e-07 | 1.7382e-07 | 0.010564 | 0.010564 | 0.010564 | 0.99322 | -0.047526 | 0.99309 | -0.048422 | 3.9127
15 | 0.059523 | 0.014926 | -0.059458 | -0.014902 | 6.4579e-05 | 2.4669e-05 | 0.089096 | 0.089096 | 0.089096 | 0.99415 | -0.040967 | 0.99304 | -0.048804 | 32.9984
16 | -0.072265 | -0.01812 | 0.072514 | 0.018216 | 0.00024892 | 9.5293e-05 | 0.10817 | 0.10817 | 0.10817 | 0.99415 | -0.040967 | 0.99768 | -0.016198 | 40.0621
17 | -0.15302 | -0.038392 | 0.15336 | 0.038524 | 0.00034467 | 0.00013201 | 0.22824 | 0.22824 | 0.22824 | 0.99768 | -0.016198 | 1 | 0 | 42.2668
18 | 0.065026 | 0.016434 | -0.064451 | -0.016214 | 0.00057548 | 0.00022006 | 0.096808 | 0.096809 | 0.096809 | 1 | 0 | 0.99087 | -0.063436 | 35.8551
19 | 0.064451 | 0.016214 | -0.064335 | -0.016169 | 0.00011581 | 4.4287e-05 | 0.096809 | 0.096809 | 0.096809 | 0.99087 | -0.063436 | 0.98904 | -0.076342 | 35.8551
20 | 0.060666 | 0.01525 | -0.060562 | -0.01521 | 0.00010405 | 3.9763e-05 | 0.091289 | 0.091289 | 0.091289 | 0.98904 | -0.076342 | 0.98729 | -0.088679 | 33.8109
21 | 0.0031957 | 0.00080064 | -0.0031953 | -0.00080083 | 3.8606e-07 | -1.8479e-07 | 0.0048441 | 0.0048442 | 0.0048442 | 0.98164 | -0.12869 | 0.98152 | -0.12956 | 1.7942
22 | 0.014075 | 0.0035281 | -0.014067 | -0.0035256 | 7.3649e-06 | 2.5068e-06 | 0.021364 | 0.021364 | 0.021364 | 0.98032 | -0.13813 | 0.97979 | -0.14191 | 7.9126
23 | 0.010276 | 0.0025749 | -0.010274 | -0.0025744 | 1.6536e-06 | 4.9867e-07 | 0.015597 | 0.015597 | 0.015597 | 0.98032 | -0.13813 | 0.98016 | -0.13929 | 5.7768
24 | -0.0029572 | -0.00074115 | 0.0029573 | 0.00074109 | 1.0567e-07 | -6.5016e-08 | 0.004492 | 0.004492 | 0.004492 | 0.9796 | -0.14327 | 0.97964 | -0.14301 | 1.6637
25 | -0.012999 | -0.0032578 | 0.013001 | 0.0032584 | 1.9848e-06 | 6.6064e-07 | 0.019745 | 0.019745 | 0.019745 | 0.97964 | -0.14301 | 0.97979 | -0.14191 | 7.313
26 | 0.010042 | 0.0025167 | -0.010039 | -0.0025159 | 2.5971e-06 | 7.737e-07 | 0.015253 | 0.015253 | 0.015253 | 0.97964 | -0.14301 | 0.97938 | -0.14488 | 5.6493
27 | 0.00089666 | 0.00022428 | -0.00089662 | -0.00022472 | 4.0533e-08 | -4.3925e-07 | 0.0013513 | 0.0013514 | 0.0013514 | 0.98729 | -0.088679 | 0.98724 | -0.089006 | 0.50053
28 | 0.012188 | 0.0030537 | -0.012173 | -0.0030488 | 1.5022e-05 | 4.8666e-06 | 0.018369 | 0.018369 | 0.018369 | 0.98729 | -0.088679 | 0.98603 | -0.097597 | 6.8035
29 | -0.0017379 | -0.00043555 | 0.0017379 | 0.00043547 | 3.2794e-08 | -8.2544e-08 | 0.0026384 | 0.0026383 | 0.0026384 | 0.98014 | -0.13943 | 0.98016 | -0.13929 | 0.97718
30 | 0.0085363 | 0.0021389 | -0.0085347 | -0.0021385 | 1.6151e-06 | 4.2698e-07 | 0.012959 | 0.012959 | 0.012959 | 0.98016 | -0.13929 | 0.97997 | -0.14066 | 4.7997
31 | 0.0064129 | 0.0016061 | -0.0064102 | -0.0016056 | 2.6774e-06 | 4.4562e-07 | 0.0096772 | 0.0096774 | 0.0096774 | 0.98603 | -0.097597 | 0.98561 | -0.10062 | 3.5842
32 | 0.0057601 | 0.0014427 | -0.0057595 | -0.0014426 | 6.1762e-07 | 7.047e-08 | 0.0086923 | 0.0086923 | 0.0086923 | 0.98603 | -0.097597 | 0.98592 | -0.098372 | 3.2194
33 | 0.0014253 | 0.00035631 | -0.0014252 | -0.00035674 | 1.0526e-07 | -4.2388e-07 | 0.0021515 | 0.0021516 | 0.0021516 | 0.98561 | -0.10062 | 0.98553 | -0.10115 | 0.7969
34 | 0.0025066 | 0.00062738 | -0.0025063 | -0.00062769 | 2.9669e-07 | -3.0953e-07 | 0.0037829 | 0.003783 | 0.003783 | 0.98592 | -0.098372 | 0.9858 | -0.099229 | 1.4011
35 | 0.0014252 | 0.00035674 | -0.0014251 | -0.00035683 | 2.3689e-08 | -9.5375e-08 | 0.0021516 | 0.0021517 | 0.0021517 | 0.98553 | -0.10115 | 0.98552 | -0.10127 | 0.79692
36 | 0.0020063 | 0.00050237 | -0.0020061 | -0.00050278 | 2.1946e-07 | -4.0446e-07 | 0.0030283 | 0.0030284 | 0.0030284 | 0.9858 | -0.099229 | 0.98569 | -0.10002 | 1.1216
37 | 0.010039 | 0.0025159 | -0.010035 | -0.0025145 | 4.6128e-06 | 1.3745e-06 | 0.015253 | 0.015253 | 0.015253 | 0.97938 | -0.14488 | 0.97891 | -0.1482 | 5.6493
38 | 0.0038518 | 0.00096485 | -0.0038508 | -0.00096505 | 9.5487e-07 | -1.9623e-07 | 0.0058485 | 0.0058487 | 0.0058487 | 0.97997 | -0.14066 | 0.97972 | -0.14245 | 2.1662
39 | 0.0029267 | 0.00073313 | -0.0029265 | -0.00073326 | 2.032e-07 | -1.2869e-07 | 0.0044487 | 0.0044488 | 0.0044488 | 0.97891 | -0.1482 | 0.97884 | -0.1487 | 1.6477
40 | 0.0029265 | 0.00073326 | -0.0029263 | -0.0007334 | 2.2689e-07 | -1.4364e-07 | 0.0044488 | 0.0044489 | 0.0044489 | 0.97884 | -0.1487 | 0.97876 | -0.14926 | 1.6477
41 | -0.0014251 | -0.00035715 | 0.0014251 | 0.00035683 | 8.0329e-08 | -3.2336e-07 | 0.0021518 | 0.0021517 | 0.0021518 | 0.98546 | -0.10168 | 0.98552 | -0.10127 | 0.79696
42 | -0.002843 | -0.00071253 | 0.0028431 | 0.0007125 | 5.494e-08 | -3.8327e-08 | 0.0043182 | 0.0043181 | 0.0043182 | 0.9797 | -0.14259 | 0.97972 | -0.14245 | 1.5993

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21919 | 0.054958

## res_load
| p_mw | q_mvar
0 | 0.0051349 | 0.0012869
1 | 0.0020549 | 0.000515
2 | 0.0014186 | 0.00035554
3 | 0.0036072 | 0.00090405
4 | 0.0023166 | 0.0005806
5 | 0.005677 | 0.0014228
6 | 0.0070505 | 0.001767
7 | 0.059458 | 0.014902
8 | 0.080506 | 0.020177
9 | 0.0036687 | 0.00091945
10 | 0.0037887 | 0.00094954
11 | 0.0013379 | 0.0003353
12 | 0.0029572 | 0.00074115
13 | 0.0017379 | 0.00043555
14 | 0.0031953 | 0.00080083
15 | 0.0010661 | 0.00026719
16 | 0.00089662 | 0.00022472
17 | 0.0049849 | 0.0012493
18 | 0.0032529 | 0.00081524
19 | 0.00050003 | 0.00012532
20 | 0.004683 | 0.0011737
21 | 0.0071079 | 0.0017814
22 | 0.0029263 | 0.0007334
23 | 0.0014251 | 0.00035715
24 | 0.0020061 | 0.00050278
25 | 0.002843 | 0.00071253
26 | 0.0010077 | 0.00025255

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1