## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1004-1_1_4_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_1004-1_1_4_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_1004-1_1_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_1004-1_1_4_node_172 | 0.4 | n |  | TRUE
4 | bus_LV_1004-1_1_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1004-1_1_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1004-1_1_4_node_214 | 0.4 | n |  | TRUE
7 | bus_LV_1004-1_1_4_node_182 | 0.4 | n |  | TRUE
8 | bus_LV_1004-1_1_4_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_1004-1_1_4_node_49 | 0.4 | n |  | TRUE
10 | bus_LV_1004-1_1_4_node_57 | 0.4 | n |  | TRUE
11 | bus_LV_1004-1_1_4_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_1004-1_1_4_node_197 | 0.4 | n |  | TRUE
13 | bus_LV_1004-1_1_4_node_152 | 0.4 | n |  | TRUE
14 | bus_LV_1004-1_1_4_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1004-1_1_4_node_52 | 0.4 | n |  | TRUE
16 | bus_LV_1004-1_1_4_node_53 | 0.4 | n |  | TRUE
17 | bus_LV_1004-1_1_4_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_1004-1_1_4_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_1004-1_1_4_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_1004-1_1_4_node_215 | 0.4 | n |  | TRUE
21 | bus_LV_1004-1_1_4_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_1004-1_1_4_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_1004-1_1_4_node_188 | 0.4 | n |  | TRUE
24 | bus_LV_1004-1_1_4_node_166 | 0.4 | n |  | TRUE
25 | bus_LV_1004-1_1_4_node_60 | 0.4 | n |  | TRUE
26 | bus_LV_1004-1_1_4_node_61 | 0.4 | n |  | TRUE
27 | bus_LV_1004-1_1_4_node_62 | 0.4 | n |  | TRUE
28 | bus_LV_1004-1_1_4_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_1004-1_1_4_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_1004-1_1_4_node_108 | 0.4 | n |  | TRUE
31 | bus_LV_1004-1_1_4_node_107 | 0.4 | n |  | TRUE
32 | bus_LV_1004-1_1_4_node_66 | 0.4 | n |  | TRUE
33 | bus_LV_1004-1_1_4_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_1004-1_1_4_node_181 | 0.4 | n |  | TRUE
35 | bus_LV_1004-1_1_4_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_1004-1_1_4_node_77 | 0.4 | n |  | TRUE
37 | bus_LV_1004-1_1_4_node_78 | 0.4 | n |  | TRUE
38 | bus_LV_1004-1_1_4_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_1004-1_1_4_node_80 | 0.4 | n |  | TRUE
40 | bus_LV_1004-1_1_4_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_1004-1_1_4_node_81 | 0.4 | n |  | TRUE
42 | bus_LV_1004-1_1_4_node_82 | 0.4 | n |  | TRUE
43 | bus_LV_1004-1_1_4_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_1004-1_1_4_node_84 | 0.4 | n |  | TRUE
45 | bus_LV_1004-1_1_4_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_1004-1_1_4_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_1004-1_1_4_node_87 | 0.4 | n |  | TRUE
48 | bus_LV_1004-1_1_4_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_1004-1_1_4_node_89 | 0.4 | n |  | TRUE
50 | bus_LV_1004-1_1_4_node_91 | 0.4 | n |  | TRUE
51 | bus_LV_1004-1_1_4_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_1004-1_1_4_node_97 | 0.4 | n |  | TRUE
53 | bus_LV_1004-1_1_4_node_95 | 0.4 | n |  | TRUE
54 | bus_LV_1004-1_1_4_node_208 | 0.4 | n |  | TRUE
55 | bus_LV_1004-1_1_4_node_96 | 0.4 | n |  | TRUE
56 | bus_LV_1004-1_1_4_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_1004-1_1_4_node_98 | 0.4 | n |  | TRUE
58 | bus_LV_1004-1_1_4_node_99 | 0.4 | n |  | TRUE
59 | bus_LV_1004-1_1_4_node_100 | 0.4 | n |  | TRUE
60 | bus_LV_1004-1_1_4_node_101 | 0.4 | n |  | TRUE
61 | bus_LV_1004-1_1_4_node_102 | 0.4 | n |  | TRUE
62 | bus_LV_1004-1_1_4_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_1004-1_1_4_node_106 | 0.4 | n |  | TRUE
64 | bus_LV_1004-1_1_4_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_1004-1_1_4_node_143 | 0.4 | n |  | TRUE
66 | bus_LV_1004-1_1_4_node_144 | 0.4 | n |  | TRUE
67 | bus_LV_1004-1_1_4_node_206 | 0.4 | n |  | TRUE
68 | bus_LV_1004-1_1_4_node_149 | 0.4 | n |  | TRUE
69 | bus_LV_1004-1_1_4_node_150 | 0.4 | n |  | TRUE
70 | bus_LV_1004-1_1_4_node_151 | 0.4 | n |  | TRUE
71 | bus_LV_1004-1_1_4_node_164 | 0.4 | n |  | TRUE
72 | bus_LV_1004-1_1_4_node_165 | 0.4 | n |  | TRUE
73 | bus_LV_1004-1_1_4_node_167 | 0.4 | n |  | TRUE
74 | bus_LV_1004-1_1_4_node_168 | 0.4 | n |  | TRUE
75 | bus_LV_1004-1_1_4_node_169 | 0.4 | n |  | TRUE
76 | bus_LV_1004-1_1_4_node_173 | 0.4 | n |  | TRUE
77 | bus_LV_1004-1_1_4_node_170 | 0.4 | n |  | TRUE
78 | bus_LV_1004-1_1_4_node_174 | 0.4 | n |  | TRUE
79 | bus_LV_1004-1_1_4_node_171 | 0.4 | n |  | TRUE
80 | bus_LV_1004-1_1_4_node_175 | 0.4 | n |  | TRUE
81 | bus_LV_1004-1_1_4_node_176 | 0.4 | n |  | TRUE
82 | bus_LV_1004-1_1_4_node_177 | 0.4 | n |  | TRUE
83 | bus_LV_1004-1_1_4_node_178 | 0.4 | n |  | TRUE
84 | bus_LV_1004-1_1_4_node_179 | 0.4 | n |  | TRUE
85 | bus_LV_1004-1_1_4_node_180 | 0.4 | n |  | TRUE
86 | bus_LV_1004-1_1_4_node_183 | 0.4 | n |  | TRUE
87 | bus_LV_1004-1_1_4_node_194 | 0.4 | n |  | TRUE
88 | bus_LV_1004-1_1_4_node_187 | 0.4 | n |  | TRUE
89 | bus_LV_1004-1_1_4_node_190 | 0.4 | n |  | TRUE
90 | bus_LV_1004-1_1_4_node_191 | 0.4 | n |  | TRUE
91 | bus_LV_1004-1_1_4_node_192 | 0.4 | n |  | TRUE
92 | bus_LV_1004-1_1_4_node_193 | 0.4 | n |  | TRUE
93 | bus_LV_1004-1_1_4_node_195 | 0.4 | n |  | TRUE
94 | bus_LV_1004-1_1_4_node_196 | 0.4 | n |  | TRUE
95 | bus_LV_1004-1_1_4_node_202 | 0.4 | n |  | TRUE
96 | bus_LV_1004-1_1_4_node_198 | 0.4 | n |  | TRUE
97 | bus_LV_1004-1_1_4_node_199 | 0.4 | n |  | TRUE
98 | bus_LV_1004-1_1_4_node_200 | 0.4 | n |  | TRUE
99 | bus_LV_1004-1_1_4_node_201 | 0.4 | n |  | TRUE
100 | bus_LV_1004-1_1_4_node_203 | 0.4 | n |  | TRUE
101 | bus_LV_1004-1_1_4_node_204 | 0.4 | n |  | TRUE
102 | bus_LV_1004-1_1_4_node_205 | 0.4 | n |  | TRUE
103 | bus_LV_1004-1_1_4_node_207 | 0.4 | n |  | TRUE
104 | bus_MV_82_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1004-1_1_4_load_4 | 0 | 0.0015104 | 0.00037853 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1004-1_1_4_load_5 | 1 | 0.0025236 | 0.00063246 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1004-1_1_4_load_172 | 3 | 0.00048142 | 0.00012065 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1004-1_1_4_load_7 | 4 | 0.0051193 | 0.001283 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1004-1_1_4_load_214 | 6 | 0.050221 | 0.012587 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1004-1_1_4_load_48 | 8 | 0.00026813 | 6.7199e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1004-1_1_4_load_57 | 10 | 0.00080623 | 0.00020206 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1004-1_1_4_load_50 | 11 | 0.00048926 | 0.00012262 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1004-1_1_4_load_197 | 12 | 0.0063431 | 0.0015897 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1004-1_1_4_load_152 | 13 | 0.00075267 | 0.00018864 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1004-1_1_4_load_51 | 14 | 0.001696 | 0.00042505 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1004-1_1_4_load_52 | 15 | 0.0011069 | 0.00027741 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1004-1_1_4_load_215 | 20 | 0.0014787 | 0.00037061 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1004-1_1_4_load_56 | 21 | 6.8521e-05 | 1.7173e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1004-1_1_4_load_58 | 22 | 0.0003616 | 9.0626e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1004-1_1_4_load_188 | 23 | 6.9344e-05 | 1.7379e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1004-1_1_4_load_60 | 25 | 0.0011972 | 0.00030005 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1004-1_1_4_load_61 | 26 | 0.001179 | 0.00029548 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1004-1_1_4_load_62 | 27 | 0.00086008 | 0.00021556 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1004-1_1_4_load_63 | 28 | 0.0017813 | 0.00044645 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1004-1_1_4_load_64 | 29 | 0.00033823 | 8.4768e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1004-1_1_4_load_108 | 30 | 0.0011383 | 0.00028529 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1004-1_1_4_load_66 | 32 | 0.0021705 | 0.00054398 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1004-1_1_4_load_68 | 33 | 0.0027383 | 0.00068628 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1004-1_1_4_load_76 | 35 | 0.0018112 | 0.00045393 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1004-1_1_4_load_77 | 36 | 0.00062639 | 0.00015699 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1004-1_1_4_load_78 | 37 | 0.00058861 | 0.00014752 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1004-1_1_4_load_79 | 38 | 0.0006487 | 0.00016258 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1004-1_1_4_load_80 | 39 | 0.00061709 | 0.00015466 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1004-1_1_4_load_105 | 40 | 0.0013068 | 0.00032751 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1004-1_1_4_load_81 | 41 | 0.0010002 | 0.00025067 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1004-1_1_4_load_82 | 42 | 0.0004204 | 0.00010536 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1004-1_1_4_load_83 | 43 | 0.00097293 | 0.00024384 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1004-1_1_4_load_84 | 44 | 0.00032856 | 8.2346e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1004-1_1_4_load_85 | 45 | 0.00064788 | 0.00016237 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1004-1_1_4_load_87 | 47 | 0.00058891 | 0.0001476 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1004-1_1_4_load_88 | 48 | 0.00048721 | 0.00012211 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1004-1_1_4_load_92 | 51 | 0.0027256 | 0.00068309 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1004-1_1_4_load_97 | 52 | 0.00041288 | 0.00010348 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1004-1_1_4_load_95 | 53 | 0.00042778 | 0.00010721 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1004-1_1_4_load_208 | 54 | 0.0025925 | 0.00064973 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1004-1_1_4_load_96 | 55 | 0.0031881 | 0.00079902 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1004-1_1_4_load_98 | 57 | 0.00025513 | 6.3941e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1004-1_1_4_load_99 | 58 | 0.00032338 | 8.1048e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1004-1_1_4_load_101 | 60 | 0.00020834 | 5.2215e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1004-1_1_4_load_102 | 61 | 0.00019704 | 4.9383e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1004-1_1_4_load_109 | 62 | 0.00026417 | 6.6206e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1004-1_1_4_load_106 | 63 | 0.00045915 | 0.00011507 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1004-1_1_4_load_143 | 65 | 0.00050363 | 0.00012622 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1004-1_1_4_load_144 | 66 | 0.00054606 | 0.00013686 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1004-1_1_4_load_206 | 67 | 0.00039178 | 9.8189e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1004-1_1_4_load_149 | 68 | 0.0010022 | 0.00025116 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1004-1_1_4_load_150 | 69 | 0.00057163 | 0.00014326 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1004-1_1_4_load_151 | 70 | 0.0012945 | 0.00032443 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1004-1_1_4_load_164 | 71 | 0.00042739 | 0.00010711 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1004-1_1_4_load_165 | 72 | 0.00038999 | 9.774e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1004-1_1_4_load_167 | 73 | 0.00016487 | 4.1319e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1004-1_1_4_load_168 | 74 | 0.00015475 | 3.8783e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1004-1_1_4_load_169 | 75 | 0.0001446 | 3.6241e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1004-1_1_4_load_170 | 77 | 0.00012165 | 3.0488e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1004-1_1_4_load_174 | 78 | 0.00045046 | 0.0001129 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1004-1_1_4_load_171 | 79 | 0.00084205 | 0.00021104 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1004-1_1_4_load_175 | 80 | 0.00027553 | 6.9055e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1004-1_1_4_load_176 | 81 | 8.584e-05 | 2.1514e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1004-1_1_4_load_177 | 82 | 0.000724 | 0.00018145 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1004-1_1_4_load_179 | 84 | 0.00038568 | 9.6661e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1004-1_1_4_load_180 | 85 | 0.01179 | 0.0029549 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1004-1_1_4_load_194 | 87 | 0.003349 | 0.00083935 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1004-1_1_4_load_187 | 88 | 0.00018287 | 4.5832e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1004-1_1_4_load_190 | 89 | 0.0022744 | 0.00057003 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1004-1_1_4_load_191 | 90 | 0.00022224 | 5.5699e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1004-1_1_4_load_192 | 91 | 0.0028895 | 0.00072419 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1004-1_1_4_load_193 | 92 | 0.00018911 | 4.7394e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1004-1_1_4_load_195 | 93 | 0.00022547 | 5.6509e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1004-1_1_4_load_196 | 94 | 0.00018611 | 4.6642e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1004-1_1_4_load_202 | 95 | 0.00020475 | 5.1314e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1004-1_1_4_load_198 | 96 | 0.00017759 | 4.4509e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1004-1_1_4_load_199 | 97 | 0.00021539 | 5.3981e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1004-1_1_4_load_200 | 98 | 0.00021539 | 5.3981e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1004-1_1_4_load_201 | 99 | 0.00022813 | 5.7174e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1004-1_1_4_load_203 | 100 | 0.00026526 | 6.648e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1004-1_1_4_load_204 | 101 | 0.00030224 | 7.5748e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1004-1_1_4_load_205 | 102 | 0.00029445 | 7.3795e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1004-1_1_4_load_207 | 103 | 0.0023069 | 0.00057816 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1004-1_1_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.051428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1004-1_1_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.029735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1004-1_1_4_line_2 | NAYY 4x150 SE | 0 | 3 | 0.19709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1004-1_1_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.079943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1004-1_1_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.064319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1004-1_1_4_line_5 | NAYY 4x150 SE | 3 | 79 | 0.046187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1004-1_1_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.050821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1004-1_1_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.058391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1004-1_1_4_line_8 | NAYY 4x150 SE | 7 | 86 | 0.016287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1004-1_1_4_line_9 | NAYY 4x150 SE | 7 | 85 | 0.061778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1004-1_1_4_line_10 | NAYY 4x150 SE | 8 | 9 | 0.12789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1004-1_1_4_line_11 | NAYY 4x150 SE | 8 | 10 | 0.22906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1004-1_1_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.20278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1004-1_1_4_line_13 | NAYY 4x150 SE | 9 | 12 | 0.17899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1004-1_1_4_line_14 | NAYY 4x150 SE | 10 | 21 | 0.26304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1004-1_1_4_line_15 | NAYY 4x150 SE | 11 | 13 | 0.042368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1004-1_1_4_line_16 | NAYY 4x150 SE | 12 | 86 | 0.017796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1004-1_1_4_line_17 | NAYY 4x150 SE | 13 | 69 | 0.028315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1004-1_1_4_line_18 | NAYY 4x150 SE | 14 | 15 | 0.039645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1004-1_1_4_line_19 | NAYY 4x150 SE | 14 | 16 | 0.053521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1004-1_1_4_line_20 | NAYY 4x150 SE | 15 | 17 | 0.055364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1004-1_1_4_line_21 | NAYY 4x150 SE | 16 | 18 | 0.020109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1004-1_1_4_line_22 | NAYY 4x150 SE | 17 | 19 | 0.22601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1004-1_1_4_line_23 | NAYY 4x150 SE | 18 | 20 | 0.026997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1004-1_1_4_line_24 | NAYY 4x150 SE | 19 | 24 | 0.023957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1004-1_1_4_line_25 | NAYY 4x150 SE | 21 | 22 | 0.50487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1004-1_1_4_line_26 | NAYY 4x150 SE | 22 | 23 | 0.56105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1004-1_1_4_line_27 | NAYY 4x150 SE | 23 | 88 | 0.022617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1004-1_1_4_line_28 | NAYY 4x150 SE | 24 | 74 | 0.022962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1004-1_1_4_line_29 | NAYY 4x150 SE | 24 | 71 | 0.020836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1004-1_1_4_line_30 | NAYY 4x150 SE | 25 | 26 | 0.026331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1004-1_1_4_line_31 | NAYY 4x150 SE | 25 | 27 | 0.034977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1004-1_1_4_line_32 | NAYY 4x150 SE | 26 | 28 | 0.1462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1004-1_1_4_line_33 | NAYY 4x150 SE | 27 | 29 | 0.019661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1004-1_1_4_line_34 | NAYY 4x150 SE | 28 | 30 | 0.012312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1004-1_1_4_line_35 | NAYY 4x150 SE | 29 | 31 | 0.062487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1004-1_1_4_line_36 | NAYY 4x150 SE | 30 | 63 | 0.0020005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1004-1_1_4_line_37 | NAYY 4x150 SE | 31 | 44 | 0.018639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1004-1_1_4_line_38 | NAYY 4x150 SE | 32 | 33 | 0.028345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1004-1_1_4_line_39 | NAYY 4x150 SE | 33 | 34 | 0.061745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1004-1_1_4_line_40 | NAYY 4x150 SE | 34 | 50 | 0.015871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1004-1_1_4_line_41 | NAYY 4x150 SE | 34 | 85 | 0.18453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1004-1_1_4_line_42 | NAYY 4x150 SE | 35 | 36 | 0.01179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1004-1_1_4_line_43 | NAYY 4x150 SE | 35 | 37 | 0.0023843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1004-1_1_4_line_44 | NAYY 4x150 SE | 36 | 38 | 0.017855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1004-1_1_4_line_45 | NAYY 4x150 SE | 37 | 39 | 0.043541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1004-1_1_4_line_46 | NAYY 4x150 SE | 39 | 40 | 0.001861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1004-1_1_4_line_47 | NAYY 4x150 SE | 40 | 63 | 0.06253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1004-1_1_4_line_48 | NAYY 4x150 SE | 41 | 42 | 0.067395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1004-1_1_4_line_49 | NAYY 4x150 SE | 41 | 43 | 0.015868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1004-1_1_4_line_50 | NAYY 4x150 SE | 42 | 44 | 0.030313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1004-1_1_4_line_51 | NAYY 4x150 SE | 43 | 45 | 0.011045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1004-1_1_4_line_52 | NAYY 4x150 SE | 45 | 46 | 0.015158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1004-1_1_4_line_53 | NAYY 4x150 SE | 46 | 52 | 0.075765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1004-1_1_4_line_54 | NAYY 4x150 SE | 46 | 53 | 0.064994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1004-1_1_4_line_55 | NAYY 4x150 SE | 46 | 48 | 0.018174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1004-1_1_4_line_56 | NAYY 4x150 SE | 47 | 48 | 0.061031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1004-1_1_4_line_57 | NAYY 4x150 SE | 47 | 49 | 0.22786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1004-1_1_4_line_58 | NAYY 4x150 SE | 49 | 50 | 0.060591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1004-1_1_4_line_59 | NAYY 4x150 SE | 49 | 51 | 0.029788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1004-1_1_4_line_60 | NAYY 4x150 SE | 50 | 54 | 0.018601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1004-1_1_4_line_61 | NAYY 4x150 SE | 52 | 56 | 0.044985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1004-1_1_4_line_62 | NAYY 4x150 SE | 53 | 55 | 0.027852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1004-1_1_4_line_63 | NAYY 4x150 SE | 54 | 103 | 0.015412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1004-1_1_4_line_64 | NAYY 4x150 SE | 56 | 59 | 0.063877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1004-1_1_4_line_65 | NAYY 4x150 SE | 56 | 64 | 0.13926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1004-1_1_4_line_66 | NAYY 4x150 SE | 57 | 58 | 0.019309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1004-1_1_4_line_67 | NAYY 4x150 SE | 58 | 59 | 0.035304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1004-1_1_4_line_68 | NAYY 4x150 SE | 60 | 61 | 0.1376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1004-1_1_4_line_69 | NAYY 4x150 SE | 60 | 62 | 0.38224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1004-1_1_4_line_70 | NAYY 4x150 SE | 62 | 64 | 0.015012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1004-1_1_4_line_71 | NAYY 4x150 SE | 65 | 66 | 0.020433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1004-1_1_4_line_72 | NAYY 4x150 SE | 66 | 67 | 0.025468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1004-1_1_4_line_73 | NAYY 4x150 SE | 67 | 102 | 0.05151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1004-1_1_4_line_74 | NAYY 4x150 SE | 68 | 69 | 0.11714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1004-1_1_4_line_75 | NAYY 4x150 SE | 68 | 70 | 0.032163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1004-1_1_4_line_76 | NAYY 4x150 SE | 71 | 72 | 0.01436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1004-1_1_4_line_77 | NAYY 4x150 SE | 72 | 73 | 0.00020314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1004-1_1_4_line_78 | NAYY 4x150 SE | 73 | 75 | 0.01356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1004-1_1_4_line_79 | NAYY 4x150 SE | 74 | 76 | 0.0057281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1004-1_1_4_line_80 | NAYY 4x150 SE | 75 | 77 | 0.0041432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1004-1_1_4_line_81 | NAYY 4x150 SE | 76 | 79 | 0.022563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1004-1_1_4_line_82 | NAYY 4x150 SE | 77 | 78 | 0.0037671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1004-1_1_4_line_83 | NAYY 4x150 SE | 78 | 80 | 0.01106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1004-1_1_4_line_84 | NAYY 4x150 SE | 80 | 81 | 0.01814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1004-1_1_4_line_85 | NAYY 4x150 SE | 81 | 82 | 0.025385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1004-1_1_4_line_86 | NAYY 4x150 SE | 82 | 83 | 0.0068178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1004-1_1_4_line_87 | NAYY 4x150 SE | 83 | 84 | 0.03867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1004-1_1_4_line_88 | NAYY 4x150 SE | 86 | 87 | 0.043154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1004-1_1_4_line_89 | NAYY 4x150 SE | 87 | 91 | 0.02023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1004-1_1_4_line_90 | NAYY 4x150 SE | 89 | 90 | 0.020245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1004-1_1_4_line_91 | NAYY 4x150 SE | 89 | 91 | 0.020651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1004-1_1_4_line_92 | NAYY 4x150 SE | 90 | 92 | 0.052054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1004-1_1_4_line_93 | NAYY 4x150 SE | 92 | 93 | 0.0052909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1004-1_1_4_line_94 | NAYY 4x150 SE | 93 | 94 | 0.016158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1004-1_1_4_line_95 | NAYY 4x150 SE | 94 | 95 | 0.0071378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1004-1_1_4_line_96 | NAYY 4x150 SE | 95 | 98 | 0.012413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1004-1_1_4_line_97 | NAYY 4x150 SE | 96 | 97 | 0.0048136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1004-1_1_4_line_98 | NAYY 4x150 SE | 96 | 98 | 0.00248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1004-1_1_4_line_99 | NAYY 4x150 SE | 97 | 99 | 0.0024189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1004-1_1_4_line_100 | NAYY 4x150 SE | 99 | 100 | 0.030905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1004-1_1_4_line_101 | NAYY 4x150 SE | 100 | 101 | 0.017344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1004-1_1_4_line_102 | NAYY 4x150 SE | 101 | 102 | 0.0068615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1004-1_1_4_trafo_182 | 0.25 MVA 20/0.4 kV | 104 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2644118.071 | 1186586.628 | 2644119.3555 | 1186581.9518 | 2644117.7263 | 1186553.4799 | 2644115.6144 | 1186548.0614 | 2644111.6466 | 1186544.975 | 2644104.4755 | 1186545.7964
1 | 2644119.7333 | 1186614.5724 | 2644114.6752 | 1186606.1973 | 2644115.4667 | 1186596.1087 | 2644118.071 | 1186586.628
2 | 2644118.071 | 1186586.628 | 2644302.4595 | 1186517.0289
3 | 2644074.8001 | 1186519.101 | 2644065.1054 | 1186529.024 | 2644062.7179 | 1186534.1093 | 2644062.1473 | 1186541.1422 | 2644063.542 | 1186546.5554 | 2644067.4934 | 1186551.8874 | 2644073.4067 | 1186554.9992 | 2644079.4291 | 1186556.7778 | 2644087.3182 | 1186555.813 | 2644093.2886 | 1186551.1655 | 2644100.795 | 1186546.218 | 2644104.4755 | 1186545.7964
4 | 2644119.7333 | 1186614.5724 | 2644113.4711 | 1186627.7668 | 2644106.9526 | 1186641.5708 | 2644100.9612 | 1186654.2559 | 2644094.4914 | 1186667.6711 | 2644092.0817 | 1186672.6672
5 | 2644323.6622 | 1186478.9199 | 2644304.106 | 1186502.1931 | 2644300.6853 | 1186509.7275 | 2644302.4595 | 1186517.0289
6 | 2644085.218 | 1186632.8062 | 2644077.0963 | 1186651.9235 | 2644075.3839 | 1186661.7051 | 2644082.2971 | 1186667.8816 | 2644092.0817 | 1186672.6672
7 | 2644067.0866 | 1186725.4566 | 2644074.8561 | 1186708.5601 | 2644092.0817 | 1186672.6672
8 | 2644081.938 | 1186732.2362 | 2644067.0866 | 1186725.4566
9 | 2644067.0866 | 1186725.4566 | 2644052.9016 | 1186754.646 | 2644039.9716 | 1186780.966
10 | 2644274.9214 | 1186762.2525 | 2644392.3481 | 1186711.5929
11 | 2644392.3481 | 1186711.5929 | 2644606.1057 | 1186793.9138
12 | 2644274.9214 | 1186762.2525 | 2644269.9101 | 1186773.3993 | 2644267.803 | 1186779.765 | 2644249.0444 | 1186879.5364 | 2644249.8491 | 1186889.3811 | 2644253.1068 | 1186902.8347 | 2644263.9844 | 1186936.2109 | 2644265.332 | 1186950.0173 | 2644264.3204 | 1186959.6024
13 | 2644099.1721 | 1186728.3497 | 2644274.9214 | 1186762.2525
14 | 2644606.1057 | 1186793.9138 | 2644615.2408 | 1186781.3304 | 2644641.6944 | 1186746.3972 | 2644682.7363 | 1186693.1295 | 2644693.611 | 1186683.661 | 2644734.419 | 1186660.8084 | 2644768.0341 | 1186643.839 | 2644778.5781 | 1186641.8945 | 2644787.3358 | 1186640.07 | 2644803.4941 | 1186642.4031 | 2644804.8151 | 1186643.2835
15 | 2644264.3204 | 1186959.6024 | 2644259.8733 | 1187001.7358
16 | 2644081.938 | 1186732.2362 | 2644089.0153 | 1186731.6435 | 2644094.5503 | 1186730.1611 | 2644099.1721 | 1186728.3497
17 | 2644256.7908 | 1187029.8677 | 2644256.9477 | 1187029.4542 | 2644259.8733 | 1187001.7358
18 | 2644541.9719 | 1186221.1632 | 2644512.1585 | 1186247.2946
19 | 2644584.1056 | 1186188.3091 | 2644572.1737 | 1186196.1913 | 2644561.5471 | 1186204.0055 | 2644541.9719 | 1186221.1632
20 | 2644469.2767 | 1186282.2852 | 2644489.5155 | 1186266.5156 | 2644498.8887 | 1186258.9255 | 2644512.1585 | 1186247.2946
21 | 2644584.1056 | 1186188.3091 | 2644582.8888 | 1186185.7097 | 2644589.0474 | 1186182.5427 | 2644584.6683 | 1186173.1828
22 | 2644342.7545 | 1186431.885 | 2644342.4832 | 1186426.28 | 2644342.1073 | 1186421.3856 | 2644343.3706 | 1186416.6924 | 2644354.9183 | 1186404.9492 | 2644359.4894 | 1186395.6002 | 2644363.2351 | 1186387.4679 | 2644368.1829 | 1186366.4042 | 2644373.6784 | 1186358.9741 | 2644383.4221 | 1186353.8657 | 2644391.3382 | 1186351.3563 | 2644393.777 | 1186353.8201 | 2644397.8243 | 1186359.5643 | 2644405.1889 | 1186360.4305 | 2644417.538 | 1186350.7389 | 2644430.5946 | 1186329.0016 | 2644469.294 | 1186299.4947 | 2644469.2767 | 1186282.2852
23 | 2644564.7109 | 1186168.4985 | 2644576.5426 | 1186164.8512 | 2644579.3635 | 1186163.1379 | 2644584.6683 | 1186173.1828
24 | 2644342.7545 | 1186431.885 | 2644355.578 | 1186440.5513 | 2644362.2919 | 1186445.8038
25 | 2644804.8151 | 1186643.2835 | 2645061.3403 | 1187078.1316
26 | 2645061.3403 | 1187078.1316 | 2645351.9547 | 1187558.0516
27 | 2645348.7433 | 1187580.1475 | 2645348.8099 | 1187571.3556 | 2645349.2546 | 1187565.0111 | 2645351.9547 | 1187558.0516
28 | 2644362.2919 | 1186445.8038 | 2644343.6039 | 1186459.1453
29 | 2644362.2919 | 1186445.8038 | 2644369.1217 | 1186449.8343 | 2644375.644 | 1186453.14 | 2644380.8952 | 1186455.0655
30 | 2643629.118 | 1186738.0193 | 2643633.2617 | 1186742.4927 | 2643639.1723 | 1186748.0943 | 2643644.0718 | 1186752.1322 | 2643649.0374 | 1186755.0136
31 | 2643629.118 | 1186738.0193 | 2643623.1325 | 1186731.5574 | 2643605.7621 | 1186711.9853
32 | 2643726.7687 | 1186871.2243 | 2643691.161 | 1186784.9041 | 2643687.0807 | 1186778.4042 | 2643683.58 | 1186774.0207 | 2643679.1425 | 1186770.4642 | 2643666.404 | 1186763.7122 | 2643657.9625 | 1186759.9153 | 2643650.9402 | 1186756.1177 | 2643649.0374 | 1186755.0136
33 | 2643605.7621 | 1186711.9853 | 2643592.7112 | 1186697.2802
34 | 2643731.4636 | 1186882.6057 | 2643726.7687 | 1186871.2243
35 | 2643549.6226 | 1186652.2132 | 2643556.0337 | 1186657.2069 | 2643562.0291 | 1186662.709 | 2643592.7112 | 1186697.2802
36 | 2643731.4636 | 1186882.6057 | 2643732.2265 | 1186884.4551
37 | 2643549.6226 | 1186652.2132 | 2643551.3829 | 1186649.38 | 2643553.6529 | 1186646.7395 | 2643557.3455 | 1186645.7436 | 2643561.4364 | 1186645.5732 | 2643565.3253 | 1186645.9016
38 | 2643845.9846 | 1186954.3305 | 2643846.8185 | 1186948.4963 | 2643848.3134 | 1186942.3038 | 2643851.1169 | 1186933.4973 | 2643853.4611 | 1186927.072
39 | 2643893.7203 | 1186881.5253 | 2643887.7033 | 1186885.3055 | 2643882.8383 | 1186889.0942 | 2643875.8424 | 1186895.2574 | 2643869.0754 | 1186902.4785 | 2643865.4958 | 1186906.8213 | 2643860.9015 | 1186913.2468 | 2643856.924 | 1186919.8213 | 2643853.9121 | 1186925.8358 | 2643853.4611 | 1186927.072
40 | 2643893.7203 | 1186881.5253 | 2643884.9439 | 1186868.2871
41 | 2643893.7203 | 1186881.5253 | 2643898.9688 | 1186878.5065 | 2643909.4047 | 1186873.5136 | 2643961.0286 | 1186854.6594 | 2643979.1562 | 1186847.4885 | 2643996.5749 | 1186838.1445 | 2644010.51 | 1186826.2959 | 2644025.2713 | 1186808.9726 | 2644037.5108 | 1186785.9611 | 2644039.8577 | 1186781.198 | 2644039.9716 | 1186780.966
42 | 2643793.22 | 1186973.9464 | 2643796.2065 | 1186977.2975 | 2643799.2248 | 1186981.8888 | 2643800.0537 | 1186983.4946
43 | 2643793.22 | 1186973.9464 | 2643791.9384 | 1186972.5082 | 2643791.5969 | 1186972.2031
44 | 2643800.0537 | 1186983.4946 | 2643801.8804 | 1186987.0332 | 2643805.0108 | 1186996.1166 | 2643805.9137 | 1187000.285
45 | 2643760.1563 | 1186942.2704 | 2643762.8734 | 1186945.8592 | 2643767.9957 | 1186951.7443 | 2643775.6903 | 1186958.5264 | 2643785.465 | 1186966.7244 | 2643791.5969 | 1186972.2031
46 | 2643759.033 | 1186940.7867 | 2643760.1563 | 1186942.2704
47 | 2643759.033 | 1186940.7867 | 2643757.5837 | 1186938.8724 | 2643753.1708 | 1186931.9697 | 2643748.9531 | 1186923.4009 | 2643733.1154 | 1186886.6098 | 2643732.2265 | 1186884.4551
48 | 2643649.2768 | 1186695.3725 | 2643649.2768 | 1186695.3725 | 2643636.8438 | 1186688.5561 | 2643605.8762 | 1186669.3536 | 2643591.8884 | 1186660.0889
49 | 2643649.2768 | 1186695.3725 | 2643654.0754 | 1186697.5531 | 2643659.4904 | 1186698.9155 | 2643664.5038 | 1186698.852 | 2643664.5038 | 1186698.852
50 | 2643565.3253 | 1186645.9016 | 2643565.3253 | 1186645.9016 | 2643569.0037 | 1186646.8511 | 2643574.1 | 1186649.0338 | 2643578.7904 | 1186651.4136 | 2643591.8884 | 1186660.0889
51 | 2643674.722 | 1186695.1191 | 2643669.1096 | 1186698.174 | 2643664.5038 | 1186698.852
52 | 2643687.7138 | 1186687.3926 | 2643685.273 | 1186689.3759 | 2643674.722 | 1186695.1191
53 | 2643687.7138 | 1186687.3926 | 2643665.2482 | 1186656.3787 | 2643650.3743 | 1186621.9878
54 | 2643687.7138 | 1186687.3926 | 2643689.2238 | 1186685.3914 | 2643690.3776 | 1186683.0763 | 2643691.1827 | 1186680.4363 | 2643692.7021 | 1186672.9767 | 2643693.852 | 1186670.1391 | 2643696.1497 | 1186666.854 | 2643698.2071 | 1186665.1347 | 2643702.9279 | 1186663.3348 | 2643708.6622 | 1186662.7652 | 2643721.5571 | 1186662.7481 | 2643728.2078 | 1186663.108 | 2643734.4444 | 1186663.7649 | 2643737.5487 | 1186664.2021
55 | 2643687.7138 | 1186687.3926 | 2643698.0943 | 1186702.3102
56 | 2643732.9541 | 1186752.4065 | 2643698.0943 | 1186702.3102
57 | 2643826.7281 | 1186860.0457 | 2643806.7518 | 1186857.1314 | 2643801.2543 | 1186850.3764 | 2643785.2488 | 1186843.8782 | 2643784.5009 | 1186855.379 | 2643778.7529 | 1186870.3785 | 2643780.9993 | 1186880.3781 | 2643769.752 | 1186871.1243 | 2643768.2489 | 1186853.3815 | 2643753.7483 | 1186835.1212 | 2643755.7469 | 1186804.8749 | 2643744.4986 | 1186775.877 | 2643736.4989 | 1186764.8794 | 2643734.4984 | 1186754.6258 | 2643732.9541 | 1186752.4065
58 | 2643826.7281 | 1186860.0457 | 2643835.6564 | 1186859.8442 | 2643861.9958 | 1186860.6817 | 2643876.3813 | 1186861.2651 | 2643884.9439 | 1186868.2871
59 | 2643826.7281 | 1186860.0457 | 2643820.6951 | 1186862.8809 | 2643816.9288 | 1186869.8016 | 2643816.7487 | 1186885.0437
60 | 2643884.9439 | 1186868.2871 | 2643890.2304 | 1186859.0319 | 2643896.3679 | 1186853.9903
61 | 2643632.5172 | 1186580.6993 | 2643650.3743 | 1186621.9878
62 | 2643764.6801 | 1186670.3113 | 2643757.122 | 1186668.822 | 2643749.6689 | 1186666.5331 | 2643742.1047 | 1186664.8436 | 2643737.5487 | 1186664.2021
63 | 2643908.277 | 1186844.2074 | 2643896.3679 | 1186853.9903
64 | 2643632.5172 | 1186580.6993 | 2643632.274 | 1186585.8003 | 2643630.7602 | 1186589.3578 | 2643629.1585 | 1186592.4145 | 2643627.1896 | 1186595.613 | 2643624.4541 | 1186598.239 | 2643620.6553 | 1186600.2013 | 2643616.9148 | 1186601.497 | 2643613.1688 | 1186602.4925 | 2643608.8169 | 1186602.8722 | 2643602.737 | 1186601.6495 | 2643596.9728 | 1186600.029 | 2643589.9277 | 1186597.2206 | 2643582.9947 | 1186593.7017
65 | 2643632.5172 | 1186580.6993 | 2643632.1964 | 1186575.4941 | 2643630.5921 | 1186570.5353 | 2643628.4277 | 1186565.9837 | 2643625.3039 | 1186559.0795 | 2643621.6666 | 1186552.4716 | 2643612.6049 | 1186539.4986 | 2643594.9902 | 1186513.8677 | 2643586.431 | 1186501.0096 | 2643578.1862 | 1186487.9425 | 2643561.0836 | 1186462.1598
66 | 2643612.1903 | 1186639.8559 | 2643601.8677 | 1186623.5374
67 | 2643582.9947 | 1186593.7017 | 2643601.8677 | 1186623.5374
68 | 2643351.1695 | 1186003.5402 | 2643350.9629 | 1186004.177 | 2643343.4046 | 1186030.0253 | 2643331.1714 | 1186109.3132 | 2643330.3025 | 1186139.075
69 | 2643550.9569 | 1186451.1927 | 2643330.3025 | 1186139.075
70 | 2643561.0836 | 1186462.1598 | 2643555.6107 | 1186455.0829 | 2643550.9569 | 1186451.1927
71 | 2643901.8021 | 1186996.2922 | 2643896.5026 | 1187002.6783 | 2643890.7016 | 1187010.3066 | 2643889.3643 | 1187012.4794
72 | 2643918.9129 | 1186977.4329 | 2643908.3669 | 1186989.1022 | 2643905.0686 | 1186992.5355 | 2643901.9678 | 1186996.0925 | 2643901.8021 | 1186996.2922
73 | 2643918.9129 | 1186977.4329 | 2643920.6433 | 1186975.5181 | 2643944.9924 | 1186948.0594 | 2643950.2386 | 1186944.318 | 2643955.1075 | 1186941.192
74 | 2644256.7908 | 1187029.8677 | 2644248.1085 | 1187052.7461 | 2644219.6175 | 1187118.1938 | 2644217.0417 | 1187126.0569 | 2644213.0746 | 1187138.4519
75 | 2644204.4958 | 1187169.4375 | 2644210.0132 | 1187148.017 | 2644213.0746 | 1187138.4519
76 | 2644380.8952 | 1186455.0655 | 2644382.1731 | 1186455.534 | 2644387.7971 | 1186456.4984 | 2644394.1368 | 1186456.6454 | 2644395.0879 | 1186456.6373
77 | 2644395.291 | 1186456.6355 | 2644395.0879 | 1186456.6373
78 | 2644395.291 | 1186456.6355 | 2644406.6284 | 1186456.5379 | 2644408.8478 | 1186456.4237
79 | 2644338.9419 | 1186462.4735 | 2644343.6039 | 1186459.1453
80 | 2644408.8478 | 1186456.4237 | 2644412.9855 | 1186456.2107
81 | 2644338.9419 | 1186462.4735 | 2644335.2906 | 1186465.0812 | 2644323.6622 | 1186478.9199
82 | 2644416.7476 | 1186456.0171 | 2644412.9855 | 1186456.2107
83 | 2644416.7476 | 1186456.0171 | 2644427.793 | 1186455.4487
84 | 2644427.793 | 1186455.4487 | 2644430.9859 | 1186455.2844 | 2644443.9993 | 1186453.7578 | 2644445.8092 | 1186453.4266
85 | 2644470.6929 | 1186448.4224 | 2644470.2328 | 1186448.5383 | 2644456.9043 | 1186451.3966 | 2644445.8092 | 1186453.4266
86 | 2644477.304 | 1186446.7565 | 2644470.6929 | 1186448.4224
87 | 2644477.304 | 1186446.7565 | 2644474.4697 | 1186454.4285 | 2644460.0113 | 1186481.2741
88 | 2644081.938 | 1186732.2362 | 2644084.0764 | 1186735.0757 | 2644087.8103 | 1186741.9402 | 2644088.8877 | 1186748.9853 | 2644087.7143 | 1186754.991 | 2644084.9609 | 1186768.3336 | 2644083.605 | 1186773.0583
89 | 2644083.605 | 1186773.0583 | 2644081.2805 | 1186781.158 | 2644076.8053 | 1186792.08
90 | 2644068.1537 | 1186810.8218 | 2644066.6109 | 1186814.0013 | 2644059.8017 | 1186829.2615
91 | 2644068.1537 | 1186810.8218 | 2644074.4047 | 1186797.9388 | 2644076.8053 | 1186792.08
92 | 2644059.8017 | 1186829.2615 | 2644052.0498 | 1186846.6343 | 2644043.2076 | 1186866.2578 | 2644038.0125 | 1186876.5252
93 | 2644038.0125 | 1186876.5252 | 2644038.0125 | 1186876.5252 | 2644035.0125 | 1186880.8834 | 2644035.0125 | 1186880.8834
94 | 2644023.488 | 1186892.1682 | 2644025.5358 | 1186890.3078 | 2644031.6111 | 1186884.8383 | 2644035.0125 | 1186880.8834
95 | 2644018.1484 | 1186896.9033 | 2644019.8672 | 1186895.4578 | 2644023.488 | 1186892.1682
96 | 2644018.1484 | 1186896.9033 | 2644008.6483 | 1186904.8929
97 | 2644006.7503 | 1186906.4891 | 2644005.557 | 1186907.4927 | 2644003.0277 | 1186909.5406
98 | 2644006.7503 | 1186906.4891 | 2644008.6483 | 1186904.8929
99 | 2644001.1478 | 1186911.0628 | 2644003.0277 | 1186909.5406
100 | 2644001.1478 | 1186911.0628 | 2643990.9432 | 1186919.3252 | 2643975.7596 | 1186928.5662
101 | 2643975.7596 | 1186928.5662 | 2643967.6066 | 1186933.5284 | 2643960.9512 | 1186937.5962
102 | 2643960.9512 | 1186937.5962 | 2643955.8882 | 1186940.6908 | 2643955.1075 | 1186941.192

## bus_geodata
| x | y | coords
0 | 2644118.071 | 1186586.628
1 | 2644104.4755 | 1186545.7964
2 | 2644119.7333 | 1186614.5724
3 | 2644302.4595 | 1186517.0289
4 | 2644074.8001 | 1186519.101
5 | 2644092.0817 | 1186672.6672
6 | 2644085.218 | 1186632.8062
7 | 2644067.0866 | 1186725.4566
8 | 2644392.3481 | 1186711.5929
9 | 2644274.9214 | 1186762.2525
10 | 2644606.1057 | 1186793.9138
11 | 2644264.3204 | 1186959.6024
12 | 2644099.1721 | 1186728.3497
13 | 2644259.8733 | 1187001.7358
14 | 2644541.9719 | 1186221.1632
15 | 2644512.1585 | 1186247.2946
16 | 2644584.1056 | 1186188.3091
17 | 2644469.2767 | 1186282.2852
18 | 2644584.6683 | 1186173.1828
19 | 2644342.7545 | 1186431.885
20 | 2644564.7109 | 1186168.4985
21 | 2644804.8151 | 1186643.2835
22 | 2645061.3403 | 1187078.1316
23 | 2645351.9547 | 1187558.0516
24 | 2644362.2919 | 1186445.8038
25 | 2643629.118 | 1186738.0193
26 | 2643649.0374 | 1186755.0136
27 | 2643605.7621 | 1186711.9853
28 | 2643726.7687 | 1186871.2243
29 | 2643592.7112 | 1186697.2802
30 | 2643731.4636 | 1186882.6057
31 | 2643549.6226 | 1186652.2132
32 | 2643845.9846 | 1186954.3305
33 | 2643853.4611 | 1186927.072
34 | 2643893.7203 | 1186881.5253
35 | 2643793.22 | 1186973.9464
36 | 2643800.0537 | 1186983.4946
37 | 2643791.5969 | 1186972.2031
38 | 2643805.9137 | 1187000.285
39 | 2643760.1563 | 1186942.2704
40 | 2643759.033 | 1186940.7867
41 | 2643649.2768 | 1186695.3725
42 | 2643591.8884 | 1186660.0889
43 | 2643664.5038 | 1186698.852
44 | 2643565.3253 | 1186645.9016
45 | 2643674.722 | 1186695.1191
46 | 2643687.7138 | 1186687.3926
47 | 2643732.9541 | 1186752.4065
48 | 2643698.0943 | 1186702.3102
49 | 2643826.7281 | 1186860.0457
50 | 2643884.9439 | 1186868.2871
51 | 2643816.7487 | 1186885.0437
52 | 2643650.3743 | 1186621.9878
53 | 2643737.5487 | 1186664.2021
54 | 2643896.3679 | 1186853.9903
55 | 2643764.6801 | 1186670.3113
56 | 2643632.5172 | 1186580.6993
57 | 2643612.1903 | 1186639.8559
58 | 2643601.8677 | 1186623.5374
59 | 2643582.9947 | 1186593.7017
60 | 2643330.3025 | 1186139.075
61 | 2643351.1695 | 1186003.5402
62 | 2643550.9569 | 1186451.1927
63 | 2643732.2265 | 1186884.4551
64 | 2643561.0836 | 1186462.1598
65 | 2643889.3643 | 1187012.4794
66 | 2643901.8021 | 1186996.2922
67 | 2643918.9129 | 1186977.4329
68 | 2644213.0746 | 1187138.4519
69 | 2644256.7908 | 1187029.8677
70 | 2644204.4958 | 1187169.4375
71 | 2644380.8952 | 1186455.0655
72 | 2644395.0879 | 1186456.6373
73 | 2644395.291 | 1186456.6355
74 | 2644343.6039 | 1186459.1453
75 | 2644408.8478 | 1186456.4237
76 | 2644338.9419 | 1186462.4735
77 | 2644412.9855 | 1186456.2107
78 | 2644416.7476 | 1186456.0171
79 | 2644323.6622 | 1186478.9199
80 | 2644427.793 | 1186455.4487
81 | 2644445.8092 | 1186453.4266
82 | 2644470.6929 | 1186448.4224
83 | 2644477.304 | 1186446.7565
84 | 2644460.0113 | 1186481.2741
85 | 2644039.9716 | 1186780.966
86 | 2644081.938 | 1186732.2362
87 | 2644083.605 | 1186773.0583
88 | 2645348.7433 | 1187580.1475
89 | 2644068.1537 | 1186810.8218
90 | 2644059.8017 | 1186829.2615
91 | 2644076.8053 | 1186792.08
92 | 2644038.0125 | 1186876.5252
93 | 2644035.0125 | 1186880.8834
94 | 2644023.488 | 1186892.1682
95 | 2644018.1484 | 1186896.9033
96 | 2644006.7503 | 1186906.4891
97 | 2644003.0277 | 1186909.5406
98 | 2644008.6483 | 1186904.8929
99 | 2644001.1478 | 1186911.0628
100 | 2643975.7596 | 1186928.5662
101 | 2643960.9512 | 1186937.5962
102 | 2643955.1075 | 1186941.192
103 | 2643908.277 | 1186844.2074
104 | 2644081.938 | 1186732.2362

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99181 | -0.057414 | 0.0015104 | 0.00037853
1 | 0.99124 | -0.061409 | 0.0025236 | 0.00063246
2 | 0.99258 | -0.051932 | 0 | 0
3 | 0.98927 | -0.075469 | 0.00048142 | 0.00012065
4 | 0.99065 | -0.065572 | 0.0051193 | 0.001283
5 | 0.99426 | -0.040102 | 0 | 0
6 | 0.99059 | -0.065967 | 0.050221 | 0.012587
7 | 1 | 0 | -0.14195 | -0.035472
8 | 0.99729 | -0.019664 | 0.00026813 | 6.7199e-05
9 | 0.99761 | -0.017205 | 0 | 0
10 | 0.99681 | -0.023414 | 0.00080623 | 0.00020206
11 | 0.99642 | -0.025637 | 0.00048926 | 0.00012262
12 | 0.99911 | -0.0063029 | 0.0063431 | 0.0015897
13 | 0.9962 | -0.027187 | 0.00075267 | 0.00018864
14 | 0.98608 | -0.098229 | 0.001696 | 0.00042505
15 | 0.98626 | -0.096933 | 0.0011069 | 0.00027741
16 | 0.98596 | -0.099046 | 0 | 0
17 | 0.9866 | -0.094493 | 0 | 0
18 | 0.98592 | -0.099352 | 0 | 0
19 | 0.988 | -0.084517 | 0 | 0
20 | 0.98586 | -0.099762 | 0.0014787 | 0.00037061
21 | 0.99655 | -0.025531 | 6.8521e-05 | 1.7173e-05
22 | 0.99611 | -0.029059 | 0.0003616 | 9.0626e-05
23 | 0.99591 | -0.030649 | 6.9344e-05 | 1.7379e-05
24 | 0.98815 | -0.083458 | 0 | 0
25 | 0.97521 | -0.17508 | 0.0011972 | 0.00030005
26 | 0.97482 | -0.1779 | 0.001179 | 0.00029548
27 | 0.9758 | -0.17091 | 0.00086008 | 0.00021556
28 | 0.9729 | -0.19174 | 0.0017813 | 0.00044645
29 | 0.97615 | -0.16838 | 0.00033823 | 8.4768e-05
30 | 0.97277 | -0.19268 | 0.0011383 | 0.00028529
31 | 0.9773 | -0.16015 | 0 | 0
32 | 0.99273 | -0.050707 | 0.0021705 | 0.00054398
33 | 0.99282 | -0.050084 | 0.0027383 | 0.00068628
34 | 0.99326 | -0.047013 | 0 | 0
35 | 0.97198 | -0.19836 | 0.0018112 | 0.00045393
36 | 0.97196 | -0.19852 | 0.00062639 | 0.00015699
37 | 0.97199 | -0.19828 | 0.00058861 | 0.00014752
38 | 0.97194 | -0.19864 | 0.0006487 | 0.00016258
39 | 0.97223 | -0.19659 | 0.00061709 | 0.00015466
40 | 0.97224 | -0.19651 | 0.0013068 | 0.00032751
41 | 0.97952 | -0.14424 | 0.0010002 | 0.00025067
42 | 0.97821 | -0.15361 | 0.0004204 | 0.00010536
43 | 0.97985 | -0.14187 | 0.00097293 | 0.00024384
44 | 0.97764 | -0.1577 | 0.00032856 | 8.2346e-05
45 | 0.9801 | -0.14011 | 0.00064788 | 0.00016237
46 | 0.98045 | -0.1376 | 0 | 0
47 | 0.98295 | -0.11977 | 0.00058891 | 0.0001476
48 | 0.98102 | -0.13357 | 0.00048721 | 0.00012211
49 | 0.99036 | -0.067342 | 0 | 0
50 | 0.99257 | -0.051848 | 0 | 0
51 | 0.99024 | -0.068168 | 0.0027256 | 0.00068309
52 | 0.98027 | -0.13897 | 0.00041288 | 0.00010348
53 | 0.98011 | -0.14004 | 0.00042778 | 0.00010721
54 | 0.99244 | -0.052771 | 0.0025925 | 0.00064973
55 | 0.97998 | -0.14096 | 0.0031881 | 0.00079902
56 | 0.98019 | -0.13959 | 0 | 0
57 | 0.9801 | -0.14024 | 0.00025513 | 6.3941e-05
58 | 0.98011 | -0.14019 | 0.00032338 | 8.1048e-05
59 | 0.98014 | -0.13998 | 0 | 0
60 | 0.97982 | -0.14248 | 0.00020834 | 5.2215e-05
61 | 0.97978 | -0.14277 | 0.00019704 | 4.9383e-05
62 | 0.98004 | -0.14075 | 0.00026417 | 6.6206e-05
63 | 0.97275 | -0.19281 | 0.00045915 | 0.00011507
64 | 0.98006 | -0.14064 | 0 | 0
65 | 0.9972 | -0.019725 | 0.00050363 | 0.00012622
66 | 0.99722 | -0.019621 | 0.00054606 | 0.00013686
67 | 0.99725 | -0.019352 | 0.00039178 | 9.8189e-05
68 | 0.9957 | -0.030726 | 0.0010022 | 0.00025116
69 | 0.99608 | -0.028009 | 0.00057163 | 0.00014326
70 | 0.99564 | -0.031146 | 0.0012945 | 0.00032443
71 | 0.98805 | -0.084136 | 0.00042739 | 0.00010711
72 | 0.988 | -0.084541 | 0.00038999 | 9.774e-05
73 | 0.98799 | -0.084546 | 0.00016487 | 4.1319e-05
74 | 0.98839 | -0.081696 | 0.00015475 | 3.8783e-05
75 | 0.98795 | -0.084851 | 0.0001446 | 3.6241e-05
76 | 0.98846 | -0.081247 | 0 | 0
77 | 0.98794 | -0.084938 | 0.00012165 | 3.0488e-05
78 | 0.98793 | -0.085012 | 0.00045046 | 0.0001129
79 | 0.98871 | -0.079481 | 0.00084205 | 0.00021104
80 | 0.98791 | -0.085179 | 0.00027553 | 6.9055e-05
81 | 0.98787 | -0.085403 | 8.584e-05 | 2.1514e-05
82 | 0.98783 | -0.085692 | 0.000724 | 0.00018145
83 | 0.98783 | -0.085719 | 0 | 0
84 | 0.98781 | -0.085873 | 0.00038568 | 9.6661e-05
85 | 0.99792 | -0.014471 | 0.01179 | 0.0029549
86 | 0.99942 | -0.004091 | 0 | 0
87 | 0.99864 | -0.0095772 | 0.003349 | 0.00083935
88 | 0.9959 | -0.030691 | 0.00018287 | 4.5832e-05
89 | 0.99818 | -0.012811 | 0.0022744 | 0.00057003
90 | 0.99806 | -0.013662 | 0.00022224 | 5.5699e-05
91 | 0.99837 | -0.011473 | 0.0028895 | 0.00072419
92 | 0.99777 | -0.015731 | 0.00018911 | 4.7394e-05
93 | 0.99774 | -0.015932 | 0.00022547 | 5.6509e-05
94 | 0.99766 | -0.016507 | 0.00018611 | 4.6642e-05
95 | 0.99762 | -0.016747 | 0.00020475 | 5.1314e-05
96 | 0.99756 | -0.017213 | 0.00017759 | 4.4509e-05
97 | 0.99754 | -0.017347 | 0.00021539 | 5.3981e-05
98 | 0.99757 | -0.01714 | 0.00021539 | 5.3981e-05
99 | 0.99753 | -0.017409 | 0.00022813 | 5.7174e-05
100 | 0.99743 | -0.018127 | 0.00026526 | 6.648e-05
101 | 0.99738 | -0.018483 | 0.00030224 | 7.5748e-05
102 | 0.99736 | -0.018603 | 0.00029445 | 7.3795e-05
103 | 0.99239 | -0.053132 | 0.0023069 | 0.00057816
104 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00765 | 0.0019165 | -0.0076458 | -0.0019156 | 4.2272e-06 | 9.6254e-07 | 0.011477 | 0.011477 | 0.011477 | 0.99181 | -0.057414 | 0.99124 | -0.061409 | 4.2509
1 | -0.018131 | -0.0045372 | 0.018145 | 0.0045421 | 1.3727e-05 | 4.8955e-06 | 0.027199 | 0.027199 | 0.027199 | 0.99181 | -0.057414 | 0.99258 | -0.051932 | 10.0738
2 | 0.0089704 | 0.0022422 | -0.0089482 | -0.0022361 | 2.227e-05 | 6.0284e-06 | 0.013456 | 0.013457 | 0.013457 | 0.99181 | -0.057414 | 0.98927 | -0.075469 | 4.9841
3 | 0.0051222 | 0.0012831 | -0.0051193 | -0.001283 | 2.9494e-06 | 1.0448e-07 | 0.007689 | 0.0076894 | 0.0076894 | 0.99124 | -0.061409 | 0.99065 | -0.065572 | 2.8479
4 | -0.018145 | -0.0045421 | 0.018174 | 0.0045527 | 2.9691e-05 | 1.0587e-05 | 0.027199 | 0.027199 | 0.027199 | 0.99258 | -0.051932 | 0.99426 | -0.040102 | 10.0738
5 | 0.0084667 | 0.0021155 | -0.0084621 | -0.0021143 | 4.6728e-06 | 1.2046e-06 | 0.012733 | 0.012733 | 0.012733 | 0.98927 | -0.075469 | 0.98871 | -0.079481 | 4.716
6 | 0.050402 | 0.012655 | -0.050221 | -0.012587 | 0.00018048 | 6.876e-05 | 0.07544 | 0.07544 | 0.07544 | 0.99426 | -0.040102 | 0.99059 | -0.065967 | 27.9409
7 | -0.068576 | -0.017208 | 0.06896 | 0.017355 | 0.00038384 | 0.00014687 | 0.10264 | 0.10264 | 0.10264 | 0.99426 | -0.040102 | 1 | 0 | 38.0145
8 | 0.024942 | 0.0062225 | -0.024928 | -0.0062174 | 1.3991e-05 | 5.1677e-06 | 0.037104 | 0.037104 | 0.037104 | 1 | 0 | 0.99942 | -0.004091 | 13.7421
9 | 0.047247 | 0.011894 | -0.047151 | -0.011859 | 9.532e-05 | 3.5044e-05 | 0.070323 | 0.070323 | 0.070323 | 1 | 0 | 0.99792 | -0.014471 | 13.0228
10 | -0.0017579 | -0.00042014 | 0.0017584 | 0.00041868 | 5.4593e-07 | -1.4593e-06 | 0.0026158 | 0.0026153 | 0.0026158 | 0.99729 | -0.019664 | 0.99761 | -0.017205 | 0.96883
11 | 0.0014898 | 0.00035294 | -0.0014891 | -0.00035566 | 7.0209e-07 | -2.7174e-06 | 0.0022158 | 0.0022168 | 0.0022168 | 0.99729 | -0.019664 | 0.99681 | -0.023414 | 0.82104
12 | 0.004117 | 0.0010272 | -0.0041122 | -0.001028 | 4.7699e-06 | -8.0992e-07 | 0.0061392 | 0.0061402 | 0.0061402 | 0.99761 | -0.017205 | 0.99642 | -0.025637 | 2.2741
13 | -0.0058754 | -0.0014459 | 0.005884 | 0.0014469 | 8.559e-06 | 9.5141e-07 | 0.0087544 | 0.0087536 | 0.0087544 | 0.99761 | -0.017205 | 0.99911 | -0.0063029 | 3.2424
14 | 0.00068282 | 0.0001536 | -0.00068266 | -0.00015696 | 1.6876e-07 | -3.3631e-06 | 0.0010134 | 0.0010145 | 0.0010145 | 0.99681 | -0.023414 | 0.99655 | -0.025531 | 0.37575
15 | 0.003623 | 0.00090542 | -0.0036222 | -0.00090567 | 7.7366e-07 | -2.5417e-07 | 0.0054095 | 0.0054097 | 0.0054097 | 0.99642 | -0.025637 | 0.9962 | -0.027187 | 2.0036
16 | -0.012227 | -0.0030366 | 0.012231 | 0.0030378 | 3.6786e-06 | 1.1817e-06 | 0.018201 | 0.018201 | 0.018201 | 0.99911 | -0.0063029 | 0.99942 | -0.004091 | 6.741
17 | 0.0028695 | 0.00071703 | -0.0028692 | -0.00071728 | 3.2449e-07 | -2.438e-07 | 0.0042855 | 0.0042856 | 0.0042856 | 0.9962 | -0.027187 | 0.99608 | -0.028009 | 1.5873
18 | -0.003175 | -0.0007945 | 0.0031756 | 0.00079421 | 5.6776e-07 | -2.8745e-07 | 0.0047908 | 0.0047906 | 0.0047908 | 0.98608 | -0.098229 | 0.98626 | -0.096933 | 1.7744
19 | 0.001479 | 0.00036944 | -0.0014789 | -0.00037006 | 1.6632e-07 | -6.1869e-07 | 0.0022315 | 0.0022317 | 0.0022317 | 0.98608 | -0.098229 | 0.98596 | -0.099046 | 0.82657
20 | -0.0042825 | -0.0010716 | 0.0042839 | 0.0010715 | 1.4419e-06 | -1.5217e-07 | 0.0064606 | 0.0064603 | 0.0064606 | 0.98626 | -0.096933 | 0.9866 | -0.094493 | 2.3928
21 | 0.0014789 | 0.00037006 | -0.0014788 | -0.00037029 | 6.2499e-08 | -2.3241e-07 | 0.0022317 | 0.0022318 | 0.0022318 | 0.98596 | -0.099046 | 0.98592 | -0.099352 | 0.8266
22 | -0.0042839 | -0.0010715 | 0.0042898 | 0.0010708 | 5.885e-06 | -6.2675e-07 | 0.0064603 | 0.0064593 | 0.0064603 | 0.9866 | -0.094493 | 0.988 | -0.084517 | 2.3927
23 | 0.0014788 | 0.00037029 | -0.0014787 | -0.00037061 | 8.3915e-08 | -3.1198e-07 | 0.0022318 | 0.0022319 | 0.0022319 | 0.98592 | -0.099352 | 0.98586 | -0.099762 | 0.82664
24 | -0.0042898 | -0.0010708 | 0.0042904 | 0.0010708 | 6.2371e-07 | -6.6958e-08 | 0.0064593 | 0.0064592 | 0.0064593 | 0.988 | -0.084517 | 0.98815 | -0.083458 | 2.3923
25 | 0.00061413 | 0.00013979 | -0.00061387 | -0.00014626 | 2.6279e-07 | -6.474e-06 | 0.00091224 | 0.00091441 | 0.00091441 | 0.99655 | -0.025531 | 0.99611 | -0.029059 | 0.33867
26 | 0.00025227 | 5.5635e-05 | -0.00025222 | -6.2918e-05 | 4.9363e-08 | -7.283e-06 | 0.00037432 | 0.00037674 | 0.00037674 | 0.99611 | -0.029059 | 0.99591 | -0.030649 | 0.13953
27 | 0.00018287 | 4.5539e-05 | -0.00018287 | -4.5832e-05 | 1.0533e-09 | -2.9389e-07 | 0.00027313 | 0.00027324 | 0.00027324 | 0.99591 | -0.030649 | 0.9959 | -0.030691 | 0.1012
28 | -0.0074611 | -0.0018635 | 0.0074629 | 0.0018639 | 1.808e-06 | 4.0116e-07 | 0.011233 | 0.011233 | 0.011233 | 0.98815 | -0.083458 | 0.98839 | -0.081696 | 4.1604
29 | 0.0031707 | 0.00079274 | -0.0031704 | -0.00079289 | 2.9632e-07 | -1.5291e-07 | 0.004774 | 0.0047741 | 0.0047741 | 0.98815 | -0.083458 | 0.98805 | -0.084136 | 1.7682
30 | 0.010183 | 0.0025514 | -0.010179 | -0.0025502 | 3.9663e-06 | 1.1971e-06 | 0.015537 | 0.015537 | 0.015537 | 0.97521 | -0.17508 | 0.97482 | -0.1779 | 5.7544
31 | -0.01138 | -0.0028515 | 0.011386 | 0.0028536 | 6.5802e-06 | 2.0942e-06 | 0.017364 | 0.017363 | 0.017364 | 0.97521 | -0.17508 | 0.9758 | -0.17091 | 6.431
32 | 0.0089997 | 0.0022548 | -0.0089825 | -0.00225 | 1.7217e-05 | 4.803e-06 | 0.013737 | 0.013738 | 0.013738 | 0.97482 | -0.1779 | 0.9729 | -0.19174 | 5.0881
33 | -0.012247 | -0.0030691 | 0.012251 | 0.0030705 | 4.2787e-06 | 1.4e-06 | 0.018675 | 0.018675 | 0.018675 | 0.9758 | -0.17091 | 0.97615 | -0.16838 | 6.9167
34 | 0.0072011 | 0.0018035 | -0.0072002 | -0.0018033 | 9.3187e-07 | 2.0555e-07 | 0.011013 | 0.011014 | 0.011014 | 0.9729 | -0.19174 | 0.97277 | -0.19268 | 4.0791
35 | -0.012589 | -0.0031553 | 0.012603 | 0.0031601 | 1.4359e-05 | 4.7408e-06 | 0.019191 | 0.01919 | 0.019191 | 0.97615 | -0.16838 | 0.9773 | -0.16015 | 7.1076
36 | 0.0060619 | 0.001518 | -0.0060618 | -0.001518 | 1.0733e-07 | 1.6444e-08 | 0.0092723 | 0.0092723 | 0.0092723 | 0.97277 | -0.19268 | 0.97275 | -0.19281 | 3.4342
37 | -0.012603 | -0.0031601 | 0.012608 | 0.0031615 | 4.2833e-06 | 1.4138e-06 | 0.01919 | 0.01919 | 0.01919 | 0.9773 | -0.16015 | 0.97764 | -0.1577 | 7.1075
38 | -0.0021705 | -0.00054398 | 0.0021707 | 0.00054369 | 1.8721e-07 | -2.9452e-07 | 0.0032534 | 0.0032533 | 0.0032534 | 0.99273 | -0.050707 | 0.99282 | -0.050084 | 1.205
39 | -0.004909 | -0.00123 | 0.0049111 | 0.00123 | 2.0855e-06 | 3.3116e-09 | 0.0073574 | 0.0073571 | 0.0073574 | 0.99282 | -0.050084 | 0.99326 | -0.047013 | 2.725
40 | 0.03029 | 0.0076178 | -0.03027 | -0.0076101 | 2.0401e-05 | 7.6414e-06 | 0.045387 | 0.045388 | 0.045388 | 0.99326 | -0.047013 | 0.99257 | -0.051848 | 16.8102
41 | -0.035201 | -0.0088477 | 0.035361 | 0.0089045 | 0.00016016 | 5.6801e-05 | 0.052745 | 0.052743 | 0.052745 | 0.99326 | -0.047013 | 0.99792 | -0.014471 | 9.7675
42 | 0.0012751 | 0.00031922 | -0.0012751 | -0.00031935 | 2.8034e-08 | -1.3535e-07 | 0.001952 | 0.001952 | 0.001952 | 0.97198 | -0.19836 | 0.97196 | -0.19852 | 0.72298
43 | -0.0030863 | -0.00077315 | 0.0030864 | 0.00077313 | 3.3214e-08 | -1.6778e-08 | 0.0047248 | 0.0047248 | 0.0047248 | 0.97198 | -0.19836 | 0.97199 | -0.19828 | 1.7499
44 | 0.00064871 | 0.00016236 | -0.0006487 | -0.00016258 | 1.0988e-08 | -2.1706e-07 | 0.00099307 | 0.00099315 | 0.00099315 | 0.97196 | -0.19852 | 0.97194 | -0.19864 | 0.36783
45 | -0.003675 | -0.00092065 | 0.0036758 | 0.00092044 | 8.5989e-07 | -2.0907e-07 | 0.0056259 | 0.0056257 | 0.0056259 | 0.97199 | -0.19828 | 0.97223 | -0.19659 | 2.0837
46 | -0.0042929 | -0.0010751 | 0.004293 | 0.0010751 | 5.0127e-08 | -3.7978e-09 | 0.0065701 | 0.0065701 | 0.0065701 | 0.97223 | -0.19659 | 0.97224 | -0.19651 | 2.4334
47 | -0.0055998 | -0.0014026 | 0.0056026 | 0.0014029 | 2.8658e-06 | 3.2638e-07 | 0.0085702 | 0.0085699 | 0.0085702 | 0.97224 | -0.19651 | 0.97275 | -0.19281 | 3.1741
48 | 0.013381 | 0.0033575 | -0.013364 | -0.0033516 | 1.738e-05 | 5.8376e-06 | 0.020329 | 0.02033 | 0.02033 | 0.97952 | -0.14424 | 0.97821 | -0.15361 | 7.5295
49 | -0.014382 | -0.0036081 | 0.014386 | 0.0036097 | 4.7268e-06 | 1.6182e-06 | 0.021849 | 0.021849 | 0.021849 | 0.97952 | -0.14424 | 0.97985 | -0.14187 | 8.0921
50 | 0.012944 | 0.0032463 | -0.012936 | -0.0032438 | 7.3335e-06 | 2.4403e-06 | 0.01969 | 0.01969 | 0.01969 | 0.97821 | -0.15361 | 0.97764 | -0.1577 | 7.2927
51 | -0.015359 | -0.0038536 | 0.015363 | 0.0038549 | 3.7502e-06 | 1.3032e-06 | 0.023326 | 0.023326 | 0.023326 | 0.97985 | -0.14187 | 0.9801 | -0.14011 | 8.6393
52 | -0.016011 | -0.0040173 | 0.016016 | 0.0040192 | 5.5896e-06 | 1.9587e-06 | 0.02431 | 0.02431 | 0.02431 | 0.9801 | -0.14011 | 0.98045 | -0.1376 | 9.0036
53 | 0.0016616 | 0.00040501 | -0.0016613 | -0.00040585 | 2.9973e-07 | -8.4005e-07 | 0.0025177 | 0.0025181 | 0.0025181 | 0.98045 | -0.1376 | 0.98027 | -0.13897 | 0.93261
54 | 0.0036176 | 0.00090569 | -0.0036163 | -0.00090604 | 1.2224e-06 | -3.4923e-07 | 0.0054899 | 0.0054902 | 0.0054902 | 0.98045 | -0.1376 | 0.98011 | -0.14004 | 2.0334
55 | -0.021296 | -0.0053299 | 0.021307 | 0.0053342 | 1.1844e-05 | 4.3261e-06 | 0.032317 | 0.032317 | 0.032317 | 0.98045 | -0.1376 | 0.98102 | -0.13357 | 11.9693
56 | 0.021836 | 0.0054716 | -0.021795 | -0.0054564 | 4.1614e-05 | 1.5233e-05 | 0.033056 | 0.033056 | 0.033056 | 0.98295 | -0.11977 | 0.98102 | -0.13357 | 12.243
57 | -0.022425 | -0.0056192 | 0.022589 | 0.0056793 | 0.00016385 | 6.0111e-05 | 0.033947 | 0.033946 | 0.033947 | 0.98295 | -0.11977 | 0.99036 | -0.067342 | 12.5731
58 | -0.025315 | -0.0063621 | 0.02537 | 0.0063824 | 5.4716e-05 | 2.0263e-05 | 0.038042 | 0.038042 | 0.038042 | 0.99036 | -0.067342 | 0.99257 | -0.051848 | 14.0896
59 | 0.0027259 | 0.00068283 | -0.0027256 | -0.00068309 | 3.1179e-07 | -2.6334e-07 | 0.0040955 | 0.0040957 | 0.0040957 | 0.99036 | -0.067342 | 0.99024 | -0.068168 | 1.5169
60 | 0.0049001 | 0.0012277 | -0.0048995 | -0.0012277 | 6.2636e-07 | 5.179e-10 | 0.0073459 | 0.007346 | 0.007346 | 0.99257 | -0.051848 | 0.99244 | -0.052771 | 2.7207
61 | 0.0012484 | 0.00030237 | -0.0012483 | -0.0003029 | 1.0042e-07 | -5.2844e-07 | 0.0018913 | 0.0018915 | 0.0018915 | 0.98027 | -0.13897 | 0.98019 | -0.13959 | 0.70057
62 | 0.0031885 | 0.00079883 | -0.0031881 | -0.00079902 | 4.0726e-07 | -1.9432e-07 | 0.0048408 | 0.0048409 | 0.0048409 | 0.98011 | -0.14004 | 0.97998 | -0.14096 | 1.7929
63 | 0.002307 | 0.00057801 | -0.0023069 | -0.00057816 | 1.1507e-07 | -1.5488e-07 | 0.003459 | 0.003459 | 0.003459 | 0.99244 | -0.052771 | 0.99239 | -0.053132 | 1.2811
64 | 0.00057856 | 0.00014351 | -0.00057853 | -0.00014431 | 3.0721e-08 | -7.9329e-07 | 0.00087778 | 0.00087807 | 0.00087807 | 0.98019 | -0.13959 | 0.98014 | -0.13998 | 0.32521
65 | 0.00066974 | 0.00015939 | -0.00066965 | -0.00016111 | 8.9361e-08 | -1.7207e-06 | 0.0010138 | 0.0010144 | 0.0010144 | 0.98019 | -0.13959 | 0.98006 | -0.14064 | 0.37569
66 | -0.00025513 | -6.3941e-05 | 0.00025513 | 6.3699e-05 | 1.8074e-09 | -2.4265e-07 | 0.00038734 | 0.00038726 | 0.00038734 | 0.9801 | -0.14024 | 0.98011 | -0.14019 | 0.14346
67 | -0.00057851 | -0.00014475 | 0.00057853 | 0.00014431 | 1.6988e-08 | -4.384e-07 | 0.00087822 | 0.00087807 | 0.00087822 | 0.98011 | -0.14019 | 0.98014 | -0.13998 | 0.32527
68 | 0.00019705 | 4.7653e-05 | -0.00019704 | -4.9383e-05 | 7.6735e-09 | -1.7301e-06 | 0.00029864 | 0.00029925 | 0.00029925 | 0.97982 | -0.14248 | 0.97978 | -0.14277 | 0.11083
69 | -0.00040539 | -9.9868e-05 | 0.00040548 | 9.5087e-05 | 8.9978e-08 | -4.7808e-06 | 0.00061504 | 0.00061338 | 0.00061504 | 0.97982 | -0.14248 | 0.98004 | -0.14075 | 0.22779
70 | -0.00066964 | -0.00016129 | 0.00066965 | 0.00016111 | 9.6392e-09 | -1.8546e-07 | 0.0010144 | 0.0010144 | 0.0010144 | 0.98004 | -0.14075 | 0.98006 | -0.14064 | 0.37572
71 | -0.00050363 | -0.00012622 | 0.00050363 | 0.00012596 | 7.2001e-09 | -2.6381e-07 | 0.00075151 | 0.00075141 | 0.00075151 | 0.9972 | -0.019725 | 0.99722 | -0.019621 | 0.27834
72 | -0.0010497 | -0.00026281 | 0.0010497 | 0.0002625 | 3.8982e-08 | -3.1728e-07 | 0.0015662 | 0.0015661 | 0.0015662 | 0.99722 | -0.019621 | 0.99725 | -0.019352 | 0.58009
73 | -0.0014415 | -0.00036069 | 0.0014417 | 0.00036007 | 1.4866e-07 | -6.1496e-07 | 0.0021507 | 0.0021505 | 0.0021507 | 0.99725 | -0.019352 | 0.99736 | -0.018603 | 0.79655
74 | -0.0022967 | -0.0005752 | 0.0022976 | 0.00057401 | 8.6092e-07 | -1.1931e-06 | 0.0034322 | 0.0034316 | 0.0034322 | 0.9957 | -0.030726 | 0.99608 | -0.028009 | 1.2712
75 | 0.0012946 | 0.00032404 | -0.0012945 | -0.00032443 | 7.5113e-08 | -3.8941e-07 | 0.0019345 | 0.0019347 | 0.0019347 | 0.9957 | -0.030726 | 0.99564 | -0.031146 | 0.71654
76 | 0.002743 | 0.00068578 | -0.0027429 | -0.00068591 | 1.5287e-07 | -1.2511e-07 | 0.0041304 | 0.0041305 | 0.0041305 | 0.98805 | -0.084136 | 0.988 | -0.084541 | 1.5298
77 | 0.0023529 | 0.00058817 | -0.0023529 | -0.00058817 | 1.5915e-09 | -1.9891e-09 | 0.0035431 | 0.0035431 | 0.0035431 | 0.988 | -0.084541 | 0.98799 | -0.084546 | 1.3123
78 | 0.002188 | 0.00054685 | -0.0021879 | -0.00054699 | 9.1859e-08 | -1.3832e-07 | 0.0032948 | 0.0032949 | 0.0032949 | 0.98799 | -0.084546 | 0.98795 | -0.084851 | 1.2203
79 | -0.0076177 | -0.0019027 | 0.0076182 | 0.0019028 | 4.6992e-07 | 1.0732e-07 | 0.011466 | 0.011466 | 0.011466 | 0.98839 | -0.081696 | 0.98846 | -0.081247 | 4.2467
80 | 0.0020433 | 0.00051075 | -0.0020433 | -0.00051079 | 2.448e-08 | -4.3638e-08 | 0.0030771 | 0.0030771 | 0.0030771 | 0.98795 | -0.084851 | 0.98794 | -0.084938 | 1.1397
81 | -0.0076182 | -0.0019028 | 0.00762 | 0.0019032 | 1.851e-06 | 4.2262e-07 | 0.011466 | 0.011466 | 0.011466 | 0.98846 | -0.081247 | 0.98871 | -0.079481 | 4.2467
82 | 0.0019217 | 0.0004803 | -0.0019216 | -0.00048034 | 1.9686e-08 | -4.0664e-08 | 0.0028939 | 0.0028939 | 0.0028939 | 0.98794 | -0.084938 | 0.98793 | -0.085012 | 1.0718
83 | 0.0014712 | 0.00036745 | -0.0014711 | -0.00036758 | 3.3874e-08 | -1.2859e-07 | 0.0022154 | 0.0022155 | 0.0022155 | 0.98793 | -0.085012 | 0.98791 | -0.085179 | 0.82055
84 | 0.0011956 | 0.00029852 | -0.0011956 | -0.00029874 | 3.6695e-08 | -2.1814e-07 | 0.0018005 | 0.0018005 | 0.0018005 | 0.98791 | -0.085179 | 0.98787 | -0.085403 | 0.66687
85 | 0.0011097 | 0.00027722 | -0.0011097 | -0.00027753 | 4.4246e-08 | -3.0798e-07 | 0.0016712 | 0.0016714 | 0.0016714 | 0.98787 | -0.085403 | 0.98783 | -0.085692 | 0.61902
86 | 0.00038569 | 9.6082e-05 | -0.00038569 | -9.6169e-05 | 1.4351e-09 | -8.6729e-08 | 0.00058078 | 0.00058081 | 0.00058081 | 0.98783 | -0.085692 | 0.98783 | -0.085719 | 0.21511
87 | 0.00038569 | 9.6169e-05 | -0.00038568 | -9.6661e-05 | 8.1425e-09 | -4.9191e-07 | 0.00058081 | 0.00058098 | 0.00058098 | 0.98783 | -0.085719 | 0.98781 | -0.085873 | 0.21518
88 | 0.012697 | 0.0031796 | -0.012687 | -0.0031765 | 9.6223e-06 | 3.1358e-06 | 0.018903 | 0.018903 | 0.018903 | 0.99942 | -0.004091 | 0.99864 | -0.0095772 | 7.0012
89 | 0.0093381 | 0.0023371 | -0.0093357 | -0.0023364 | 2.4436e-06 | 6.7524e-07 | 0.013913 | 0.013913 | 0.013913 | 0.99864 | -0.0095772 | 0.99837 | -0.011473 | 5.153
90 | 0.0041705 | 0.001042 | -0.00417 | -0.0010421 | 4.8811e-07 | -7.6861e-08 | 0.006216 | 0.0062161 | 0.0062161 | 0.99818 | -0.012811 | 0.99806 | -0.013662 | 2.3023
91 | -0.006445 | -0.0016121 | 0.0064462 | 0.0016122 | 1.1892e-06 | 1.8739e-07 | 0.0096066 | 0.0096065 | 0.0096066 | 0.99818 | -0.012811 | 0.99837 | -0.011473 | 3.558
92 | 0.0039478 | 0.0009864 | -0.0039467 | -0.00098665 | 1.1249e-06 | -2.4742e-07 | 0.0058847 | 0.005885 | 0.005885 | 0.99806 | -0.013662 | 0.99777 | -0.015731 | 2.1796
93 | 0.0037576 | 0.00093926 | -0.0037575 | -0.00093929 | 1.0364e-07 | -2.9237e-08 | 0.0056029 | 0.005603 | 0.005603 | 0.99777 | -0.015731 | 0.99774 | -0.015932 | 2.0752
94 | 0.003532 | 0.00088278 | -0.0035317 | -0.00088288 | 2.7967e-07 | -1.0344e-07 | 0.0052667 | 0.0052668 | 0.0052668 | 0.99774 | -0.015932 | 0.99766 | -0.016507 | 1.9507
95 | 0.0033456 | 0.00083624 | -0.0033455 | -0.00083629 | 1.1087e-07 | -5.0559e-08 | 0.0049892 | 0.0049892 | 0.0049892 | 0.99766 | -0.016507 | 0.99762 | -0.016747 | 1.8479
96 | 0.0031407 | 0.00078497 | -0.0031406 | -0.00078507 | 1.6993e-07 | -9.6711e-08 | 0.0046838 | 0.0046839 | 0.0046839 | 0.99762 | -0.016747 | 0.99757 | -0.01714 | 1.7348
97 | 0.0027476 | 0.0006866 | -0.0027475 | -0.00068664 | 5.0436e-08 | -4.3443e-08 | 0.0040977 | 0.0040977 | 0.0040977 | 0.99756 | -0.017213 | 0.99754 | -0.017347 | 1.5177
98 | -0.0029251 | -0.00073111 | 0.0029252 | 0.00073109 | 2.9453e-08 | -2.1049e-08 | 0.0043626 | 0.0043626 | 0.0043626 | 0.99756 | -0.017213 | 0.99757 | -0.01714 | 1.6158
99 | 0.0025321 | 0.00063266 | -0.0025321 | -0.00063269 | 2.1527e-08 | -2.3299e-08 | 0.0037764 | 0.0037765 | 0.0037765 | 0.99754 | -0.017347 | 0.99753 | -0.017409 | 1.3987
100 | 0.002304 | 0.00057551 | -0.0023037 | -0.00057583 | 2.2771e-07 | -3.1583e-07 | 0.0034362 | 0.0034363 | 0.0034363 | 0.99753 | -0.017409 | 0.99743 | -0.018127 | 1.2727
101 | 0.0020385 | 0.00050935 | -0.0020384 | -0.00050954 | 1.0006e-07 | -1.8788e-07 | 0.0030406 | 0.0030407 | 0.0030407 | 0.99743 | -0.018127 | 0.99738 | -0.018483 | 1.1262
102 | 0.0017361 | 0.00043379 | -0.0017361 | -0.00043387 | 2.8716e-08 | -7.85e-08 | 0.0025897 | 0.0025898 | 0.0025898 | 0.99738 | -0.018483 | 0.99736 | -0.018603 | 0.95917

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14195 | 0.035472

## res_load
| p_mw | q_mvar
0 | 0.0015104 | 0.00037853
1 | 0.0025236 | 0.00063246
2 | 0.00048142 | 0.00012065
3 | 0.0051193 | 0.001283
4 | 0.050221 | 0.012587
5 | 0.00026813 | 6.7199e-05
6 | 0.00080623 | 0.00020206
7 | 0.00048926 | 0.00012262
8 | 0.0063431 | 0.0015897
9 | 0.00075267 | 0.00018864
10 | 0.001696 | 0.00042505
11 | 0.0011069 | 0.00027741
12 | 0.0014787 | 0.00037061
13 | 6.8521e-05 | 1.7173e-05
14 | 0.0003616 | 9.0626e-05
15 | 6.9344e-05 | 1.7379e-05
16 | 0.0011972 | 0.00030005
17 | 0.001179 | 0.00029548
18 | 0.00086008 | 0.00021556
19 | 0.0017813 | 0.00044645
20 | 0.00033823 | 8.4768e-05
21 | 0.0011383 | 0.00028529
22 | 0.0021705 | 0.00054398
23 | 0.0027383 | 0.00068628
24 | 0.0018112 | 0.00045393
25 | 0.00062639 | 0.00015699
26 | 0.00058861 | 0.00014752
27 | 0.0006487 | 0.00016258
28 | 0.00061709 | 0.00015466
29 | 0.0013068 | 0.00032751
30 | 0.0010002 | 0.00025067
31 | 0.0004204 | 0.00010536
32 | 0.00097293 | 0.00024384
33 | 0.00032856 | 8.2346e-05
34 | 0.00064788 | 0.00016237
35 | 0.00058891 | 0.0001476
36 | 0.00048721 | 0.00012211
37 | 0.0027256 | 0.00068309
38 | 0.00041288 | 0.00010348
39 | 0.00042778 | 0.00010721
40 | 0.0025925 | 0.00064973
41 | 0.0031881 | 0.00079902
42 | 0.00025513 | 6.3941e-05
43 | 0.00032338 | 8.1048e-05
44 | 0.00020834 | 5.2215e-05
45 | 0.00019704 | 4.9383e-05
46 | 0.00026417 | 6.6206e-05
47 | 0.00045915 | 0.00011507
48 | 0.00050363 | 0.00012622
49 | 0.00054606 | 0.00013686
50 | 0.00039178 | 9.8189e-05
51 | 0.0010022 | 0.00025116
52 | 0.00057163 | 0.00014326
53 | 0.0012945 | 0.00032443
54 | 0.00042739 | 0.00010711
55 | 0.00038999 | 9.774e-05
56 | 0.00016487 | 4.1319e-05
57 | 0.00015475 | 3.8783e-05
58 | 0.0001446 | 3.6241e-05
59 | 0.00012165 | 3.0488e-05
60 | 0.00045046 | 0.0001129
61 | 0.00084205 | 0.00021104
62 | 0.00027553 | 6.9055e-05
63 | 8.584e-05 | 2.1514e-05
64 | 0.000724 | 0.00018145
65 | 0.00038568 | 9.6661e-05
66 | 0.01179 | 0.0029549
67 | 0.003349 | 0.00083935
68 | 0.00018287 | 4.5832e-05
69 | 0.0022744 | 0.00057003
70 | 0.00022224 | 5.5699e-05
71 | 0.0028895 | 0.00072419
72 | 0.00018911 | 4.7394e-05
73 | 0.00022547 | 5.6509e-05
74 | 0.00018611 | 4.6642e-05
75 | 0.00020475 | 5.1314e-05
76 | 0.00017759 | 4.4509e-05
77 | 0.00021539 | 5.3981e-05
78 | 0.00021539 | 5.3981e-05
79 | 0.00022813 | 5.7174e-05
80 | 0.00026526 | 6.648e-05
81 | 0.00030224 | 7.5748e-05
82 | 0.00029445 | 7.3795e-05
83 | 0.0023069 | 0.00057816

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1