## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1004-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1004-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1004-9_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1004-9_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1004-9_0_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1004-9_0_3_node_70 | 0.4 | n |  | TRUE
6 | bus_LV_1004-9_0_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1004-9_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1004-9_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1004-9_0_3_node_69 | 0.4 | n |  | TRUE
10 | bus_LV_1004-9_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1004-9_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1004-9_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1004-9_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1004-9_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1004-9_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1004-9_0_3_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_1004-9_0_3_node_87 | 0.4 | n |  | TRUE
18 | bus_LV_1004-9_0_3_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1004-9_0_3_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1004-9_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1004-9_0_3_node_51 | 0.4 | n |  | TRUE
22 | bus_LV_1004-9_0_3_node_78 | 0.4 | n |  | TRUE
23 | bus_LV_1004-9_0_3_node_52 | 0.4 | n |  | TRUE
24 | bus_LV_1004-9_0_3_node_79 | 0.4 | n |  | TRUE
25 | bus_LV_1004-9_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1004-9_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1004-9_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1004-9_0_3_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_1004-9_0_3_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_1004-9_0_3_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_1004-9_0_3_node_50 | 0.4 | n |  | TRUE
32 | bus_LV_1004-9_0_3_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_1004-9_0_3_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_1004-9_0_3_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1004-9_0_3_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_1004-9_0_3_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_1004-9_0_3_node_64 | 0.4 | n |  | TRUE
38 | bus_LV_1004-9_0_3_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_1004-9_0_3_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_1004-9_0_3_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_1004-9_0_3_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1004-9_0_3_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_1004-9_0_3_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_1004-9_0_3_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_1004-9_0_3_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1004-9_0_3_node_57 | 0.4 | n |  | TRUE
47 | bus_LV_1004-9_0_3_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1004-9_0_3_node_56 | 0.4 | n |  | TRUE
49 | bus_LV_1004-9_0_3_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_1004-9_0_3_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_1004-9_0_3_node_28 | 0.4 | n |  | TRUE
52 | bus_LV_1004-9_0_3_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1004-9_0_3_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_1004-9_0_3_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_1004-9_0_3_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_1004-9_0_3_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_1004-9_0_3_node_31 | 0.4 | n |  | TRUE
58 | bus_LV_1004-9_0_3_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_1004-9_0_3_node_32 | 0.4 | n |  | TRUE
60 | bus_LV_1004-9_0_3_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_1004-9_0_3_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_1004-9_0_3_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_1004-9_0_3_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_1004-9_0_3_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_1004-9_0_3_node_39 | 0.4 | n |  | TRUE
66 | bus_LV_1004-9_0_3_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_1004-9_0_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_1004-9_0_3_node_66 | 0.4 | n |  | TRUE
69 | bus_LV_1004-9_0_3_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_1004-9_0_3_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_1004-9_0_3_node_84 | 0.4 | n |  | TRUE
72 | bus_LV_1004-9_0_3_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_1004-9_0_3_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_1004-9_0_3_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_1004-9_0_3_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_1004-9_0_3_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1004-9_0_3_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_1004-9_0_3_node_63 | 0.4 | n |  | TRUE
79 | bus_LV_1004-9_0_3_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_1004-9_0_3_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_1004-9_0_3_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1004-9_0_3_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_1004-9_0_3_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_1004-9_0_3_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_1004-9_0_3_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_1004-9_0_3_node_85 | 0.4 | n |  | TRUE
87 | bus_MV_82_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1004-9_0_3_load_0 | 0 | 0.003263 | 0.00081778 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1004-9_0_3_load_3 | 2 | 0.0043582 | 0.0010923 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1004-9_0_3_load_11 | 4 | 0.0021101 | 0.00052885 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1004-9_0_3_load_70 | 5 | 0.0021332 | 0.00053462 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1004-9_0_3_load_13 | 6 | 0.0029256 | 0.00073324 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1004-9_0_3_load_12 | 8 | 0.0014536 | 0.0003643 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1004-9_0_3_load_5 | 10 | 0.00578 | 0.0014486 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1004-9_0_3_load_6 | 11 | 0.052904 | 0.013259 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1004-9_0_3_load_7 | 12 | 0.0024625 | 0.00061717 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1004-9_0_3_load_9 | 13 | 0.015974 | 0.0040034 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1004-9_0_3_load_8 | 14 | 0.0015146 | 0.0003796 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1004-9_0_3_load_86 | 16 | 0.0012824 | 0.00032139 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1004-9_0_3_load_87 | 17 | 0.0085065 | 0.0021319 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1004-9_0_3_load_18 | 19 | 0.001937 | 0.00048546 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1004-9_0_3_load_19 | 20 | 0.0013468 | 0.00033753 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1004-9_0_3_load_51 | 21 | 0.0019237 | 0.00048212 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1004-9_0_3_load_78 | 22 | 0.0025034 | 0.00062741 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1004-9_0_3_load_79 | 24 | 0.0016609 | 0.00041627 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1004-9_0_3_load_26 | 25 | 0.0014696 | 0.00036832 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1004-9_0_3_load_14 | 26 | 0.0076649 | 0.001921 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1004-9_0_3_load_15 | 27 | 0.0039374 | 0.00098681 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1004-9_0_3_load_44 | 29 | 0.0016295 | 0.0004084 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1004-9_0_3_load_45 | 30 | 0.0010821 | 0.00027119 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1004-9_0_3_load_49 | 32 | 0.00094886 | 0.00023781 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1004-9_0_3_load_80 | 35 | 0.00085244 | 0.00021364 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1004-9_0_3_load_41 | 36 | 0.0010418 | 0.00026111 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1004-9_0_3_load_64 | 37 | 0.0020141 | 0.00050478 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1004-9_0_3_load_65 | 38 | 0.0012004 | 0.00030084 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1004-9_0_3_load_62 | 39 | 0.0015038 | 0.00037688 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1004-9_0_3_load_20 | 40 | 0.001354 | 0.00033935 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1004-9_0_3_load_21 | 41 | 0.00136 | 0.00034086 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1004-9_0_3_load_59 | 43 | 0.0011013 | 0.00027602 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1004-9_0_3_load_23 | 44 | 0.002048 | 0.00051328 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1004-9_0_3_load_24 | 45 | 0.002018 | 0.00050575 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1004-9_0_3_load_57 | 46 | 0.001336 | 0.00033483 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1004-9_0_3_load_27 | 47 | 0.0013811 | 0.00034614 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1004-9_0_3_load_56 | 48 | 0.0016024 | 0.00040161 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1004-9_0_3_load_58 | 49 | 0.0021375 | 0.0005357 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1004-9_0_3_load_46 | 50 | 0.0023607 | 0.00059166 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1004-9_0_3_load_28 | 51 | 0.0017961 | 0.00045015 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1004-9_0_3_load_47 | 52 | 0.0022723 | 0.0005695 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1004-9_0_3_load_55 | 54 | 0.0016924 | 0.00042415 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1004-9_0_3_load_33 | 55 | 0.0018969 | 0.00047542 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1004-9_0_3_load_29 | 56 | 0.0011038 | 0.00027664 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1004-9_0_3_load_31 | 57 | 0.001295 | 0.00032455 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1004-9_0_3_load_30 | 58 | 0.0014182 | 0.00035543 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1004-9_0_3_load_32 | 59 | 0.00098568 | 0.00024704 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1004-9_0_3_load_34 | 60 | 0.00077881 | 0.00019519 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1004-9_0_3_load_35 | 61 | 0.00093681 | 0.00023479 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1004-9_0_3_load_38 | 64 | 0.0011375 | 0.00028508 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1004-9_0_3_load_39 | 65 | 0.0010582 | 0.00026522 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1004-9_0_3_load_67 | 66 | 0.0046291 | 0.0011602 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1004-9_0_3_load_68 | 67 | 0.0029233 | 0.00073265 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1004-9_0_3_load_66 | 68 | 0.0010081 | 0.00025266 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1004-9_0_3_load_53 | 69 | 0.001008 | 0.00025263 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1004-9_0_3_load_40 | 70 | 0.0011545 | 0.00028934 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1004-9_0_3_load_84 | 71 | 0.0011103 | 0.00027827 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1004-9_0_3_load_48 | 72 | 0.0022321 | 0.00055942 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1004-9_0_3_load_60 | 73 | 0.0024305 | 0.00060915 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1004-9_0_3_load_71 | 74 | 0.0020013 | 0.00050157 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1004-9_0_3_load_72 | 75 | 0.0020628 | 0.00051699 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1004-9_0_3_load_73 | 76 | 0.002169 | 0.0005436 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1004-9_0_3_load_61 | 77 | 0.0023412 | 0.00058676 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1004-9_0_3_load_63 | 78 | 0.0012754 | 0.00031965 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1004-9_0_3_load_75 | 79 | 0.0020706 | 0.00051893 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1004-9_0_3_load_74 | 80 | 0.0014191 | 0.00035565 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1004-9_0_3_load_77 | 81 | 0.002289 | 0.00057368 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1004-9_0_3_load_76 | 82 | 0.0016869 | 0.00042278 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1004-9_0_3_load_82 | 83 | 0.00088625 | 0.00022212 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1004-9_0_3_load_81 | 84 | 0.00064488 | 0.00016162 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1004-9_0_3_load_83 | 85 | 0.0016401 | 0.00041104 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1004-9_0_3_load_85 | 86 | 0.0014645 | 0.00036703 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1004-9_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0097922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1004-9_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.021634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1004-9_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.00597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1004-9_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0062648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1004-9_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.027838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1004-9_0_3_line_5 | NAYY 4x150 SE | 4 | 8 | 0.0089928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1004-9_0_3_line_6 | NAYY 4x150 SE | 5 | 9 | 0.0058289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1004-9_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.014085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1004-9_0_3_line_8 | NAYY 4x150 SE | 7 | 13 | 0.0047376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1004-9_0_3_line_9 | NAYY 4x150 SE | 9 | 67 | 0.02749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1004-9_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.045618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1004-9_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.022335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1004-9_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.055818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1004-9_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.029955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1004-9_0_3_line_14 | NAYY 4x150 SE | 12 | 15 | 0.050472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1004-9_0_3_line_15 | NAYY 4x150 SE | 14 | 18 | 0.025764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1004-9_0_3_line_16 | NAYY 4x150 SE | 15 | 19 | 0.0091882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1004-9_0_3_line_17 | NAYY 4x150 SE | 15 | 20 | 0.028817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1004-9_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.011814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1004-9_0_3_line_19 | NAYY 4x150 SE | 17 | 49 | 0.11675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1004-9_0_3_line_20 | NAYY 4x150 SE | 18 | 25 | 0.0038846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1004-9_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.024899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1004-9_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.0025551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1004-9_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.017377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1004-9_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.028052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1004-9_0_3_line_25 | NAYY 4x150 SE | 23 | 69 | 0.032252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1004-9_0_3_line_26 | NAYY 4x150 SE | 25 | 53 | 0.024582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1004-9_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.029318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1004-9_0_3_line_28 | NAYY 4x150 SE | 27 | 33 | 0.015706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1004-9_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.034777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1004-9_0_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.0080307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1004-9_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.030886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1004-9_0_3_line_32 | NAYY 4x150 SE | 30 | 34 | 0.028908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1004-9_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.016817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1004-9_0_3_line_34 | NAYY 4x150 SE | 32 | 63 | 0.03011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1004-9_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.008923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1004-9_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.051513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1004-9_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.028297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1004-9_0_3_line_38 | NAYY 4x150 SE | 36 | 70 | 0.010001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1004-9_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.015624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1004-9_0_3_line_40 | NAYY 4x150 SE | 37 | 39 | 0.0055661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1004-9_0_3_line_41 | NAYY 4x150 SE | 38 | 71 | 0.018852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1004-9_0_3_line_42 | NAYY 4x150 SE | 39 | 78 | 0.0012945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1004-9_0_3_line_43 | NAYY 4x150 SE | 40 | 41 | 0.030325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1004-9_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.016791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1004-9_0_3_line_45 | NAYY 4x150 SE | 40 | 43 | 0.028748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1004-9_0_3_line_46 | NAYY 4x150 SE | 41 | 44 | 0.0088879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1004-9_0_3_line_47 | NAYY 4x150 SE | 42 | 45 | 0.01943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1004-9_0_3_line_48 | NAYY 4x150 SE | 43 | 46 | 0.026249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1004-9_0_3_line_49 | NAYY 4x150 SE | 44 | 47 | 0.026892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1004-9_0_3_line_50 | NAYY 4x150 SE | 45 | 50 | 0.00094216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1004-9_0_3_line_51 | NAYY 4x150 SE | 46 | 48 | 0.0076046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1004-9_0_3_line_52 | NAYY 4x150 SE | 47 | 51 | 0.00073261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1004-9_0_3_line_53 | NAYY 4x150 SE | 48 | 49 | 0.0064392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1004-9_0_3_line_54 | NAYY 4x150 SE | 50 | 52 | 0.024093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1004-9_0_3_line_55 | NAYY 4x150 SE | 51 | 56 | 0.0072987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1004-9_0_3_line_56 | NAYY 4x150 SE | 52 | 72 | 0.001579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1004-9_0_3_line_57 | NAYY 4x150 SE | 53 | 54 | 0.020097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1004-9_0_3_line_58 | NAYY 4x150 SE | 53 | 55 | 0.0079752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1004-9_0_3_line_59 | NAYY 4x150 SE | 54 | 78 | 0.021456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1004-9_0_3_line_60 | NAYY 4x150 SE | 55 | 59 | 0.029941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1004-9_0_3_line_61 | NAYY 4x150 SE | 56 | 57 | 0.0049066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1004-9_0_3_line_62 | NAYY 4x150 SE | 57 | 58 | 0.03308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1004-9_0_3_line_63 | NAYY 4x150 SE | 58 | 59 | 0.014054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1004-9_0_3_line_64 | NAYY 4x150 SE | 60 | 61 | 0.046323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1004-9_0_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.020921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1004-9_0_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.029652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1004-9_0_3_line_67 | NAYY 4x150 SE | 62 | 64 | 0.021464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1004-9_0_3_line_68 | NAYY 4x150 SE | 62 | 65 | 0.0090727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1004-9_0_3_line_69 | NAYY 4x150 SE | 64 | 66 | 0.055134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1004-9_0_3_line_70 | NAYY 4x150 SE | 65 | 69 | 0.0063284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1004-9_0_3_line_71 | NAYY 4x150 SE | 66 | 67 | 0.032689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1004-9_0_3_line_72 | NAYY 4x150 SE | 66 | 68 | 0.0056835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1004-9_0_3_line_73 | NAYY 4x150 SE | 71 | 83 | 0.0044971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1004-9_0_3_line_74 | NAYY 4x150 SE | 72 | 73 | 0.018573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1004-9_0_3_line_75 | NAYY 4x150 SE | 73 | 77 | 0.01087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1004-9_0_3_line_76 | NAYY 4x150 SE | 74 | 75 | 0.021289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1004-9_0_3_line_77 | NAYY 4x150 SE | 74 | 76 | 3.4587e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1004-9_0_3_line_78 | NAYY 4x150 SE | 75 | 80 | 0.002465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1004-9_0_3_line_79 | NAYY 4x150 SE | 77 | 79 | 0.032133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1004-9_0_3_line_80 | NAYY 4x150 SE | 79 | 81 | 0.020019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1004-9_0_3_line_81 | NAYY 4x150 SE | 79 | 80 | 0.022275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1004-9_0_3_line_82 | NAYY 4x150 SE | 81 | 82 | 0.0034501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1004-9_0_3_line_83 | NAYY 4x150 SE | 83 | 84 | 0.0053059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1004-9_0_3_line_84 | NAYY 4x150 SE | 84 | 85 | 0.023934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1004-9_0_3_line_85 | NAYY 4x150 SE | 85 | 86 | 0.01178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1004-9_0_3_trafo_7 | 0.25 MVA 20/0.4 kV | 87 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2645468.3721 | 1185792.4899 | 2645463.4265 | 1185797.5886 | 2645461.4515 | 1185799.4136
1 | 2645468.3721 | 1185792.4899 | 2645477.0191 | 1185800.4043 | 2645481.2859 | 1185804.3054 | 2645484.2662 | 1185807.1655
2 | 2645472.4118 | 1185788.0849 | 2645468.3721 | 1185792.4899
3 | 2645484.2662 | 1185807.1655 | 2645488.4906 | 1185811.2194 | 2645488.7435 | 1185811.542
4 | 2645472.4118 | 1185788.0849 | 2645483.3671 | 1185774.4161 | 2645489.3708 | 1185766.0214
5 | 2645488.7435 | 1185811.542 | 2645490.5161 | 1185813.8029 | 2645491.696 | 1185816.202 | 2645492.1176 | 1185817.9617 | 2645492.0136 | 1185819.5952
6 | 2645492.7616 | 1185761.2802 | 2645489.3708 | 1185766.0214
7 | 2645428.7516 | 1185738.0599 | 2645417.144 | 1185746.0386
8 | 2645428.7516 | 1185738.0599 | 2645431.8265 | 1185734.4558
9 | 2645492.7616 | 1185761.2802 | 2645514.2809 | 1185778.3867
10 | 2645489.0889 | 1185651.9206 | 2645482.8889 | 1185656.4481 | 2645477.0083 | 1185662.0622 | 2645462.715 | 1185679.1408 | 2645458.8561 | 1185685.6184
11 | 2645489.0889 | 1185651.9206 | 2645499.7944 | 1185644.103 | 2645507.4361 | 1185639.2005
12 | 2645458.8561 | 1185685.6184 | 2645431.8265 | 1185734.4558
13 | 2645507.4361 | 1185639.2005 | 2645513.8205 | 1185635.1046 | 2645517.5596 | 1185631.1197 | 2645524.5937 | 1185620.3339 | 2645526.585 | 1185616.8322
14 | 2645507.4361 | 1185639.2005 | 2645550.4945 | 1185665.533
15 | 2645534.9916 | 1185592.6978 | 2645532.3489 | 1185605.0511 | 2645529.0567 | 1185612.4857 | 2645526.585 | 1185616.8322
16 | 2645550.4945 | 1185665.533 | 2645545.7018 | 1185673.3722
17 | 2645550.4945 | 1185665.533 | 2645575.2063 | 1185680.3567
18 | 2645347.1859 | 1185624.5362 | 2645336.6899 | 1185629.9598
19 | 2645432.2863 | 1185544.6147 | 2645347.1859 | 1185624.5362
20 | 2645534.9916 | 1185592.6978 | 2645535.2399 | 1185588.8211
21 | 2645532.7139 | 1185694.6159 | 2645545.7018 | 1185673.3722
22 | 2645575.2063 | 1185680.3567 | 2645577.3975 | 1185681.6711
23 | 2645523.6497 | 1185709.4419 | 2645532.7139 | 1185694.6159
24 | 2645596.8708 | 1185701.5274 | 2645582.4612 | 1185684.7086 | 2645577.3975 | 1185681.6711
25 | 2645523.6497 | 1185709.4419 | 2645552.1397 | 1185724.5595
26 | 2645531.8052 | 1185565.1141 | 2645534.0081 | 1185568.466 | 2645535.3005 | 1185573.1339 | 2645535.8315 | 1185579.5859 | 2645535.2399 | 1185588.8211
27 | 2645578.1169 | 1185627.7468 | 2645579.436 | 1185625.9425 | 2645598.1234 | 1185606.3403
28 | 2645608.9609 | 1185594.9723 | 2645598.1234 | 1185606.3403
29 | 2645616.7289 | 1185639.1778 | 2645617.902 | 1185643.4668 | 2645620.7728 | 1185649.3029 | 2645628.8496 | 1185661.9491 | 2645634.1395 | 1185669.0083
30 | 2645616.7289 | 1185639.1778 | 2645614.6156 | 1185631.4302
31 | 2645653.0531 | 1185693.406 | 2645648.3199 | 1185686.6329 | 2645636.1473 | 1185671.6877 | 2645634.1395 | 1185669.0083
32 | 2645612.9083 | 1185602.7288 | 2645613.3575 | 1185605.8784 | 2645612.6813 | 1185618.5135 | 2645614.1824 | 1185629.8422 | 2645614.6156 | 1185631.4302
33 | 2645653.0531 | 1185693.406 | 2645657.3816 | 1185705.2232 | 2645658.1621 | 1185709.3831
34 | 2645652.8476 | 1185738.4179 | 2645656.6646 | 1185729.2197 | 2645658.3672 | 1185722.0955 | 2645659.061 | 1185714.1742 | 2645658.1621 | 1185709.3831
35 | 2645608.9609 | 1185594.9723 | 2645612.5026 | 1185599.8909 | 2645612.9083 | 1185602.7288
36 | 2645608.9609 | 1185594.9723 | 2645624.1674 | 1185582.3256 | 2645650.1908 | 1185564.1624
37 | 2645612.9083 | 1185602.7288 | 2645620.2969 | 1185602.5516 | 2645627.1953 | 1185604.6052 | 2645640.7643 | 1185606.554 | 2645640.7643 | 1185606.554
38 | 2645646.9789 | 1185613.1059 | 2645646.1322 | 1185609.163 | 2645640.7643 | 1185606.554
39 | 2645578.8031 | 1185528.4283 | 2645574.6694 | 1185531.2213 | 2645565.3978 | 1185536.4306
40 | 2645560.5451 | 1185539.1571 | 2645565.3978 | 1185536.4306
41 | 2645589.9712 | 1185513.5801 | 2645586.2028 | 1185520.8922 | 2645580.8521 | 1185527.0438 | 2645578.8031 | 1185528.4283
42 | 2645560.5451 | 1185539.1571 | 2645559.4165 | 1185539.7912
43 | 2645478.9365 | 1185545.6474 | 2645479.5913 | 1185537.903 | 2645480.8508 | 1185532.8431 | 2645483.0032 | 1185528.7795 | 2645492.466 | 1185520.2487
44 | 2645503.516 | 1185507.757 | 2645501.0671 | 1185511.6739 | 2645498.1792 | 1185515.0983 | 2645492.466 | 1185520.2487
45 | 2645492.466 | 1185520.2487 | 2645463.729 | 1185519.4445
46 | 2645478.9365 | 1185545.6474 | 2645478.1876 | 1185554.5037
47 | 2645503.516 | 1185507.757 | 2645509.3845 | 1185506.7677 | 2645520.8606 | 1185499.6976
48 | 2645463.729 | 1185519.4445 | 2645453.3497 | 1185528.4544 | 2645443.4286 | 1185536.0661
49 | 2645478.1876 | 1185554.5037 | 2645477.4954 | 1185562.6895 | 2645475.2724 | 1185569.0205 | 2645472.5228 | 1185574.347 | 2645469.4161 | 1185579.4484
50 | 2645521.6628 | 1185499.2034 | 2645520.8606 | 1185499.6976
51 | 2645437.3951 | 1185540.6951 | 2645443.4286 | 1185536.0661
52 | 2645469.035 | 1185580.0741 | 2645469.4161 | 1185579.4484
53 | 2645432.2863 | 1185544.6147 | 2645437.3951 | 1185540.6951
54 | 2645521.6628 | 1185499.2034 | 2645531.7734 | 1185492.9746 | 2645541.6453 | 1185485.7761
55 | 2645466.2779 | 1185586.7286 | 2645466.2779 | 1185586.7286 | 2645467.0438 | 1185583.3437 | 2645469.035 | 1185580.0741
56 | 2645542.9211 | 1185484.8458 | 2645541.6453 | 1185485.7761
57 | 2645531.8052 | 1185565.1141 | 2645532.3507 | 1185556.6025 | 2645534.4472 | 1185552.8719 | 2645538.2435 | 1185548.3983 | 2645539.5651 | 1185547.874
58 | 2645531.8052 | 1185565.1141 | 2645529.6376 | 1185564.1527 | 2645526.6691 | 1185564.1301 | 2645524.6341 | 1185565.8045
59 | 2645539.5651 | 1185547.874 | 2645546.6022 | 1185545.0822 | 2645557.2946 | 1185540.9835 | 2645559.4165 | 1185539.7912
60 | 2645524.6341 | 1185565.8045 | 2645522.6721 | 1185572.9268 | 2645518.7545 | 1185579.3005 | 2645513.145 | 1185584.3829 | 2645506.9827 | 1185588.6617
61 | 2645467.0079 | 1185591.5307 | 2645466.6214 | 1185590.7445 | 2645466.2779 | 1185586.7286
62 | 2645495.4383 | 1185596.6775 | 2645489.7396 | 1185599.4357 | 2645484.9015 | 1185600.4107 | 2645479.4912 | 1185600.3696 | 2645474.1415 | 1185599.3729 | 2645471.549 | 1185598.0859 | 2645468.8159 | 1185595.208 | 2645467.0079 | 1185591.5307
63 | 2645495.4383 | 1185596.6775 | 2645495.4383 | 1185596.6775 | 2645506.9827 | 1185588.6617
64 | 2645584.1162 | 1185741.3963 | 2645594.6083 | 1185747.1461 | 2645597.318 | 1185748.0672 | 2645599.4987 | 1185748.3062 | 2645601.6176 | 1185747.6441 | 2645604.1138 | 1185746.5403 | 2645619.7178 | 1185738.7548 | 2645626.0616 | 1185736.002
65 | 2645565.395 | 1185732.227 | 2645569.963 | 1185733.6403 | 2645584.1162 | 1185741.3963
66 | 2645652.8476 | 1185738.4179 | 2645644.1321 | 1185732.4816 | 2645641.1941 | 1185731.4809 | 2645638.1805 | 1185731.3802 | 2645632.8105 | 1185733.0735 | 2645626.0616 | 1185736.002
67 | 2645569.6985 | 1185752.3596 | 2645567.3804 | 1185750.1185 | 2645566.3864 | 1185748.3656 | 2645566.1126 | 1185735.2008 | 2645565.395 | 1185732.227
68 | 2645565.395 | 1185732.227 | 2645564.2901 | 1185731.0068 | 2645557.7298 | 1185727.5258
69 | 2645539.8695 | 1185798.728 | 2645569.6985 | 1185752.3596
70 | 2645552.1397 | 1185724.5595 | 2645557.7298 | 1185727.5258
71 | 2645514.2809 | 1185778.3867 | 2645539.8695 | 1185798.728
72 | 2645544.3185 | 1185802.2647 | 2645539.8695 | 1185798.728
73 | 2645589.9712 | 1185513.5801 | 2645590.0835 | 1185513.3621 | 2645592.1036 | 1185509.6207
74 | 2645542.9211 | 1185484.8458 | 2645543.8293 | 1185484.1836 | 2645556.9666 | 1185472.6993
75 | 2645563.8842 | 1185464.315 | 2645556.9666 | 1185472.6993 | 2645556.9666 | 1185472.6993
76 | 2645506.853 | 1185454.6824 | 2645526.3387 | 1185446.1078
77 | 2645506.8214 | 1185454.6964 | 2645506.853 | 1185454.6824
78 | 2645526.3387 | 1185446.1078 | 2645528.5949 | 1185445.115
79 | 2645563.8842 | 1185464.315 | 2645548.8746 | 1185435.9034
80 | 2645567.0509 | 1185427.515 | 2645561.4267 | 1185430.11 | 2645548.8746 | 1185435.9034
81 | 2645528.5949 | 1185445.115 | 2645535.5027 | 1185442.0752 | 2645548.8746 | 1185435.9034
82 | 2645567.0509 | 1185427.515 | 2645570.1836 | 1185426.0696
83 | 2645594.6244 | 1185504.9519 | 2645592.1036 | 1185509.6207
84 | 2645594.6244 | 1185504.9519 | 2645600.9513 | 1185493.2338 | 2645605.7899 | 1185485.1884 | 2645606.6929 | 1185484.3553
85 | 2645615.3507 | 1185476.3674 | 2645606.6929 | 1185484.3553

## bus_geodata
| x | y | coords
0 | 2645461.4515 | 1185799.4136
1 | 2645468.3721 | 1185792.4899
2 | 2645484.2662 | 1185807.1655
3 | 2645472.4118 | 1185788.0849
4 | 2645488.7435 | 1185811.542
5 | 2645489.3708 | 1185766.0214
6 | 2645417.144 | 1185746.0386
7 | 2645428.7516 | 1185738.0599
8 | 2645492.0136 | 1185819.5952
9 | 2645492.7616 | 1185761.2802
10 | 2645489.0889 | 1185651.9206
11 | 2645458.8561 | 1185685.6184
12 | 2645507.4361 | 1185639.2005
13 | 2645431.8265 | 1185734.4558
14 | 2645526.585 | 1185616.8322
15 | 2645550.4945 | 1185665.533
16 | 2645336.6899 | 1185629.9598
17 | 2645347.1859 | 1185624.5362
18 | 2645534.9916 | 1185592.6978
19 | 2645545.7018 | 1185673.3722
20 | 2645575.2063 | 1185680.3567
21 | 2645532.7139 | 1185694.6159
22 | 2645577.3975 | 1185681.6711
23 | 2645523.6497 | 1185709.4419
24 | 2645596.8708 | 1185701.5274
25 | 2645535.2399 | 1185588.8211
26 | 2645578.1169 | 1185627.7468
27 | 2645598.1234 | 1185606.3403
28 | 2645616.7289 | 1185639.1778
29 | 2645634.1395 | 1185669.0083
30 | 2645614.6156 | 1185631.4302
31 | 2645653.0531 | 1185693.406
32 | 2645658.1621 | 1185709.3831
33 | 2645608.9609 | 1185594.9723
34 | 2645612.9083 | 1185602.7288
35 | 2645650.1908 | 1185564.1625
36 | 2645640.7643 | 1185606.554
37 | 2645565.3978 | 1185536.4306
38 | 2645578.8031 | 1185528.4283
39 | 2645560.5451 | 1185539.1571
40 | 2645492.466 | 1185520.2487
41 | 2645478.9365 | 1185545.6474
42 | 2645503.516 | 1185507.757
43 | 2645463.729 | 1185519.4445
44 | 2645478.1876 | 1185554.5037
45 | 2645520.8606 | 1185499.6976
46 | 2645443.4286 | 1185536.0661
47 | 2645469.4161 | 1185579.4484
48 | 2645437.3951 | 1185540.6951
49 | 2645432.2863 | 1185544.6147
50 | 2645521.6628 | 1185499.2034
51 | 2645469.035 | 1185580.0741
52 | 2645541.6453 | 1185485.7761
53 | 2645531.8052 | 1185565.1141
54 | 2645539.5651 | 1185547.874
55 | 2645524.6341 | 1185565.8045
56 | 2645466.2779 | 1185586.7286
57 | 2645467.0079 | 1185591.5307
58 | 2645495.4383 | 1185596.6775
59 | 2645506.9827 | 1185588.6617
60 | 2645584.1161 | 1185741.3963
61 | 2645626.0616 | 1185736.002
62 | 2645565.395 | 1185732.227
63 | 2645652.8476 | 1185738.4179
64 | 2645569.6985 | 1185752.3596
65 | 2645557.7298 | 1185727.5258
66 | 2645539.8695 | 1185798.728
67 | 2645514.2809 | 1185778.3867
68 | 2645544.3185 | 1185802.2647
69 | 2645552.1397 | 1185724.5595
70 | 2645646.9789 | 1185613.1059
71 | 2645589.9712 | 1185513.5801
72 | 2645542.9211 | 1185484.8458
73 | 2645556.9666 | 1185472.6993
74 | 2645506.853 | 1185454.6824
75 | 2645526.3387 | 1185446.1078
76 | 2645506.8214 | 1185454.6964
77 | 2645563.8842 | 1185464.315
78 | 2645559.4165 | 1185539.7912
79 | 2645548.8746 | 1185435.9034
80 | 2645528.5949 | 1185445.1149
81 | 2645567.0509 | 1185427.515
82 | 2645570.1836 | 1185426.0696
83 | 2645592.1036 | 1185509.6207
84 | 2645594.6244 | 1185504.9519
85 | 2645606.6929 | 1185484.3553
86 | 2645615.3507 | 1185476.3674
87 | 2645534.9916 | 1185592.6978

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98501 | -0.10514 | 0.003263 | 0.00081778
1 | 0.98506 | -0.10481 | 0 | 0
2 | 0.98481 | -0.10657 | 0.0043582 | 0.0010923
3 | 0.98515 | -0.10412 | 0 | 0
4 | 0.98478 | -0.1068 | 0.0021101 | 0.00052885
5 | 0.98561 | -0.10092 | 0.0021332 | 0.00053462
6 | 0.99121 | -0.061614 | 0.0029256 | 0.00073324
7 | 0.99127 | -0.061196 | 0 | 0
8 | 0.98476 | -0.10694 | 0.0014536 | 0.0003643
9 | 0.98572 | -0.10012 | 0 | 0
10 | 0.99751 | -0.01734 | 0.00578 | 0.0014486
11 | 0.99281 | -0.050354 | 0.052904 | 0.013259
12 | 1 | 0 | -0.2099 | -0.052742
13 | 0.99129 | -0.061055 | 0.015974 | 0.0040034
14 | 0.99676 | -0.022329 | 0.0015146 | 0.0003796
15 | 0.99603 | -0.027592 | 0 | 0
16 | 0.9756 | -0.17144 | 0.0012824 | 0.00032139
17 | 0.97562 | -0.17128 | 0.0085065 | 0.0021319
18 | 0.99403 | -0.041255 | 0 | 0
19 | 0.99538 | -0.032128 | 0.001937 | 0.00048546
20 | 0.9958 | -0.029191 | 0.0013468 | 0.00033753
21 | 0.99368 | -0.043961 | 0.0019237 | 0.00048212
22 | 0.99579 | -0.029298 | 0.0025034 | 0.00062741
23 | 0.99255 | -0.051905 | 0 | 0
24 | 0.99572 | -0.029768 | 0.0016609 | 0.00041627
25 | 0.99362 | -0.044117 | 0.0014696 | 0.00036832
26 | 0.98244 | -0.12337 | 0.0076649 | 0.001921
27 | 0.98277 | -0.12104 | 0.0039374 | 0.00098681
28 | 0.98399 | -0.11233 | 0 | 0
29 | 0.98479 | -0.10669 | 0.0016295 | 0.0004084
30 | 0.98381 | -0.11364 | 0.0010821 | 0.00027119
31 | 0.98556 | -0.10117 | 0 | 0
32 | 0.98599 | -0.098166 | 0.00094886 | 0.00023781
33 | 0.98303 | -0.11916 | 0 | 0
34 | 0.9832 | -0.11801 | 0 | 0
35 | 0.98297 | -0.11961 | 0.00085244 | 0.00021364
36 | 0.98311 | -0.11865 | 0.0010418 | 0.00026111
37 | 0.99023 | -0.067877 | 0.0020141 | 0.00050478
38 | 0.99007 | -0.068982 | 0.0012004 | 0.00030084
39 | 0.9903 | -0.067369 | 0.0015038 | 0.00037688
40 | 0.97879 | -0.14856 | 0.001354 | 0.00033935
41 | 0.98077 | -0.13446 | 0.00136 | 0.00034086
42 | 0.97812 | -0.15335 | 0 | 0
43 | 0.97812 | -0.15335 | 0.0011013 | 0.00027602
44 | 0.98137 | -0.13022 | 0.002048 | 0.00051328
45 | 0.97734 | -0.1589 | 0.002018 | 0.00050575
46 | 0.97755 | -0.15743 | 0.001336 | 0.00033483
47 | 0.98326 | -0.11683 | 0.0013811 | 0.00034614
48 | 0.9774 | -0.1585 | 0.0016024 | 0.00040161
49 | 0.97729 | -0.15931 | 0.0021375 | 0.0005357
50 | 0.97731 | -0.15915 | 0.0023607 | 0.00059166
51 | 0.98331 | -0.11646 | 0.0017961 | 0.00045015
52 | 0.9765 | -0.16495 | 0.0022723 | 0.0005695
53 | 0.99107 | -0.06192 | 0 | 0
54 | 0.99068 | -0.064666 | 0.0016924 | 0.00042415
55 | 0.9904 | -0.066624 | 0.0018969 | 0.00047542
56 | 0.98385 | -0.1126 | 0.0011038 | 0.00027664
57 | 0.98423 | -0.10995 | 0.001295 | 0.00032455
58 | 0.98682 | -0.091691 | 0.0014182 | 0.00035543
59 | 0.98795 | -0.08376 | 0.00098568 | 0.00024704
60 | 0.98887 | -0.077805 | 0.00077881 | 0.00019519
61 | 0.98757 | -0.086933 | 0.00093681 | 0.00023479
62 | 0.98947 | -0.073524 | 0 | 0
63 | 0.98679 | -0.092502 | 0 | 0
64 | 0.98876 | -0.078568 | 0.0011375 | 0.00028508
65 | 0.99004 | -0.06954 | 0.0010582 | 0.00026522
66 | 0.98702 | -0.090913 | 0.0046291 | 0.0011602
67 | 0.98625 | -0.096361 | 0.0029233 | 0.00073265
68 | 0.98701 | -0.090972 | 0.0010081 | 0.00025266
69 | 0.99044 | -0.066695 | 0.001008 | 0.00025263
70 | 0.98309 | -0.11877 | 0.0011545 | 0.00028934
71 | 0.98991 | -0.070087 | 0.0011103 | 0.00027827
72 | 0.97645 | -0.16529 | 0.0022321 | 0.00055942
73 | 0.97595 | -0.16888 | 0.0024305 | 0.00060915
74 | 0.97465 | -0.17822 | 0.0020013 | 0.00050157
75 | 0.97478 | -0.17728 | 0.0020628 | 0.00051699
76 | 0.97465 | -0.17822 | 0.002169 | 0.0005436
77 | 0.9757 | -0.17071 | 0.0023412 | 0.00058676
78 | 0.99032 | -0.067231 | 0.0012754 | 0.00031965
79 | 0.97505 | -0.17533 | 0.0020706 | 0.00051893
80 | 0.9748 | -0.17712 | 0.0014191 | 0.00035565
81 | 0.97494 | -0.17617 | 0.002289 | 0.00057368
82 | 0.97493 | -0.17623 | 0.0016869 | 0.00042278
83 | 0.98988 | -0.070299 | 0.00088625 | 0.00022212
84 | 0.98986 | -0.070502 | 0.00064488 | 0.00016162
85 | 0.98975 | -0.071259 | 0.0016401 | 0.00041104
86 | 0.98972 | -0.071435 | 0.0014645 | 0.00036703
87 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.003263 | -0.00081778 | 0.0032631 | 0.00081771 | 1.4847e-07 | -6.7549e-08 | 0.0049293 | 0.0049292 | 0.0049293 | 0.98501 | -0.10514 | 0.98506 | -0.10481 | 1.8257
1 | 0.007924 | 0.0019857 | -0.0079221 | -0.0019853 | 1.9342e-06 | 4.6859e-07 | 0.01197 | 0.01197 | 0.01197 | 0.98506 | -0.10481 | 0.98481 | -0.10657 | 4.4333
2 | -0.011187 | -0.0028035 | 0.011188 | 0.0028038 | 1.0639e-06 | 3.3317e-07 | 0.016899 | 0.016899 | 0.016899 | 0.98506 | -0.10481 | 0.98515 | -0.10412 | 6.2589
3 | 0.0035638 | 0.00089301 | -0.0035637 | -0.00089304 | 1.1335e-07 | -3.6112e-08 | 0.0053848 | 0.0053848 | 0.0053848 | 0.98481 | -0.10657 | 0.98478 | -0.1068 | 1.9944
4 | -0.011188 | -0.0028038 | 0.011193 | 0.0028054 | 4.9607e-06 | 1.5533e-06 | 0.016899 | 0.016899 | 0.016899 | 0.98515 | -0.10412 | 0.98561 | -0.10092 | 6.2589
5 | 0.0014536 | 0.0003642 | -0.0014536 | -0.0003643 | 2.7071e-08 | -1.04e-07 | 0.0021964 | 0.0021964 | 0.0021964 | 0.98478 | -0.1068 | 0.98476 | -0.10694 | 0.81349
6 | -0.013326 | -0.00334 | 0.013328 | 0.0033405 | 1.4723e-06 | 4.9198e-07 | 0.020119 | 0.020119 | 0.020119 | 0.98561 | -0.10092 | 0.98572 | -0.10012 | 7.4516
7 | -0.0029256 | -0.00073324 | 0.0029258 | 0.00073312 | 1.6954e-07 | -1.1636e-07 | 0.004392 | 0.0043919 | 0.004392 | 0.99121 | -0.061614 | 0.99127 | -0.061196 | 1.6267
8 | -0.0029258 | -0.00073312 | 0.0029259 | 0.00073308 | 5.7023e-08 | -3.9142e-08 | 0.0043919 | 0.0043919 | 0.0043919 | 0.99127 | -0.061196 | 0.99129 | -0.061055 | 1.6266
9 | -0.013328 | -0.0033405 | 0.013335 | 0.0033428 | 6.9437e-06 | 2.32e-06 | 0.020119 | 0.020119 | 0.020119 | 0.98572 | -0.10012 | 0.98625 | -0.096361 | 7.4516
10 | 0.072162 | 0.018132 | -0.071832 | -0.018006 | 0.00032995 | 0.00012631 | 0.10766 | 0.10766 | 0.10766 | 0.99751 | -0.01734 | 0.99281 | -0.050354 | 39.8749
11 | -0.077942 | -0.01958 | 0.07813 | 0.019653 | 0.00018846 | 7.2192e-05 | 0.11628 | 0.11628 | 0.11628 | 0.99751 | -0.01734 | 1 | 0 | 43.0682
12 | 0.018928 | 0.0047465 | -0.0189 | -0.0047365 | 2.8033e-05 | 1.0061e-05 | 0.02837 | 0.02837 | 0.02837 | 0.99281 | -0.050354 | 0.99129 | -0.061055 | 10.5074
13 | 0.075784 | 0.019172 | -0.075546 | -0.019081 | 0.00023796 | 9.1133e-05 | 0.11283 | 0.11283 | 0.11283 | 1 | 0 | 0.99676 | -0.022329 | 41.7895
14 | 0.05519 | 0.013916 | -0.054978 | -0.013835 | 0.00021256 | 8.1096e-05 | 0.082154 | 0.082154 | 0.082154 | 1 | 0 | 0.99603 | -0.027592 | 30.4274
15 | 0.074032 | 0.018702 | -0.073835 | -0.018626 | 0.00019655 | 7.5262e-05 | 0.11057 | 0.11057 | 0.11057 | 0.99676 | -0.022329 | 0.99403 | -0.041255 | 40.9521
16 | 0.049465 | 0.012454 | -0.049434 | -0.012442 | 3.1327e-05 | 1.193e-05 | 0.073919 | 0.073919 | 0.073919 | 0.99603 | -0.027592 | 0.99538 | -0.032128 | 27.3773
17 | 0.0055125 | 0.001381 | -0.0055113 | -0.0013809 | 1.2195e-06 | 9.4065e-08 | 0.0082352 | 0.0082353 | 0.0082353 | 0.99603 | -0.027592 | 0.9958 | -0.029191 | 3.0501
18 | -0.0012824 | -0.00032139 | 0.0012824 | 0.00032125 | 2.8202e-08 | -1.3668e-07 | 0.0019559 | 0.0019558 | 0.0019559 | 0.9756 | -0.17144 | 0.97562 | -0.17128 | 0.7244
19 | -0.0097889 | -0.0024532 | 0.0098052 | 0.002458 | 1.6238e-05 | 4.785e-06 | 0.01493 | 0.014929 | 0.01493 | 0.97562 | -0.17128 | 0.97729 | -0.15931 | 5.5296
20 | 0.073835 | 0.018626 | -0.073806 | -0.018615 | 2.9636e-05 | 1.1348e-05 | 0.11057 | 0.11057 | 0.11057 | 0.99403 | -0.041255 | 0.99362 | -0.044117 | 40.9521
21 | 0.047497 | 0.011957 | -0.047419 | -0.011927 | 7.8374e-05 | 2.9821e-05 | 0.071023 | 0.071023 | 0.071023 | 0.99538 | -0.032128 | 0.99368 | -0.043961 | 26.3049
22 | 0.0041645 | 0.0010433 | -0.0041644 | -0.0010434 | 6.1741e-08 | -9.4934e-09 | 0.0062228 | 0.0062229 | 0.0062229 | 0.9958 | -0.029191 | 0.99579 | -0.029298 | 2.3048
23 | 0.045495 | 0.011445 | -0.045445 | -0.011426 | 5.0351e-05 | 1.9141e-05 | 0.068143 | 0.068143 | 0.068143 | 0.99368 | -0.043961 | 0.99255 | -0.051905 | 25.238
24 | 0.001661 | 0.00041594 | -0.0016609 | -0.00041627 | 1.0784e-07 | -3.2343e-07 | 0.002482 | 0.0024821 | 0.0024821 | 0.99579 | -0.029298 | 0.99572 | -0.029768 | 0.9193
25 | 0.045445 | 0.011426 | -0.045351 | -0.01139 | 9.3452e-05 | 3.5527e-05 | 0.068143 | 0.068143 | 0.068143 | 0.99255 | -0.051905 | 0.99044 | -0.066695 | 25.2381
26 | 0.072336 | 0.018247 | -0.072156 | -0.018178 | 0.00018015 | 6.897e-05 | 0.10837 | 0.10837 | 0.10837 | 0.99362 | -0.044117 | 0.99107 | -0.06192 | 40.137
27 | -0.0076649 | -0.001921 | 0.0076673 | 0.0019216 | 2.4656e-06 | 5.7694e-07 | 0.011609 | 0.011609 | 0.011609 | 0.98244 | -0.12337 | 0.98277 | -0.12104 | 4.2997
28 | -0.011605 | -0.0029084 | 0.011608 | 0.0029094 | 3.0258e-06 | 9.6469e-07 | 0.017571 | 0.017571 | 0.017571 | 0.98277 | -0.12104 | 0.98303 | -0.11916 | 6.5077
29 | -0.015753 | -0.0039483 | 0.015765 | 0.0039526 | 1.2314e-05 | 4.2942e-06 | 0.023822 | 0.023821 | 0.023822 | 0.98399 | -0.11233 | 0.98479 | -0.10669 | 8.8228
30 | 0.015753 | 0.0039483 | -0.01575 | -0.0039473 | 2.8436e-06 | 9.9172e-07 | 0.023822 | 0.023822 | 0.023822 | 0.98399 | -0.11233 | 0.98381 | -0.11364 | 8.8228
31 | -0.017394 | -0.004361 | 0.017408 | 0.0043657 | 1.3314e-05 | 4.7276e-06 | 0.026284 | 0.026283 | 0.026284 | 0.98479 | -0.10669 | 0.98556 | -0.10117 | 9.7347
32 | 0.014668 | 0.0036761 | -0.014659 | -0.0036731 | 8.8782e-06 | 3.0479e-06 | 0.022185 | 0.022185 | 0.022185 | 0.98381 | -0.11364 | 0.9832 | -0.11801 | 8.2167
33 | -0.017408 | -0.0043657 | 0.017415 | 0.0043683 | 7.2495e-06 | 2.5739e-06 | 0.026283 | 0.026283 | 0.026283 | 0.98556 | -0.10117 | 0.98599 | -0.098166 | 9.7346
34 | -0.018364 | -0.0046061 | 0.018378 | 0.0046113 | 1.4432e-05 | 5.1665e-06 | 0.027715 | 0.027715 | 0.027715 | 0.98599 | -0.098166 | 0.98679 | -0.092502 | 10.2649
35 | -0.01246 | -0.0031224 | 0.012462 | 0.003123 | 1.9807e-06 | 6.4867e-07 | 0.018861 | 0.018861 | 0.018861 | 0.98303 | -0.11916 | 0.9832 | -0.11801 | 6.9855
36 | 0.0008525 | 0.00021301 | -0.00085244 | -0.00021364 | 5.3517e-08 | -6.3246e-07 | 0.0012902 | 0.0012904 | 0.0012904 | 0.98303 | -0.11916 | 0.98297 | -0.11961 | 0.47794
37 | 0.0021965 | 0.00055004 | -0.0021963 | -0.00055033 | 1.9512e-07 | -2.8378e-07 | 0.0033242 | 0.0033243 | 0.0033243 | 0.9832 | -0.11801 | 0.98311 | -0.11865 | 1.2312
38 | 0.0011545 | 0.00028922 | -0.0011545 | -0.00028934 | 1.9055e-08 | -1.1948e-07 | 0.0017474 | 0.0017474 | 0.0017474 | 0.98311 | -0.11865 | 0.98309 | -0.11877 | 0.64719
39 | 0.0069489 | 0.0017409 | -0.0069478 | -0.0017407 | 1.063e-06 | 2.0789e-07 | 0.010442 | 0.010442 | 0.010442 | 0.99023 | -0.067877 | 0.99007 | -0.068982 | 3.8674
40 | -0.008963 | -0.0022456 | 0.0089636 | 0.0022458 | 6.3005e-07 | 1.7072e-07 | 0.013468 | 0.013468 | 0.013468 | 0.99023 | -0.067877 | 0.9903 | -0.067369 | 4.9883
41 | 0.0057475 | 0.0014398 | -0.0057466 | -0.0014397 | 8.7773e-07 | 9.5188e-08 | 0.0086379 | 0.008638 | 0.008638 | 0.99007 | -0.068982 | 0.98991 | -0.070087 | 3.1992
42 | -0.010467 | -0.0026227 | 0.010468 | 0.0026228 | 1.9982e-07 | 6.0199e-08 | 0.015728 | 0.015728 | 0.015728 | 0.9903 | -0.067369 | 0.99032 | -0.067231 | 5.8252
43 | -0.044797 | -0.011239 | 0.044885 | 0.011272 | 8.7776e-05 | 3.3378e-05 | 0.068107 | 0.068107 | 0.068107 | 0.97879 | -0.14856 | 0.98077 | -0.13446 | 25.2249
44 | 0.027438 | 0.0068856 | -0.02742 | -0.0068788 | 1.8234e-05 | 6.8021e-06 | 0.041716 | 0.041716 | 0.041716 | 0.97879 | -0.14856 | 0.97812 | -0.15335 | 15.4505
45 | 0.016005 | 0.0040139 | -0.015994 | -0.0040101 | 1.0621e-05 | 3.7239e-06 | 0.024332 | 0.024332 | 0.024332 | 0.97879 | -0.14856 | 0.97812 | -0.15335 | 9.012
46 | -0.046245 | -0.011613 | 0.046272 | 0.011623 | 2.7308e-05 | 1.0391e-05 | 0.07017 | 0.07017 | 0.07017 | 0.98077 | -0.13446 | 0.98137 | -0.13022 | 25.9891
47 | 0.02742 | 0.0068788 | -0.027399 | -0.0068709 | 2.11e-05 | 7.8717e-06 | 0.041716 | 0.041717 | 0.041717 | 0.97812 | -0.15335 | 0.97734 | -0.1589 | 15.4506
48 | 0.014893 | 0.0037341 | -0.014884 | -0.0037312 | 8.4082e-06 | 2.9047e-06 | 0.022657 | 0.022657 | 0.022657 | 0.97812 | -0.15335 | 0.97755 | -0.15743 | 8.3915
49 | -0.04832 | -0.012137 | 0.04841 | 0.012171 | 9.0101e-05 | 3.4314e-05 | 0.073276 | 0.073276 | 0.073276 | 0.98137 | -0.13022 | 0.98326 | -0.11683 | 27.1392
50 | 0.025381 | 0.0063652 | -0.02538 | -0.0063649 | 8.7797e-07 | 3.2587e-07 | 0.038644 | 0.038644 | 0.038644 | 0.97734 | -0.1589 | 0.97731 | -0.15915 | 14.3127
51 | 0.013548 | 0.0033964 | -0.013546 | -0.0033957 | 2.0183e-06 | 6.8095e-07 | 0.020623 | 0.020624 | 0.020624 | 0.97755 | -0.15743 | 0.9774 | -0.1585 | 7.6383
52 | -0.049791 | -0.012517 | 0.049794 | 0.012518 | 2.5966e-06 | 9.894e-07 | 0.075366 | 0.075366 | 0.075366 | 0.98326 | -0.11683 | 0.98331 | -0.11646 | 27.9132
53 | 0.011944 | 0.0029941 | -0.011943 | -0.0029937 | 1.3286e-06 | 4.3031e-07 | 0.018184 | 0.018184 | 0.018184 | 0.9774 | -0.1585 | 0.97729 | -0.15931 | 6.7348
54 | 0.023019 | 0.0057732 | -0.023001 | -0.0057664 | 1.8469e-05 | 6.8019e-06 | 0.03505 | 0.03505 | 0.03505 | 0.97731 | -0.15915 | 0.9765 | -0.16495 | 12.9815
55 | -0.05159 | -0.012968 | 0.051618 | 0.012979 | 2.7768e-05 | 1.0588e-05 | 0.078084 | 0.078084 | 0.078084 | 0.98331 | -0.11646 | 0.98385 | -0.1126 | 28.9199
56 | 0.020729 | 0.0051969 | -0.020728 | -0.0051965 | 9.8309e-07 | 3.5836e-07 | 0.031587 | 0.031587 | 0.031587 | 0.9765 | -0.16495 | 0.97645 | -0.16529 | 11.699
57 | 0.013445 | 0.0033696 | -0.01344 | -0.0033679 | 5.1102e-06 | 1.7066e-06 | 0.020186 | 0.020186 | 0.020186 | 0.99107 | -0.06192 | 0.99068 | -0.064666 | 7.4764
58 | 0.058711 | 0.014808 | -0.058672 | -0.014793 | 3.8699e-05 | 1.4782e-05 | 0.088184 | 0.088184 | 0.088184 | 0.99107 | -0.06192 | 0.9904 | -0.066624 | 32.6606
59 | 0.011747 | 0.0029437 | -0.011743 | -0.0029424 | 4.1681e-06 | 1.327e-06 | 0.017644 | 0.017644 | 0.017644 | 0.99068 | -0.064666 | 0.99032 | -0.067231 | 6.535
60 | 0.056775 | 0.014318 | -0.056639 | -0.014266 | 0.00013605 | 5.1941e-05 | 0.085334 | 0.085334 | 0.085334 | 0.9904 | -0.066624 | 0.98795 | -0.08376 | 31.6051
61 | -0.052722 | -0.013256 | 0.052741 | 0.013263 | 1.9474e-05 | 7.4278e-06 | 0.079753 | 0.079753 | 0.079753 | 0.98385 | -0.1126 | 0.98423 | -0.10995 | 29.5382
62 | -0.054036 | -0.013588 | 0.054174 | 0.01364 | 0.00013782 | 5.2586e-05 | 0.081711 | 0.081711 | 0.081711 | 0.98423 | -0.10995 | 0.98682 | -0.091691 | 30.2633
63 | -0.055592 | -0.013996 | 0.055654 | 0.014019 | 6.1659e-05 | 2.3535e-05 | 0.083849 | 0.083849 | 0.083849 | 0.98682 | -0.091691 | 0.98795 | -0.08376 | 31.0553
64 | 0.019354 | 0.00486 | -0.019329 | -0.0048511 | 2.4522e-05 | 8.8381e-06 | 0.029126 | 0.029127 | 0.029127 | 0.98887 | -0.077805 | 0.98757 | -0.086933 | 10.7876
65 | -0.020133 | -0.0050552 | 0.020145 | 0.0050595 | 1.1984e-05 | 4.3406e-06 | 0.030298 | 0.030298 | 0.030298 | 0.98887 | -0.077805 | 0.98947 | -0.073524 | 11.2216
66 | 0.018393 | 0.0046163 | -0.018378 | -0.0046113 | 1.4212e-05 | 5.0872e-06 | 0.027715 | 0.027715 | 0.027715 | 0.98757 | -0.086933 | 0.98679 | -0.092502 | 10.2649
67 | 0.023099 | 0.0057972 | -0.023083 | -0.0057913 | 1.6164e-05 | 5.9415e-06 | 0.03474 | 0.03474 | 0.03474 | 0.98947 | -0.073524 | 0.98876 | -0.078568 | 12.8666
68 | -0.043243 | -0.010857 | 0.043267 | 0.010866 | 2.3947e-05 | 9.0939e-06 | 0.065038 | 0.065038 | 0.065038 | 0.98947 | -0.073524 | 0.99004 | -0.06954 | 24.0882
69 | 0.021945 | 0.0055062 | -0.021908 | -0.0054925 | 3.753e-05 | 1.3729e-05 | 0.033028 | 0.033028 | 0.033028 | 0.98876 | -0.078568 | 0.98702 | -0.090913 | 12.2327
70 | -0.044326 | -0.011131 | 0.044343 | 0.011138 | 1.7531e-05 | 6.6612e-06 | 0.066628 | 0.066628 | 0.066628 | 0.99004 | -0.06954 | 0.99044 | -0.066695 | 24.6772
71 | 0.01627 | 0.0040797 | -0.016258 | -0.0040754 | 1.2273e-05 | 4.3031e-06 | 0.02453 | 0.02453 | 0.02453 | 0.98702 | -0.090913 | 0.98625 | -0.096361 | 9.0851
72 | 0.0010082 | 0.0002526 | -0.0010081 | -0.00025266 | 8.1924e-09 | -6.9488e-08 | 0.0015199 | 0.0015199 | 0.0015199 | 0.98702 | -0.090913 | 0.98701 | -0.090972 | 0.56292
73 | 0.0046363 | 0.0011615 | -0.0046362 | -0.0011615 | 1.3629e-07 | -5.3946e-09 | 0.006969 | 0.006969 | 0.006969 | 0.98991 | -0.070087 | 0.98988 | -0.070299 | 2.5811
74 | 0.018495 | 0.0046371 | -0.018486 | -0.0046338 | 9.2073e-06 | 3.3091e-06 | 0.028186 | 0.028186 | 0.028186 | 0.97645 | -0.16529 | 0.97595 | -0.16888 | 10.4392
75 | 0.016056 | 0.0040247 | -0.016052 | -0.0040232 | 4.0647e-06 | 1.4276e-06 | 0.02448 | 0.02448 | 0.02448 | 0.97595 | -0.16888 | 0.9757 | -0.17071 | 9.0667
76 | -0.0041703 | -0.0010452 | 0.0041708 | 0.0010451 | 5.3849e-07 | -5.8239e-08 | 0.0063668 | 0.0063667 | 0.0063668 | 0.97465 | -0.17822 | 0.97478 | -0.17728 | 2.3581
77 | 0.002169 | 0.0005436 | -0.002169 | -0.0005436 | 2.3886e-10 | -3.398e-10 | 0.0033114 | 0.0033114 | 0.0033114 | 0.97465 | -0.17822 | 0.97465 | -0.17822 | 1.2264
78 | -0.0062336 | -0.0015621 | 0.0062338 | 0.0015621 | 1.3927e-07 | 2.2838e-08 | 0.0095157 | 0.0095156 | 0.0095157 | 0.97478 | -0.17728 | 0.9748 | -0.17712 | 3.5243
79 | 0.01371 | 0.0034365 | -0.013702 | -0.0034335 | 8.7665e-06 | 2.9707e-06 | 0.02091 | 0.02091 | 0.02091 | 0.9757 | -0.17071 | 0.97505 | -0.17533 | 7.7444
80 | 0.0039764 | 0.00099634 | -0.0039759 | -0.00099642 | 4.5999e-07 | -7.2741e-08 | 0.0060682 | 0.0060683 | 0.0060683 | 0.97505 | -0.17533 | 0.97494 | -0.17617 | 2.2475
81 | 0.0076547 | 0.0019182 | -0.0076528 | -0.0019178 | 1.8967e-06 | 4.5176e-07 | 0.011682 | 0.011682 | 0.011682 | 0.97505 | -0.17533 | 0.9748 | -0.17712 | 4.3266
82 | 0.0016869 | 0.00042274 | -0.0016869 | -0.00042278 | 1.4271e-08 | -3.7533e-08 | 0.0025747 | 0.0025747 | 0.0025747 | 0.97494 | -0.17617 | 0.97493 | -0.17623 | 0.95358
83 | 0.0037499 | 0.00093935 | -0.0037498 | -0.00093938 | 1.052e-07 | -2.7746e-08 | 0.0056368 | 0.0056368 | 0.0056368 | 0.98988 | -0.070299 | 0.98986 | -0.070502 | 2.0877
84 | 0.0031049 | 0.00077775 | -0.0031046 | -0.00077794 | 3.2535e-07 | -1.8249e-07 | 0.0046674 | 0.0046675 | 0.0046675 | 0.98986 | -0.070502 | 0.98975 | -0.071259 | 1.7287
85 | 0.0014645 | 0.0003669 | -0.0014645 | -0.00036703 | 3.5634e-08 | -1.3768e-07 | 0.0022017 | 0.0022018 | 0.0022018 | 0.98975 | -0.071259 | 0.98972 | -0.071435 | 0.81548

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21237 | 0.053359

## res_load
| p_mw | q_mvar
0 | 0.003263 | 0.00081778
1 | 0.0043582 | 0.0010923
2 | 0.0021101 | 0.00052885
3 | 0.0021332 | 0.00053462
4 | 0.0029256 | 0.00073324
5 | 0.0014536 | 0.0003643
6 | 0.00578 | 0.0014486
7 | 0.052904 | 0.013259
8 | 0.0024625 | 0.00061717
9 | 0.015974 | 0.0040034
10 | 0.0015146 | 0.0003796
11 | 0.0012824 | 0.00032139
12 | 0.0085065 | 0.0021319
13 | 0.001937 | 0.00048546
14 | 0.0013468 | 0.00033753
15 | 0.0019237 | 0.00048212
16 | 0.0025034 | 0.00062741
17 | 0.0016609 | 0.00041627
18 | 0.0014696 | 0.00036832
19 | 0.0076649 | 0.001921
20 | 0.0039374 | 0.00098681
21 | 0.0016295 | 0.0004084
22 | 0.0010821 | 0.00027119
23 | 0.00094886 | 0.00023781
24 | 0.00085244 | 0.00021364
25 | 0.0010418 | 0.00026111
26 | 0.0020141 | 0.00050478
27 | 0.0012004 | 0.00030084
28 | 0.0015038 | 0.00037688
29 | 0.001354 | 0.00033935
30 | 0.00136 | 0.00034086
31 | 0.0011013 | 0.00027602
32 | 0.002048 | 0.00051328
33 | 0.002018 | 0.00050575
34 | 0.001336 | 0.00033483
35 | 0.0013811 | 0.00034614
36 | 0.0016024 | 0.00040161
37 | 0.0021375 | 0.0005357
38 | 0.0023607 | 0.00059166
39 | 0.0017961 | 0.00045015
40 | 0.0022723 | 0.0005695
41 | 0.0016924 | 0.00042415
42 | 0.0018969 | 0.00047542
43 | 0.0011038 | 0.00027664
44 | 0.001295 | 0.00032455
45 | 0.0014182 | 0.00035543
46 | 0.00098568 | 0.00024704
47 | 0.00077881 | 0.00019519
48 | 0.00093681 | 0.00023479
49 | 0.0011375 | 0.00028508
50 | 0.0010582 | 0.00026522
51 | 0.0046291 | 0.0011602
52 | 0.0029233 | 0.00073265
53 | 0.0010081 | 0.00025266
54 | 0.001008 | 0.00025263
55 | 0.0011545 | 0.00028934
56 | 0.0011103 | 0.00027827
57 | 0.0022321 | 0.00055942
58 | 0.0024305 | 0.00060915
59 | 0.0020013 | 0.00050157
60 | 0.0020628 | 0.00051699
61 | 0.002169 | 0.0005436
62 | 0.0023412 | 0.00058676
63 | 0.0012754 | 0.00031965
64 | 0.0020706 | 0.00051893
65 | 0.0014191 | 0.00035565
66 | 0.002289 | 0.00057368
67 | 0.0016869 | 0.00042278
68 | 0.00088625 | 0.00022212
69 | 0.00064488 | 0.00016162
70 | 0.0016401 | 0.00041104
71 | 0.0014645 | 0.00036703

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1