## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1005-1_2_2_node_12 | 0.4 | n |  | TRUE
1 | bus_LV_1005-1_2_2_node_13 | 0.4 | n |  | TRUE
2 | bus_LV_1005-1_2_2_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_1005-1_2_2_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1005-1_2_2_node_16 | 0.4 | n |  | TRUE
5 | bus_LV_1005-1_2_2_node_323 | 0.4 | n |  | TRUE
6 | bus_LV_1005-1_2_2_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1005-1_2_2_node_119 | 0.4 | n |  | TRUE
8 | bus_LV_1005-1_2_2_node_124 | 0.4 | n |  | TRUE
9 | bus_LV_1005-1_2_2_node_359 | 0.4 | n |  | TRUE
10 | bus_LV_1005-1_2_2_node_120 | 0.4 | n |  | TRUE
11 | bus_LV_1005-1_2_2_node_125 | 0.4 | n |  | TRUE
12 | bus_LV_1005-1_2_2_node_126 | 0.4 | n |  | TRUE
13 | bus_LV_1005-1_2_2_node_361 | 0.4 | n |  | TRUE
14 | bus_LV_1005-1_2_2_node_292 | 0.4 | n |  | TRUE
15 | bus_LV_1005-1_2_2_node_344 | 0.4 | n |  | TRUE
16 | bus_LV_1005-1_2_2_node_339 | 0.4 | n |  | TRUE
17 | bus_LV_1005-1_2_2_node_261 | 0.4 | n |  | TRUE
18 | bus_LV_1005-1_2_2_node_262 | 0.4 | n |  | TRUE
19 | bus_LV_1005-1_2_2_node_263 | 0.4 | n |  | TRUE
20 | bus_LV_1005-1_2_2_node_264 | 0.4 | n |  | TRUE
21 | bus_LV_1005-1_2_2_node_265 | 0.4 | n |  | TRUE
22 | bus_LV_1005-1_2_2_node_266 | 0.4 | n |  | TRUE
23 | bus_LV_1005-1_2_2_node_268 | 0.4 | n |  | TRUE
24 | bus_LV_1005-1_2_2_node_267 | 0.4 | n |  | TRUE
25 | bus_LV_1005-1_2_2_node_273 | 0.4 | n |  | TRUE
26 | bus_LV_1005-1_2_2_node_270 | 0.4 | n |  | TRUE
27 | bus_LV_1005-1_2_2_node_271 | 0.4 | n |  | TRUE
28 | bus_LV_1005-1_2_2_node_272 | 0.4 | n |  | TRUE
29 | bus_LV_1005-1_2_2_node_274 | 0.4 | n |  | TRUE
30 | bus_LV_1005-1_2_2_node_275 | 0.4 | n |  | TRUE
31 | bus_LV_1005-1_2_2_node_276 | 0.4 | n |  | TRUE
32 | bus_LV_1005-1_2_2_node_355 | 0.4 | n |  | TRUE
33 | bus_LV_1005-1_2_2_node_281 | 0.4 | n |  | TRUE
34 | bus_LV_1005-1_2_2_node_277 | 0.4 | n |  | TRUE
35 | bus_LV_1005-1_2_2_node_278 | 0.4 | n |  | TRUE
36 | bus_LV_1005-1_2_2_node_279 | 0.4 | n |  | TRUE
37 | bus_LV_1005-1_2_2_node_280 | 0.4 | n |  | TRUE
38 | bus_LV_1005-1_2_2_node_282 | 0.4 | n |  | TRUE
39 | bus_LV_1005-1_2_2_node_291 | 0.4 | n |  | TRUE
40 | bus_LV_1005-1_2_2_node_283 | 0.4 | n |  | TRUE
41 | bus_LV_1005-1_2_2_node_284 | 0.4 | n |  | TRUE
42 | bus_LV_1005-1_2_2_node_285 | 0.4 | n |  | TRUE
43 | bus_LV_1005-1_2_2_node_286 | 0.4 | n |  | TRUE
44 | bus_LV_1005-1_2_2_node_287 | 0.4 | n |  | TRUE
45 | bus_LV_1005-1_2_2_node_288 | 0.4 | n |  | TRUE
46 | bus_LV_1005-1_2_2_node_289 | 0.4 | n |  | TRUE
47 | bus_LV_1005-1_2_2_node_290 | 0.4 | n |  | TRUE
48 | bus_LV_1005-1_2_2_node_296 | 0.4 | n |  | TRUE
49 | bus_LV_1005-1_2_2_node_356 | 0.4 | n |  | TRUE
50 | bus_LV_1005-1_2_2_node_293 | 0.4 | n |  | TRUE
51 | bus_LV_1005-1_2_2_node_294 | 0.4 | n |  | TRUE
52 | bus_LV_1005-1_2_2_node_295 | 0.4 | n |  | TRUE
53 | bus_LV_1005-1_2_2_node_297 | 0.4 | n |  | TRUE
54 | bus_LV_1005-1_2_2_node_301 | 0.4 | n |  | TRUE
55 | bus_LV_1005-1_2_2_node_299 | 0.4 | n |  | TRUE
56 | bus_LV_1005-1_2_2_node_298 | 0.4 | n |  | TRUE
57 | bus_LV_1005-1_2_2_node_306 | 0.4 | n |  | TRUE
58 | bus_LV_1005-1_2_2_node_318 | 0.4 | n |  | TRUE
59 | bus_LV_1005-1_2_2_node_300 | 0.4 | n |  | TRUE
60 | bus_LV_1005-1_2_2_node_302 | 0.4 | n |  | TRUE
61 | bus_LV_1005-1_2_2_node_303 | 0.4 | n |  | TRUE
62 | bus_LV_1005-1_2_2_node_317 | 0.4 | n |  | TRUE
63 | bus_LV_1005-1_2_2_node_304 | 0.4 | n |  | TRUE
64 | bus_LV_1005-1_2_2_node_305 | 0.4 | n |  | TRUE
65 | bus_LV_1005-1_2_2_node_307 | 0.4 | n |  | TRUE
66 | bus_LV_1005-1_2_2_node_309 | 0.4 | n |  | TRUE
67 | bus_LV_1005-1_2_2_node_310 | 0.4 | n |  | TRUE
68 | bus_LV_1005-1_2_2_node_308 | 0.4 | n |  | TRUE
69 | bus_LV_1005-1_2_2_node_324 | 0.4 | n |  | TRUE
70 | bus_LV_1005-1_2_2_node_322 | 0.4 | n |  | TRUE
71 | bus_LV_1005-1_2_2_node_328 | 0.4 | n |  | TRUE
72 | bus_LV_1005-1_2_2_node_313 | 0.4 | n |  | TRUE
73 | bus_LV_1005-1_2_2_node_316 | 0.4 | n |  | TRUE
74 | bus_LV_1005-1_2_2_node_311 | 0.4 | n |  | TRUE
75 | bus_LV_1005-1_2_2_node_312 | 0.4 | n |  | TRUE
76 | bus_LV_1005-1_2_2_node_314 | 0.4 | n |  | TRUE
77 | bus_LV_1005-1_2_2_node_352 | 0.4 | n |  | TRUE
78 | bus_LV_1005-1_2_2_node_315 | 0.4 | n |  | TRUE
79 | bus_LV_1005-1_2_2_node_319 | 0.4 | n |  | TRUE
80 | bus_LV_1005-1_2_2_node_320 | 0.4 | n |  | TRUE
81 | bus_LV_1005-1_2_2_node_321 | 0.4 | n |  | TRUE
82 | bus_LV_1005-1_2_2_node_325 | 0.4 | n |  | TRUE
83 | bus_LV_1005-1_2_2_node_326 | 0.4 | n |  | TRUE
84 | bus_LV_1005-1_2_2_node_327 | 0.4 | n |  | TRUE
85 | bus_LV_1005-1_2_2_node_335 | 0.4 | n |  | TRUE
86 | bus_LV_1005-1_2_2_node_336 | 0.4 | n |  | TRUE
87 | bus_LV_1005-1_2_2_node_337 | 0.4 | n |  | TRUE
88 | bus_LV_1005-1_2_2_node_338 | 0.4 | n |  | TRUE
89 | bus_LV_1005-1_2_2_node_340 | 0.4 | n |  | TRUE
90 | bus_LV_1005-1_2_2_node_341 | 0.4 | n |  | TRUE
91 | bus_LV_1005-1_2_2_node_342 | 0.4 | n |  | TRUE
92 | bus_LV_1005-1_2_2_node_343 | 0.4 | n |  | TRUE
93 | bus_LV_1005-1_2_2_node_346 | 0.4 | n |  | TRUE
94 | bus_LV_1005-1_2_2_node_345 | 0.4 | n |  | TRUE
95 | bus_LV_1005-1_2_2_node_347 | 0.4 | n |  | TRUE
96 | bus_LV_1005-1_2_2_node_348 | 0.4 | n |  | TRUE
97 | bus_LV_1005-1_2_2_node_351 | 0.4 | n |  | TRUE
98 | bus_LV_1005-1_2_2_node_349 | 0.4 | n |  | TRUE
99 | bus_LV_1005-1_2_2_node_350 | 0.4 | n |  | TRUE
100 | bus_LV_1005-1_2_2_node_371 | 0.4 | n |  | TRUE
101 | bus_LV_1005-1_2_2_node_353 | 0.4 | n |  | TRUE
102 | bus_LV_1005-1_2_2_node_357 | 0.4 | n |  | TRUE
103 | bus_LV_1005-1_2_2_node_362 | 0.4 | n |  | TRUE
104 | bus_MV_0_node_304 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1005-1_2_2_load_12 | 0 | 0.00031532 | 7.9026e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1005-1_2_2_load_13 | 1 | 0.00015555 | 3.8984e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1005-1_2_2_load_16 | 4 | 0.0016093 | 0.00040332 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1005-1_2_2_load_323 | 5 | 0.00020913 | 5.2413e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1005-1_2_2_load_35 | 6 | 0.00070874 | 0.00017763 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1005-1_2_2_load_119 | 7 | 0.00017799 | 4.4609e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1005-1_2_2_load_359 | 9 | 0.00015936 | 3.9938e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1005-1_2_2_load_120 | 10 | 7.2078e-05 | 1.8065e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1005-1_2_2_load_361 | 13 | 0.00040139 | 0.0001006 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1005-1_2_2_load_292 | 14 | 8.9721e-05 | 2.2486e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1005-1_2_2_load_344 | 15 | 5.1402e-05 | 1.2883e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1005-1_2_2_load_339 | 16 | 4.9903e-05 | 1.2507e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1005-1_2_2_load_261 | 17 | 0.00023017 | 5.7686e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1005-1_2_2_load_262 | 18 | 9.5076e-05 | 2.3828e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1005-1_2_2_load_263 | 19 | 0.00018311 | 4.5892e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1005-1_2_2_load_264 | 20 | 0.00010572 | 2.6495e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1005-1_2_2_load_266 | 22 | 0.00053535 | 0.00013417 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1005-1_2_2_load_267 | 24 | 0.0001806 | 4.5263e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1005-1_2_2_load_273 | 25 | 7.6086e-05 | 1.9069e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1005-1_2_2_load_270 | 26 | 0.00027515 | 6.8959e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1005-1_2_2_load_271 | 27 | 0.00010693 | 2.68e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1005-1_2_2_load_274 | 29 | 0.00017594 | 4.4094e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1005-1_2_2_load_275 | 30 | 0.00069764 | 0.00017485 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1005-1_2_2_load_276 | 31 | 7.7654e-05 | 1.9462e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1005-1_2_2_load_355 | 32 | 0.0018068 | 0.00045282 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1005-1_2_2_load_281 | 33 | 0.00011377 | 2.8514e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1005-1_2_2_load_277 | 34 | 0.00013329 | 3.3407e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1005-1_2_2_load_278 | 35 | 0.00013963 | 3.4994e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1005-1_2_2_load_279 | 36 | 0.00021328 | 5.3454e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1005-1_2_2_load_283 | 40 | 0.0003809 | 9.5463e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1005-1_2_2_load_284 | 41 | 0.0001671 | 4.1878e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1005-1_2_2_load_285 | 42 | 0.00026914 | 6.7453e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1005-1_2_2_load_286 | 43 | 0.00058952 | 0.00014775 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1005-1_2_2_load_288 | 45 | 0.00019054 | 4.7754e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1005-1_2_2_load_289 | 46 | 0.00021402 | 5.3639e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1005-1_2_2_load_356 | 49 | 0.00038968 | 9.7663e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1005-1_2_2_load_293 | 50 | 0.00082873 | 0.0002077 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1005-1_2_2_load_294 | 51 | 0.0003243 | 8.1278e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1005-1_2_2_load_295 | 52 | 7.5456e-05 | 1.8911e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1005-1_2_2_load_301 | 54 | 7.4551e-05 | 1.8684e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1005-1_2_2_load_299 | 55 | 0.00056152 | 0.00014073 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1005-1_2_2_load_318 | 58 | 0.00039686 | 9.9463e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1005-1_2_2_load_300 | 59 | 0.00015574 | 3.9032e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1005-1_2_2_load_317 | 62 | 0.00016732 | 4.1934e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1005-1_2_2_load_304 | 63 | 0.00013331 | 3.341e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1005-1_2_2_load_305 | 64 | 0.00020355 | 5.1015e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1005-1_2_2_load_328 | 71 | 0.00020461 | 5.128e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1005-1_2_2_load_316 | 73 | 0.00043667 | 0.00010944 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1005-1_2_2_load_311 | 74 | 0.00036147 | 9.0593e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1005-1_2_2_load_312 | 75 | 0.00068444 | 0.00017154 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1005-1_2_2_load_352 | 77 | 0.0049983 | 0.0012527 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1005-1_2_2_load_319 | 79 | 0.00071351 | 0.00017882 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1005-1_2_2_load_320 | 80 | 0.00030674 | 7.6876e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1005-1_2_2_load_321 | 81 | 0.00043261 | 0.00010842 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1005-1_2_2_load_325 | 82 | 0.0003151 | 7.8972e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1005-1_2_2_load_326 | 83 | 0.00031737 | 7.9541e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1005-1_2_2_load_327 | 84 | 0.00082414 | 0.00020655 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1005-1_2_2_load_335 | 85 | 0.00011743 | 2.943e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1005-1_2_2_load_336 | 86 | 0.0001699 | 4.258e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1005-1_2_2_load_338 | 88 | 0.00033094 | 8.294e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1005-1_2_2_load_340 | 89 | 0.00019522 | 4.8927e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1005-1_2_2_load_341 | 90 | 5.0166e-05 | 1.2573e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1005-1_2_2_load_346 | 93 | 0.00019811 | 4.9652e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1005-1_2_2_load_345 | 94 | 5.3609e-05 | 1.3436e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1005-1_2_2_load_349 | 98 | 0.00043235 | 0.00010836 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1005-1_2_2_load_350 | 99 | 0.00020312 | 5.0906e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1005-1_2_2_load_371 | 100 | 5.081e-05 | 1.2734e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1005-1_2_2_load_353 | 101 | 0.0049097 | 0.0012305 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1005-1_2_2_load_357 | 102 | 0.00015279 | 3.8293e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1005-1_2_2_load_362 | 103 | 0.00019335 | 4.8459e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1005-1_2_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.062437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1005-1_2_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1005-1_2_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.01264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1005-1_2_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1005-1_2_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.31199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1005-1_2_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0015213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1005-1_2_2_line_6 | NAYY 4x150 SE | 5 | 68 | 0.059171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1005-1_2_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.19036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1005-1_2_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.12199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1005-1_2_2_line_9 | NAYY 4x150 SE | 8 | 11 | 0.15216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1005-1_2_2_line_10 | NAYY 4x150 SE | 8 | 12 | 0.017686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1005-1_2_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.062329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1005-1_2_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.058794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1005-1_2_2_line_13 | NAYY 4x150 SE | 11 | 14 | 0.28043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1005-1_2_2_line_14 | NAYY 4x150 SE | 11 | 15 | 0.048766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1005-1_2_2_line_15 | NAYY 4x150 SE | 12 | 16 | 0.17662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1005-1_2_2_line_16 | NAYY 4x150 SE | 13 | 103 | 0.0049259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1005-1_2_2_line_17 | NAYY 4x150 SE | 14 | 39 | 0.0032632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1005-1_2_2_line_18 | NAYY 4x150 SE | 15 | 91 | 0.13473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1005-1_2_2_line_19 | NAYY 4x150 SE | 16 | 87 | 0.05393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1005-1_2_2_line_20 | NAYY 4x150 SE | 17 | 18 | 0.0043439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1005-1_2_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.00052133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1005-1_2_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.10212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1005-1_2_2_line_23 | NAYY 4x150 SE | 19 | 21 | 0.1762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1005-1_2_2_line_24 | NAYY 4x150 SE | 20 | 22 | 0.010735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1005-1_2_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.13538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1005-1_2_2_line_26 | NAYY 4x150 SE | 22 | 24 | 0.038059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1005-1_2_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.048169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1005-1_2_2_line_28 | NAYY 4x150 SE | 23 | 26 | 0.025229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1005-1_2_2_line_29 | NAYY 4x150 SE | 25 | 31 | 0.087951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1005-1_2_2_line_30 | NAYY 4x150 SE | 26 | 27 | 0.025196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1005-1_2_2_line_31 | NAYY 4x150 SE | 27 | 28 | 0.19563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1005-1_2_2_line_32 | NAYY 4x150 SE | 28 | 29 | 0.037034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1005-1_2_2_line_33 | NAYY 4x150 SE | 28 | 30 | 0.015324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1005-1_2_2_line_34 | NAYY 4x150 SE | 30 | 32 | 0.014381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1005-1_2_2_line_35 | NAYY 4x150 SE | 31 | 33 | 0.15601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1005-1_2_2_line_36 | NAYY 4x150 SE | 33 | 38 | 0.16357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1005-1_2_2_line_37 | NAYY 4x150 SE | 33 | 40 | 0.012453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1005-1_2_2_line_38 | NAYY 4x150 SE | 34 | 35 | 0.01689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1005-1_2_2_line_39 | NAYY 4x150 SE | 34 | 36 | 0.025004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1005-1_2_2_line_40 | NAYY 4x150 SE | 35 | 37 | 0.023606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1005-1_2_2_line_41 | NAYY 4x150 SE | 37 | 38 | 0.002301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1005-1_2_2_line_42 | NAYY 4x150 SE | 37 | 39 | 0.12305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1005-1_2_2_line_43 | NAYY 4x150 SE | 38 | 41 | 0.024015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1005-1_2_2_line_44 | NAYY 4x150 SE | 39 | 45 | 0.10831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1005-1_2_2_line_45 | NAYY 4x150 SE | 42 | 43 | 0.05368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1005-1_2_2_line_46 | NAYY 4x150 SE | 42 | 44 | 0.059407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1005-1_2_2_line_47 | NAYY 4x150 SE | 43 | 45 | 0.013825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1005-1_2_2_line_48 | NAYY 4x150 SE | 44 | 46 | 0.1083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1005-1_2_2_line_49 | NAYY 4x150 SE | 44 | 47 | 0.068628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1005-1_2_2_line_50 | NAYY 4x150 SE | 47 | 48 | 0.26532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1005-1_2_2_line_51 | NAYY 4x150 SE | 47 | 49 | 0.10814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1005-1_2_2_line_52 | NAYY 4x150 SE | 48 | 53 | 0.074505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1005-1_2_2_line_53 | NAYY 4x150 SE | 48 | 51 | 0.16594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1005-1_2_2_line_54 | NAYY 4x150 SE | 49 | 102 | 0.0059806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1005-1_2_2_line_55 | NAYY 4x150 SE | 50 | 51 | 0.0032833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1005-1_2_2_line_56 | NAYY 4x150 SE | 50 | 52 | 0.0093841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1005-1_2_2_line_57 | NAYY 4x150 SE | 53 | 54 | 0.096522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1005-1_2_2_line_58 | NAYY 4x150 SE | 53 | 55 | 0.039255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1005-1_2_2_line_59 | NAYY 4x150 SE | 54 | 60 | 0.17028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1005-1_2_2_line_60 | NAYY 4x150 SE | 55 | 59 | 0.0187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1005-1_2_2_line_61 | NAYY 4x150 SE | 56 | 57 | 0.081499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1005-1_2_2_line_62 | NAYY 4x150 SE | 56 | 58 | 0.028627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1005-1_2_2_line_63 | NAYY 4x150 SE | 57 | 66 | 0.27713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1005-1_2_2_line_64 | NAYY 4x150 SE | 57 | 63 | 0.20823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1005-1_2_2_line_65 | NAYY 4x150 SE | 58 | 79 | 0.014091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1005-1_2_2_line_66 | NAYY 4x150 SE | 60 | 61 | 0.049242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1005-1_2_2_line_67 | NAYY 4x150 SE | 61 | 62 | 0.12175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1005-1_2_2_line_68 | NAYY 4x150 SE | 62 | 78 | 0.043489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1005-1_2_2_line_69 | NAYY 4x150 SE | 63 | 64 | 0.021253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1005-1_2_2_line_70 | NAYY 4x150 SE | 64 | 65 | 0.075275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1005-1_2_2_line_71 | NAYY 4x150 SE | 65 | 67 | 0.026366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1005-1_2_2_line_72 | NAYY 4x150 SE | 66 | 70 | 0.069827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1005-1_2_2_line_73 | NAYY 4x150 SE | 66 | 69 | 0.07918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1005-1_2_2_line_74 | NAYY 4x150 SE | 66 | 71 | 0.018326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1005-1_2_2_line_75 | NAYY 4x150 SE | 67 | 72 | 0.094626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1005-1_2_2_line_76 | NAYY 4x150 SE | 67 | 73 | 0.047075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1005-1_2_2_line_77 | NAYY 4x150 SE | 68 | 69 | 0.024026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1005-1_2_2_line_78 | NAYY 4x150 SE | 69 | 83 | 0.025997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1005-1_2_2_line_79 | NAYY 4x150 SE | 70 | 82 | 0.056598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1005-1_2_2_line_80 | NAYY 4x150 SE | 70 | 81 | 0.0094627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1005-1_2_2_line_81 | NAYY 4x150 SE | 71 | 74 | 0.13632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1005-1_2_2_line_82 | NAYY 4x150 SE | 72 | 75 | 0.010613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1005-1_2_2_line_83 | NAYY 4x150 SE | 73 | 78 | 0.031875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1005-1_2_2_line_84 | NAYY 4x150 SE | 75 | 76 | 0.20056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1005-1_2_2_line_85 | NAYY 4x150 SE | 76 | 77 | 0.44252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1005-1_2_2_line_86 | NAYY 4x150 SE | 77 | 101 | 0.0036266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1005-1_2_2_line_87 | NAYY 4x150 SE | 80 | 81 | 0.25846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1005-1_2_2_line_88 | NAYY 4x150 SE | 82 | 84 | 0.11167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1005-1_2_2_line_89 | NAYY 4x150 SE | 85 | 86 | 0.011178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1005-1_2_2_line_90 | NAYY 4x150 SE | 85 | 87 | 0.13871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1005-1_2_2_line_91 | NAYY 4x150 SE | 86 | 88 | 0.0061233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1005-1_2_2_line_92 | NAYY 4x150 SE | 89 | 90 | 0.011762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1005-1_2_2_line_93 | NAYY 4x150 SE | 89 | 91 | 0.12493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1005-1_2_2_line_94 | NAYY 4x150 SE | 91 | 92 | 0.034367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1005-1_2_2_line_95 | NAYY 4x150 SE | 92 | 93 | 0.024321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1005-1_2_2_line_96 | NAYY 4x150 SE | 93 | 94 | 0.0056438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1005-1_2_2_line_97 | NAYY 4x150 SE | 94 | 95 | 0.05145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1005-1_2_2_line_98 | NAYY 4x150 SE | 95 | 96 | 0.15504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1005-1_2_2_line_99 | NAYY 4x150 SE | 96 | 97 | 0.033467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1005-1_2_2_line_100 | NAYY 4x150 SE | 96 | 98 | 0.14132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1005-1_2_2_line_101 | NAYY 4x150 SE | 97 | 100 | 0.18607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1005-1_2_2_line_102 | NAYY 4x150 SE | 98 | 99 | 0.022908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1005-1_2_2_trafo_304 | 0.25 MVA 20/0.4 kV | 104 | 63 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33
0 | 2646320.2188 | 1201133.2756 | 2646315.717 | 1201128.622 | 2646313.3495 | 1201121.7887 | 2646311.0967 | 1201108.9862 | 2646309.0628 | 1201105.2684 | 2646293.5174 | 1201087.8937 | 2646289.0036 | 1201081.0721
1 | 2646329.103 | 1201136.8526 | 2646323.6382 | 1201136.8103 | 2646320.2188 | 1201133.2756
2 | 2646290.8851 | 1201069.0404 | 2646288.1166 | 1201076.6233 | 2646288.7925 | 1201080.7531 | 2646289.0036 | 1201081.0721
3 | 2646329.103 | 1201136.8526 | 2646339.3279 | 1201126.3565
4 | 2646544.017 | 1200886.66 | 2646290.8851 | 1201069.0404
5 | 2646340.3895 | 1201125.2668 | 2646339.3279 | 1201126.3565
6 | 2646585.4155 | 1200928.9368 | 2646547.2111 | 1200889.8949 | 2646544.017 | 1200886.66
7 | 2646964.5033 | 1202278.8818 | 2646960.9492 | 1202279.8656 | 2646956.3526 | 1202280.8411 | 2646950.5585 | 1202281.1958 | 2646942.3826 | 1202280.5535 | 2646862.9307 | 1202262.3532 | 2646831.2099 | 1202254.7892 | 2646819.4725 | 1202253.163 | 2646804.8956 | 1202253.5936 | 2646777.9244 | 1202258.4949
8 | 2646777.9244 | 1202258.4949 | 2646701.9142 | 1202163.0811
9 | 2646964.5033 | 1202278.8818 | 2646962.2556 | 1202272.4494 | 2646949.0796 | 1202234.0573 | 2646916.6661 | 1202134.4238
10 | 2646970.2392 | 1202295.6142 | 2646967.5447 | 1202287.9331 | 2646964.5033 | 1202278.8818
11 | 2646701.9142 | 1202163.0811 | 2646704.3731 | 1202162.9781 | 2646707.2247 | 1202161.3216 | 2646708.5258 | 1202159.4085 | 2646704.3195 | 1202136.7293 | 2646702.6841 | 1202130.791 | 2646700.2498 | 1202128.7152 | 2646697.2879 | 1202127.925 | 2646692.3595 | 1202130.4546 | 2646687.1558 | 1202136.0727 | 2646684.1574 | 1202140.7651
12 | 2646916.6661 | 1202134.4238 | 2646909.9633 | 1202136.1167 | 2646903.2808 | 1202136.1976 | 2646875.8197 | 1202133.6697 | 2646872.5907 | 1202133.9445 | 2646867.1384 | 1202136.3143 | 2646861.1722 | 1202139.1803 | 2646859.4339 | 1202139.7056
13 | 2646916.6661 | 1202134.4238 | 2646868.6578 | 1201978.4918 | 2646845.9696 | 1201901.937 | 2646834.5024 | 1201866.3124
14 | 2646916.6661 | 1202134.4238 | 2646919.9286 | 1202133.7491 | 2646921.5114 | 1202131.8382 | 2646942.3313 | 1202094.2686
15 | 2646970.2392 | 1202295.6142 | 2647055.0506 | 1202274.8137 | 2647068.6482 | 1202270.207 | 2647078.5878 | 1202265.2824 | 2647088.8856 | 1202258.3707 | 2647101.3927 | 1202248.2634 | 2647118.1589 | 1202232.7089 | 2647125.1929 | 1202228.573 | 2647129.2091 | 1202226.9537
16 | 2646854.7186 | 1202141.1308 | 2646859.4339 | 1202139.7056
17 | 2646833.5025 | 1201863.2061 | 2646834.5024 | 1201866.3124
18 | 2647014.6654 | 1201981.4731 | 2646989.7243 | 1202008.7481 | 2646942.3313 | 1202094.2686
19 | 2647182.7814 | 1202225.4366 | 2647161.5867 | 1202224.5021 | 2647141.7709 | 1202224.3458 | 2647132.2243 | 1202225.738 | 2647129.2091 | 1202226.9537
20 | 2646262.5874 | 1201865.8033 | 2646259.907 | 1201862.3849 | 2646259.907 | 1201862.3849
21 | 2646262.5874 | 1201865.8033 | 2646262.9091 | 1201866.2135
22 | 2646259.907 | 1201862.3849 | 2646230.2169 | 1201809.3585 | 2646208.4555 | 1201783.0864 | 2646205.8286 | 1201776.3512 | 2646205.8286 | 1201776.3512
23 | 2646394.2234 | 1201976.6684 | 2646354.2288 | 1201962.1166 | 2646333.5638 | 1201949.6605 | 2646309.3746 | 1201925.4704 | 2646262.9091 | 1201866.2135
24 | 2646198.2404 | 1201768.7576 | 2646205.8286 | 1201776.3512
25 | 2646384.1571 | 1201842.0248 | 2646387.3333 | 1201923.0734 | 2646392.08 | 1201971.4155 | 2646394.2234 | 1201976.6684
26 | 2646171.3776 | 1201741.7973 | 2646188.6091 | 1201759.1195 | 2646198.2404 | 1201768.7576
27 | 2646384.1571 | 1201842.0248 | 2646415.714 | 1201843.615 | 2646432.1181 | 1201841.2633 | 2646432.1181 | 1201841.2633
28 | 2646384.1571 | 1201842.0248 | 2646384.7626 | 1201827.7547 | 2646386.9728 | 1201818.5333 | 2646387.5757 | 1201817.2001
29 | 2646432.1181 | 1201841.2633 | 2646442.7366 | 1201841.0567 | 2646455.6758 | 1201844.8483 | 2646513.5518 | 1201871.8085
30 | 2646387.5757 | 1201817.2001 | 2646394.368 | 1201802.1813 | 2646396.7796 | 1201794.4623 | 2646396.7719 | 1201793.8365
31 | 2646322.4254 | 1201615.3729 | 2646340.1585 | 1201681.2033 | 2646345.4725 | 1201694.741 | 2646372.5383 | 1201735.752 | 2646387.9826 | 1201761.9756 | 2646394.8281 | 1201780.1613 | 2646396.6956 | 1201787.6356 | 2646396.7719 | 1201793.8365
32 | 2646322.4254 | 1201615.3729 | 2646305.8645 | 1201619.2246 | 2646301.2949 | 1201619.6116 | 2646285.7673 | 1201618.7798
33 | 2646322.4254 | 1201615.3729 | 2646323.8001 | 1201600.111
34 | 2646325.0903 | 1201585.7878 | 2646323.8001 | 1201600.111
35 | 2646579.7343 | 1201730.5305 | 2646513.5518 | 1201871.8085
36 | 2646715.979 | 1201820.2734 | 2646705.6527 | 1201813.2777 | 2646677.3755 | 1201792.256 | 2646663.735 | 1201782.7664 | 2646617.6555 | 1201758.86 | 2646579.7343 | 1201730.5305
37 | 2646569.7579 | 1201723.0775 | 2646579.7343 | 1201730.5305
38 | 2646701.1725 | 1201857.7458 | 2646703.6841 | 1201855.7865 | 2646705.7746 | 1201852.2119 | 2646709.3003 | 1201843.3218
39 | 2646681.9397 | 1201866.5895 | 2646685.5269 | 1201869.1857 | 2646686.9887 | 1201869.1082 | 2646692.2931 | 1201861.3563 | 2646695.0633 | 1201859.4101 | 2646698.678 | 1201858.4934 | 2646701.1725 | 1201857.7458
40 | 2646718.0025 | 1201821.3788 | 2646709.3003 | 1201843.3218
41 | 2646715.979 | 1201820.2734 | 2646718.0025 | 1201821.3788
42 | 2646833.5025 | 1201863.2061 | 2646826.2967 | 1201863.0163 | 2646808.6208 | 1201856.7076 | 2646752.0064 | 1201837.0535 | 2646723.7998 | 1201824.5592 | 2646718.0025 | 1201821.3788
43 | 2646715.979 | 1201820.2734 | 2646725.0746 | 1201798.0473
44 | 2646833.5025 | 1201863.2061 | 2646815.0586 | 1201800.4704 | 2646801.3716 | 1201759.7892
45 | 2646782.8337 | 1201694.8865 | 2646797.3545 | 1201746.565
46 | 2646765.993 | 1201637.9161 | 2646782.4688 | 1201693.5878 | 2646782.8337 | 1201694.8865
47 | 2646797.3545 | 1201746.565 | 2646799.5437 | 1201754.356 | 2646801.3716 | 1201759.7892
48 | 2646765.993 | 1201637.9161 | 2646783.0047 | 1201629.9891 | 2646792.2871 | 1201622.602 | 2646804.3793 | 1201606.2985 | 2646809.4069 | 1201600.8792 | 2646816.16 | 1201597.6969 | 2646824.4006 | 1201596.0271 | 2646834.3628 | 1201596.1052 | 2646844.8155 | 1201598.6663 | 2646857.3789 | 1201603.261
49 | 2646746.0179 | 1201572.2559 | 2646758.0775 | 1201611.6726 | 2646765.993 | 1201637.9161
50 | 2646746.0179 | 1201572.2559 | 2646739.1848 | 1201548.6891 | 2646737.4973 | 1201541.6052 | 2646736.7232 | 1201536.4517 | 2646736.4726 | 1201531.5136 | 2646736.9678 | 1201526.5814 | 2646738.2783 | 1201521.5443 | 2646740.8623 | 1201516.1837 | 2646744.5953 | 1201511.8326 | 2646749.7851 | 1201508.071 | 2646755.6966 | 1201505.4602 | 2646762.3936 | 1201503.6115 | 2646771.1362 | 1201502.0012 | 2646779.5246 | 1201500.9106 | 2646787.5437 | 1201500.3286 | 2646795.3822 | 1201500.4567 | 2646803.3383 | 1201501.1082 | 2646811.1422 | 1201502.7369 | 2646819.1384 | 1201505.0786 | 2646829.2712 | 1201508.6711 | 2646837.6731 | 1201512.6503 | 2646849.0912 | 1201519.2768 | 2646866.7406 | 1201529.0763 | 2646875.7054 | 1201533.1044 | 2646880.1409 | 1201534.2954 | 2646884.5951 | 1201535.053 | 2646887.7317 | 1201534.9442 | 2646890.2693 | 1201534.5527 | 2646892.9328 | 1201533.6287 | 2646903.1085 | 1201533.6752 | 2646911.6073 | 1201533.0637 | 2646924.0867 | 1201530.5157 | 2646930.7292 | 1201529.8008 | 2646935.8625 | 1201529.363
51 | 2646746.0179 | 1201572.2559 | 2646723.6095 | 1201567.567 | 2646663.2256 | 1201549.7409 | 2646652.4363 | 1201546.3992 | 2646646.1391 | 1201541.8808 | 2646644.0471 | 1201539.4057
52 | 2646935.8625 | 1201529.363 | 2646941.9366 | 1201529.3107 | 2646948.593 | 1201529.7299 | 2646956.2655 | 1201530.6351 | 2646962.427 | 1201532.0509 | 2646968.9668 | 1201533.7588 | 2646989.4423 | 1201540.3234 | 2647004.2099 | 1201542.9632 | 2647008.868 | 1201542.9554
53 | 2646935.8625 | 1201529.363 | 2646932.7574 | 1201540.9675 | 2646931.4644 | 1201546.6717 | 2646931.1567 | 1201553.8734 | 2646933.8243 | 1201563.0885 | 2646947.0922 | 1201588.0402 | 2646951.0021 | 1201598.0099 | 2646952.6981 | 1201603.9821 | 2646952.6356 | 1201611.9417 | 2646949.5607 | 1201622.6014 | 2646923.706 | 1201684.4589
54 | 2646644.0471 | 1201539.4057 | 2646640.1865 | 1201534.8382
55 | 2646922.4398 | 1201687.4882 | 2646923.706 | 1201684.4589
56 | 2646918.8209 | 1201696.1465 | 2646922.4398 | 1201687.4882
57 | 2647008.868 | 1201542.9554 | 2647016.9586 | 1201542.9523 | 2647031.1851 | 1201541.8191 | 2647051.5498 | 1201537.3101 | 2647069.7415 | 1201529.4377 | 2647084.6314 | 1201520.4164 | 2647094.3883 | 1201511.7994 | 2647096.2231 | 1201509.3597
58 | 2647008.868 | 1201542.9554 | 2647015.7599 | 1201549.2354 | 2647041.1416 | 1201565.0975
59 | 2647210.8356 | 1201385.9794 | 2647191.5633 | 1201397.6116 | 2647177.7218 | 1201406.8188 | 2647164.6957 | 1201419.7567 | 2647154.3077 | 1201432.1263 | 2647096.2231 | 1201509.3597
60 | 2647056.9994 | 1201575.0078 | 2647041.1416 | 1201565.0975
61 | 2646748.0591 | 1201205.2297 | 2646758.6996 | 1201230.5829 | 2646762.7204 | 1201241.0314 | 2646764.9332 | 1201249.0866 | 2646766.3172 | 1201257.0353 | 2646767.1799 | 1201264.4796 | 2646766.9604 | 1201275.9955 | 2646766.5831 | 1201283.3634
62 | 2646766.5831 | 1201283.3634 | 2646740.6957 | 1201271.1438
63 | 2646748.0591 | 1201205.2297 | 2646732.709 | 1201170.8568 | 2646707.2261 | 1201117.2162 | 2646675.7597 | 1201033.3784 | 2646671.6722 | 1201025.5754 | 2646665.7443 | 1201017.569 | 2646640.7463 | 1200994.283 | 2646646.1649 | 1200989.5337 | 2646650.0875 | 1200987.2519 | 2646657.9934 | 1200984.6899 | 2646667.4447 | 1200983.0627 | 2646671.276 | 1200981.7585 | 2646673.39 | 1200980.074 | 2646674.1662 | 1200979.1351
64 | 2646748.0591 | 1201205.2297 | 2646802.9107 | 1201221.379 | 2646846.1683 | 1201232.8465 | 2646856.9849 | 1201234.7101 | 2646865.7021 | 1201235.4233 | 2646952.2117 | 1201231.9437
65 | 2646727.953 | 1201265.1288 | 2646740.6957 | 1201271.1438
66 | 2647210.8356 | 1201385.9794 | 2647223.3754 | 1201375.8504 | 2647226.4489 | 1201371.2165 | 2647228.9469 | 1201364.2878 | 2647229.5512 | 1201357.1663 | 2647228.7737 | 1201351.5347 | 2647225.1407 | 1201345.0913
67 | 2647225.1407 | 1201345.0913 | 2647218.9092 | 1201340.9619 | 2647192.1113 | 1201331.1003 | 2647143.6466 | 1201319.9117 | 2647129.197 | 1201313.5608 | 2647123.7753 | 1201310.0049 | 2647119.0948 | 1201306.0769 | 2647115.3246 | 1201301.578 | 2647114.3351 | 1201300.1512
68 | 2647114.6298 | 1201258.4035 | 2647110.4783 | 1201272.3343 | 2647109.3298 | 1201278.9846 | 2647109.2534 | 1201285.7879 | 2647110.5901 | 1201291.9463 | 2647112.4949 | 1201297.4978 | 2647114.3351 | 1201300.1512
69 | 2646952.2117 | 1201231.9437 | 2646956.3607 | 1201231.7768 | 2646973.333 | 1201229.6833
70 | 2647047.2482 | 1201215.5153 | 2647019.7566 | 1201221.1689 | 2646995.2392 | 1201226.1012 | 2646975.9336 | 1201229.3625 | 2646973.333 | 1201229.6833
71 | 2647047.2482 | 1201215.5153 | 2647073.1465 | 1201210.1938
72 | 2646641.7492 | 1200920.3822 | 2646641.7926 | 1200928.476 | 2646642.4496 | 1200932.0832 | 2646643.6439 | 1200935.1053 | 2646644.8521 | 1200937.316 | 2646647.7812 | 1200941.4078 | 2646657.5194 | 1200952.768 | 2646667.1211 | 1200962.1149 | 2646671.3225 | 1200968.0066 | 2646673.263 | 1200971.9684 | 2646674.0755 | 1200975.1433 | 2646674.3751 | 1200977.7248 | 2646674.1662 | 1200979.1351
73 | 2646607.4611 | 1200937.5135 | 2646610.5261 | 1200940.7725 | 2646627.959 | 1200954.2161 | 2646643.536 | 1200965.5106 | 2646651.1202 | 1200970.0279 | 2646660.1255 | 1200973.8559 | 2646674.1662 | 1200979.1351
74 | 2646674.1662 | 1200979.1351 | 2646684.9577 | 1200983.2884 | 2646690.7943 | 1200986.7044
75 | 2647033.6746 | 1201163.5789 | 2647046.0999 | 1201169.9359 | 2647051.8684 | 1201172.0046 | 2647061.5147 | 1201174.6042 | 2647078.0225 | 1201178.6809 | 2647083.3537 | 1201181.1799 | 2647086.3881 | 1201183.4495 | 2647088.5531 | 1201185.9235 | 2647090.0647 | 1201189.2151 | 2647090.8243 | 1201193.2789 | 2647090.6158 | 1201197.5242 | 2647089.3266 | 1201200.7825 | 2647086.7436 | 1201204.0196 | 2647083.1452 | 1201206.6817 | 2647078.5769 | 1201208.7913 | 2647073.1465 | 1201210.1938
76 | 2647073.1465 | 1201210.1938 | 2647071.1202 | 1201229.7223 | 2647071.7931 | 1201234.1635 | 2647073.0168 | 1201237.286 | 2647075.2899 | 1201239.5719 | 2647078.0179 | 1201241.1053 | 2647080.2976 | 1201241.5791 | 2647083.0285 | 1201241.7896 | 2647086.1006 | 1201241.1912 | 2647088.9492 | 1201239.9908 | 2647090.7595 | 1201239.2547
77 | 2646585.4155 | 1200928.9368 | 2646589.8894 | 1200929.1718 | 2646593.0816 | 1200929.797 | 2646596.2689 | 1200931.0337 | 2646607.4611 | 1200937.5135
78 | 2646607.4611 | 1200937.5135 | 2646623.6473 | 1200945.8666 | 2646630.2195 | 1200950.034
79 | 2646641.7492 | 1200920.3822 | 2646648.9156 | 1200919.9267 | 2646652.9058 | 1200920.7027 | 2646656.6904 | 1200922.4554 | 2646688.189 | 1200940.8895 | 2646692.3484 | 1200943.0458
80 | 2646641.7492 | 1200920.3822 | 2646642.5003 | 1200910.9493
81 | 2646795.2574 | 1201073.5808 | 2646792.624 | 1201071.1465 | 2646777.7684 | 1201055.2657 | 2646764.9432 | 1201043.5253 | 2646753.5078 | 1201032.1739 | 2646730.8889 | 1201016.188 | 2646702.885 | 1200995.7577 | 2646692.9668 | 1200987.9758 | 2646690.7943 | 1200986.7044
82 | 2647033.6746 | 1201163.5789 | 2647029.362 | 1201160.2765 | 2647025.561 | 1201156.7557
83 | 2647114.6298 | 1201258.4035 | 2647108.6678 | 1201251.9306 | 2647103.2143 | 1201245.6397 | 2647099.5422 | 1201242.1977 | 2647096.8625 | 1201240.3199 | 2647094.2613 | 1201239.1099 | 2647092.5432 | 1201238.8406 | 2647091.0414 | 1201239.1401 | 2647090.7595 | 1201239.2547
84 | 2647166.3478 | 1201127.4811 | 2647161.1139 | 1201128.0735 | 2647155.4663 | 1201128.0401 | 2647144.7443 | 1201126.7215 | 2647091.0265 | 1201118.349 | 2647071.0993 | 1201113.5005 | 2647061.9685 | 1201110.2045 | 2647051.4911 | 1201105.8529 | 2647045.6093 | 1201103.661 | 2647040.8753 | 1201102.6342 | 2647036.2407 | 1201102.5199 | 2647031.597 | 1201103.5618 | 2647027.4038 | 1201105.3854 | 2647024.1023 | 1201108.0387 | 2647020.9571 | 1201112.1163 | 2647018.5863 | 1201116.4446 | 2647016.8641 | 1201121.5228 | 2647015.793 | 1201126.0948 | 2647015.4343 | 1201132.0176 | 2647015.8307 | 1201138.7134 | 2647016.9125 | 1201143.4357 | 2647018.9492 | 1201147.7097 | 2647022.2651 | 1201152.9054 | 2647025.561 | 1201156.7557
85 | 2647166.3478 | 1201127.4811 | 2647580.5146 | 1200971.6286
86 | 2647580.5146 | 1200971.6286 | 2647581.4004 | 1200968.1118
87 | 2646669.4344 | 1200668.7664 | 2646670.2347 | 1200673.5087 | 2646673.0554 | 1200679.8009 | 2646683.8618 | 1200694.7938 | 2646689.0462 | 1200703.4947 | 2646691.7594 | 1200711.854 | 2646694.2878 | 1200724.3697 | 2646694.8283 | 1200734.1017 | 2646695.0065 | 1200755.1484 | 2646693.0731 | 1200768.7743 | 2646688.0891 | 1200781.198 | 2646678.3308 | 1200798.6985 | 2646674.3607 | 1200810.93 | 2646669.071 | 1200834.2464 | 2646666.5302 | 1200840.8637 | 2646658.0176 | 1200854.8274 | 2646653.0823 | 1200865.9063 | 2646642.5003 | 1200910.9493 | 2646642.5003 | 1200910.9493
88 | 2646791.9037 | 1200992.9964 | 2646775.6635 | 1200981.8741 | 2646728.8618 | 1200961.9747 | 2646692.3484 | 1200943.0458
89 | 2647269.9193 | 1202329.2397 | 2647271.3663 | 1202335.8438 | 2647271.5216 | 1202340.2586
90 | 2647182.7814 | 1202225.4366 | 2647184.6062 | 1202233.3555 | 2647186.9108 | 1202238.3432 | 2647189.8804 | 1202242.9581 | 2647193.8448 | 1202246.8806 | 2647198.3884 | 1202250.6964 | 2647214.9947 | 1202260.2218 | 2647218.1194 | 1202262.5367 | 2647223.1972 | 1202267.1239 | 2647232.7862 | 1202277.6834 | 2647252.2251 | 1202299.505 | 2647259.9142 | 1202309.7272 | 2647265.6836 | 1202320.1899 | 2647269.9193 | 1202329.2397 | 2647269.9193 | 1202329.2397
91 | 2647270.1123 | 1202346.2176 | 2647271.5216 | 1202340.2586
92 | 2646924.169 | 1201884.4847 | 2646926.4036 | 1201893.5852 | 2646927.2835 | 1201895.8091
93 | 2647014.6654 | 1201981.4731 | 2647007.0717 | 1201973.5311 | 2646991.8395 | 1201960.4261 | 2646980.2643 | 1201950.6851 | 2646971.0914 | 1201944.176 | 2646955.4824 | 1201935.4262 | 2646949.7455 | 1201931.3566 | 2646944.0298 | 1201925.564 | 2646938.541 | 1201918.9727 | 2646932.0602 | 1201907.8822 | 2646927.2835 | 1201895.8091
94 | 2647014.6654 | 1201981.4731 | 2647027.2472 | 1201965.7964 | 2647037.9162 | 1201956.2638
95 | 2647037.9162 | 1201956.2638 | 2647041.195 | 1201954.4997 | 2647045.2936 | 1201953.0089 | 2647050.2971 | 1201951.6252 | 2647055.7439 | 1201950.9566 | 2647061.2977 | 1201950.7683
96 | 2647066.9366 | 1201950.9104 | 2647062.6637 | 1201950.722 | 2647061.2977 | 1201950.7683
97 | 2647118.3045 | 1201951.7164 | 2647107.3386 | 1201952.5638 | 2647096.379 | 1201952.5997 | 2647077.096 | 1201951.3582 | 2647066.9366 | 1201950.9104
98 | 2647256.391 | 1201911.2831 | 2647258.0203 | 1201912.1631 | 2647258.8152 | 1201913.6591 | 2647258.6481 | 1201916.5039 | 2647257.9341 | 1201919.2109 | 2647256.7236 | 1201922.1586 | 2647254.9849 | 1201924.5128 | 2647253.1067 | 1201926.2434 | 2647249.5056 | 1201928.3273 | 2647243.1179 | 1201930.5558 | 2647229.1738 | 1201933.6252 | 2647171.2439 | 1201942.0505 | 2647141.6298 | 1201947.9981 | 2647127.8433 | 1201950.4019 | 2647118.3045 | 1201951.7164
99 | 2647256.391 | 1201911.2831 | 2647257.6775 | 1201907.391 | 2647257.0708 | 1201902.3055 | 2647255.4606 | 1201896.1226 | 2647249.3449 | 1201879.3425
100 | 2647256.391 | 1201911.2831 | 2647245.9758 | 1201909.8444 | 2647226.0934 | 1201906.4187 | 2647197.4002 | 1201897.8873 | 2647186.5758 | 1201892.3653 | 2647144.7639 | 1201864.2528 | 2647142.6652 | 1201862.0906 | 2647141.5456 | 1201859.3024 | 2647141.3906 | 1201856.7553 | 2647141.6002 | 1201854.3111 | 2647144.2084 | 1201847.663
101 | 2647249.3449 | 1201879.3425 | 2647253.4385 | 1201876.5844 | 2647256.0069 | 1201876.1266 | 2647258.7441 | 1201876.4596 | 2647274.571 | 1201881.6877 | 2647299.4026 | 1201891.5564 | 2647307.5843 | 1201893.4555 | 2647320.6126 | 1201894.5592 | 2647328.1219 | 1201896.7866 | 2647339.6154 | 1201902.3697 | 2647362.7515 | 1201914.8934 | 2647381.9176 | 1201923.2055 | 2647410.0792 | 1201934.4351 | 2647422.0747 | 1201940.0335
102 | 2647152.5748 | 1201826.3372 | 2647144.2084 | 1201847.663

## bus_geodata
| x | y | coords
0 | 2646320.2188 | 1201133.2756
1 | 2646289.0036 | 1201081.0721
2 | 2646329.103 | 1201136.8526
3 | 2646290.8851 | 1201069.0404
4 | 2646339.3279 | 1201126.3565
5 | 2646544.017 | 1200886.66
6 | 2646340.3895 | 1201125.2668
7 | 2646777.9244 | 1202258.4949
8 | 2646964.5033 | 1202278.8818
9 | 2646701.9142 | 1202163.0811
10 | 2646684.1574 | 1202140.7651
11 | 2646916.6661 | 1202134.4238
12 | 2646970.2392 | 1202295.6142
13 | 2646859.4339 | 1202139.7056
14 | 2646834.5024 | 1201866.3124
15 | 2646942.3313 | 1202094.2686
16 | 2647129.2091 | 1202226.9537
17 | 2646262.5874 | 1201865.8033
18 | 2646259.907 | 1201862.3849
19 | 2646262.9091 | 1201866.2135
20 | 2646205.8286 | 1201776.3512
21 | 2646394.2234 | 1201976.6684
22 | 2646198.2404 | 1201768.7576
23 | 2646384.1571 | 1201842.0248
24 | 2646171.3776 | 1201741.7973
25 | 2646432.1181 | 1201841.2633
26 | 2646387.5757 | 1201817.2001
27 | 2646396.7719 | 1201793.8365
28 | 2646322.4254 | 1201615.3729
29 | 2646285.7673 | 1201618.7798
30 | 2646323.8001 | 1201600.111
31 | 2646513.5518 | 1201871.8085
32 | 2646325.0903 | 1201585.7878
33 | 2646579.7343 | 1201730.5305
34 | 2646701.1725 | 1201857.7458
35 | 2646709.3003 | 1201843.3218
36 | 2646681.9397 | 1201866.5895
37 | 2646718.0025 | 1201821.3788
38 | 2646715.979 | 1201820.2734
39 | 2646833.5025 | 1201863.2061
40 | 2646569.7579 | 1201723.0775
41 | 2646725.0746 | 1201798.0473
42 | 2646782.8337 | 1201694.8865
43 | 2646797.3545 | 1201746.565
44 | 2646765.993 | 1201637.9161
45 | 2646801.3716 | 1201759.7892
46 | 2646857.3789 | 1201603.261
47 | 2646746.0179 | 1201572.2559
48 | 2646935.8625 | 1201529.363
49 | 2646644.0471 | 1201539.4057
50 | 2646922.4398 | 1201687.4882
51 | 2646923.706 | 1201684.4589
52 | 2646918.8209 | 1201696.1465
53 | 2647008.868 | 1201542.9554
54 | 2647096.2231 | 1201509.3597
55 | 2647041.1416 | 1201565.0975
56 | 2646766.5831 | 1201283.3634
57 | 2646748.0591 | 1201205.2297
58 | 2646740.6957 | 1201271.1438
59 | 2647056.9994 | 1201575.0078
60 | 2647210.8356 | 1201385.9794
61 | 2647225.1407 | 1201345.0913
62 | 2647114.3351 | 1201300.1512
63 | 2646952.2117 | 1201231.9437
64 | 2646973.333 | 1201229.6833
65 | 2647047.2482 | 1201215.5153
66 | 2646674.1662 | 1200979.1351
67 | 2647073.1465 | 1201210.1938
68 | 2646585.4155 | 1200928.9368
69 | 2646607.4611 | 1200937.5135
70 | 2646641.7492 | 1200920.3822
71 | 2646690.7943 | 1200986.7044
72 | 2647033.6746 | 1201163.5789
73 | 2647090.7595 | 1201239.2547
74 | 2646795.2574 | 1201073.5808
75 | 2647025.561 | 1201156.7557
76 | 2647166.3478 | 1201127.4811
77 | 2647580.5146 | 1200971.6286
78 | 2647114.6298 | 1201258.4035
79 | 2646727.953 | 1201265.1288
80 | 2646669.4344 | 1200668.7664
81 | 2646642.5003 | 1200910.9493
82 | 2646692.3484 | 1200943.0458
83 | 2646630.2195 | 1200950.034
84 | 2646791.9037 | 1200992.9964
85 | 2647269.9193 | 1202329.2397
86 | 2647271.5216 | 1202340.2586
87 | 2647182.7814 | 1202225.4366
88 | 2647270.1123 | 1202346.2176
89 | 2646927.2835 | 1201895.8091
90 | 2646924.169 | 1201884.4847
91 | 2647014.6654 | 1201981.4731
92 | 2647037.9162 | 1201956.2638
93 | 2647061.2977 | 1201950.7683
94 | 2647066.9366 | 1201950.9104
95 | 2647118.3045 | 1201951.7164
96 | 2647256.391 | 1201911.2831
97 | 2647249.3449 | 1201879.3425
98 | 2647144.2084 | 1201847.663
99 | 2647152.5748 | 1201826.3372
100 | 2647422.0747 | 1201940.0335
101 | 2647581.4004 | 1200968.1118
102 | 2646640.1865 | 1201534.8382
103 | 2646854.7186 | 1202141.1308
104 | 2646952.2117 | 1201231.9437

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9934 | -0.0472 | 0.00031532 | 7.9026e-05
1 | 0.99363 | -0.045534 | 0.00015555 | 3.8984e-05
2 | 0.99336 | -0.047443 | 0 | 0
3 | 0.99369 | -0.045176 | 0 | 0
4 | 0.99332 | -0.047787 | 0.0016093 | 0.00040332
5 | 0.99493 | -0.036314 | 0.00020913 | 5.2413e-05
6 | 0.99331 | -0.047798 | 0.00070874 | 0.00017763
7 | 0.97443 | -0.18628 | 0.00017799 | 4.4609e-05
8 | 0.97455 | -0.18541 | 0 | 0
9 | 0.97439 | -0.18659 | 0.00015936 | 3.9938e-05
10 | 0.97439 | -0.18664 | 7.2078e-05 | 1.8065e-05
11 | 0.97479 | -0.18356 | 0 | 0
12 | 0.97453 | -0.18554 | 0 | 0
13 | 0.97474 | -0.18393 | 0.00040139 | 0.0001006
14 | 0.97598 | -0.17443 | 8.9721e-05 | 2.2486e-05
15 | 0.9747 | -0.18423 | 5.1402e-05 | 1.2883e-05
16 | 0.97436 | -0.18683 | 4.9903e-05 | 1.2507e-05
17 | 0.9712 | -0.20942 | 0.00023017 | 5.7686e-05
18 | 0.9712 | -0.20946 | 9.5076e-05 | 2.3828e-05
19 | 0.9712 | -0.20941 | 0.00018311 | 4.5892e-05
20 | 0.97107 | -0.21036 | 0.00010572 | 2.6495e-05
21 | 0.97155 | -0.20689 | 0 | 0
22 | 0.97106 | -0.21044 | 0.00053535 | 0.00013417
23 | 0.97181 | -0.20494 | 0 | 0
24 | 0.97105 | -0.21052 | 0.0001806 | 4.5263e-05
25 | 0.97212 | -0.20266 | 7.6086e-05 | 1.9069e-05
26 | 0.9717 | -0.20576 | 0.00027515 | 6.8959e-05
27 | 0.97159 | -0.20651 | 0.00010693 | 2.68e-05
28 | 0.97082 | -0.21209 | 0 | 0
29 | 0.97081 | -0.21216 | 0.00017594 | 4.4094e-05
30 | 0.97077 | -0.2125 | 0.00069764 | 0.00017485
31 | 0.9727 | -0.19844 | 7.7654e-05 | 1.9462e-05
32 | 0.97073 | -0.21277 | 0.0018068 | 0.00045282
33 | 0.97374 | -0.19082 | 0.00011377 | 2.8514e-05
34 | 0.97494 | -0.18202 | 0.00013329 | 3.3407e-05
35 | 0.97495 | -0.18196 | 0.00013963 | 3.4994e-05
36 | 0.97493 | -0.18207 | 0.00021328 | 5.3454e-05
37 | 0.97496 | -0.18183 | 0 | 0
38 | 0.97495 | -0.18196 | 0 | 0
39 | 0.97599 | -0.17432 | 0 | 0
40 | 0.97373 | -0.19087 | 0.0003809 | 9.5463e-05
41 | 0.97494 | -0.182 | 0.0001671 | 4.1878e-05
42 | 0.97829 | -0.15723 | 0.00026914 | 6.7453e-05
43 | 0.97755 | -0.16274 | 0.00058952 | 0.00014775
44 | 0.97914 | -0.15098 | 0 | 0
45 | 0.97737 | -0.16407 | 0.00019054 | 4.7754e-05
46 | 0.9791 | -0.15122 | 0.00021402 | 5.3639e-05
47 | 0.98014 | -0.1436 | 0 | 0
48 | 0.98421 | -0.11367 | 0 | 0
49 | 0.98005 | -0.14422 | 0.00038968 | 9.7663e-05
50 | 0.98391 | -0.11582 | 0.00082873 | 0.0002077
51 | 0.98391 | -0.11579 | 0.0003243 | 8.1278e-05
52 | 0.9839 | -0.11582 | 7.5456e-05 | 1.8911e-05
53 | 0.98548 | -0.10434 | 0 | 0
54 | 0.98723 | -0.091574 | 7.4551e-05 | 1.8684e-05
55 | 0.98544 | -0.10463 | 0.00056152 | 0.00014073
56 | 0.99782 | -0.015579 | 0 | 0
57 | 0.99795 | -0.014665 | 0 | 0
58 | 0.99778 | -0.015898 | 0.00039686 | 9.9463e-05
59 | 0.98544 | -0.10466 | 0.00015574 | 3.9032e-05
60 | 0.99034 | -0.069006 | 0 | 0
61 | 0.99124 | -0.062501 | 0 | 0
62 | 0.99347 | -0.046457 | 0.00016732 | 4.1934e-05
63 | 1 | 0 | -0.032082 | -0.0078032
64 | 0.99926 | -0.0052013 | 0.00020355 | 5.1015e-05
65 | 0.99667 | -0.023528 | 0 | 0
66 | 0.99567 | -0.031076 | 0 | 0
67 | 0.99576 | -0.029968 | 0 | 0
68 | 0.99519 | -0.034501 | 0 | 0
69 | 0.99529 | -0.033764 | 0 | 0
70 | 0.99548 | -0.032429 | 0 | 0
71 | 0.99565 | -0.031183 | 0.00020461 | 5.128e-05
72 | 0.99431 | -0.040136 | 0 | 0
73 | 0.99486 | -0.036428 | 0.00043667 | 0.00010944
74 | 0.99558 | -0.031689 | 0.00036147 | 9.0593e-05
75 | 0.99415 | -0.041278 | 0.00068444 | 0.00017154
76 | 0.99127 | -0.061509 | 0 | 0
77 | 0.98493 | -0.10643 | 0.0049983 | 0.0012527
78 | 0.99427 | -0.040667 | 0 | 0
79 | 0.99776 | -0.015999 | 0.00071351 | 0.00017882
80 | 0.99536 | -0.033333 | 0.00030674 | 7.6876e-05
81 | 0.99547 | -0.032502 | 0.00043261 | 0.00010842
82 | 0.99539 | -0.033087 | 0.0003151 | 7.8972e-05
83 | 0.99528 | -0.033847 | 0.00031737 | 7.9541e-05
84 | 0.99526 | -0.03402 | 0.00082414 | 0.00020655
85 | 0.97418 | -0.1881 | 0.00011743 | 2.943e-05
86 | 0.97418 | -0.18816 | 0.0001699 | 4.258e-05
87 | 0.97431 | -0.18719 | 0 | 0
88 | 0.97417 | -0.18818 | 0.00033094 | 8.294e-05
89 | 0.97442 | -0.18635 | 0.00019522 | 4.8927e-05
90 | 0.97442 | -0.18636 | 5.0166e-05 | 1.2573e-05
91 | 0.97447 | -0.18602 | 0 | 0
92 | 0.97442 | -0.18638 | 0 | 0
93 | 0.97439 | -0.18664 | 0.00019811 | 4.9652e-05
94 | 0.97438 | -0.18668 | 5.3609e-05 | 1.3436e-05
95 | 0.97433 | -0.18708 | 0 | 0
96 | 0.97417 | -0.18827 | 0 | 0
97 | 0.97417 | -0.1883 | 0 | 0
98 | 0.97404 | -0.18923 | 0.00043235 | 0.00010836
99 | 0.97404 | -0.18928 | 0.00020312 | 5.0906e-05
100 | 0.97416 | -0.18841 | 5.081e-05 | 1.2734e-05
101 | 0.9849 | -0.10661 | 0.0049097 | 0.0012305
102 | 0.98005 | -0.14423 | 0.00015279 | 3.8293e-05
103 | 0.97473 | -0.18394 | 0.00019335 | 4.8459e-05
104 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0026335 | -0.0006597 | 0.0026341 | 0.00065913 | 6.0619e-07 | -5.754e-07 | 0.0039446 | 0.0039443 | 0.0039446 | 0.9934 | -0.0472 | 0.99363 | -0.045534 | 1.461
1 | 0.0023182 | 0.00058068 | -0.0023181 | -0.00058078 | 7.8117e-08 | -1.0437e-07 | 0.0034723 | 0.0034724 | 0.0034724 | 0.9934 | -0.0472 | 0.99336 | -0.047443 | 1.2861
2 | -0.0027897 | -0.00069811 | 0.0027898 | 0.000698 | 1.3763e-07 | -1.1079e-07 | 0.0041773 | 0.0041772 | 0.0041773 | 0.99363 | -0.045534 | 0.99369 | -0.045176 | 1.5471
3 | 0.0023181 | 0.00058078 | -0.002318 | -0.00058093 | 1.1025e-07 | -1.4728e-07 | 0.0034724 | 0.0034724 | 0.0034724 | 0.99336 | -0.047443 | 0.99332 | -0.047787 | 1.2861
4 | -0.0027898 | -0.000698 | 0.0027932 | 0.00069526 | 3.3959e-06 | -2.7405e-06 | 0.0041772 | 0.0041758 | 0.0041772 | 0.99369 | -0.045176 | 0.99493 | -0.036314 | 1.5471
5 | 0.00070874 | 0.00017761 | -0.00070874 | -0.00017763 | 1.0701e-09 | -1.9281e-08 | 0.0010617 | 0.0010617 | 0.0010617 | 0.99332 | -0.047787 | 0.99331 | -0.047798 | 0.39323
6 | -0.0030023 | -0.00074767 | 0.0030031 | 0.00074719 | 7.4385e-07 | -4.8253e-07 | 0.0044886 | 0.0044883 | 0.0044886 | 0.99493 | -0.036314 | 0.99519 | -0.034501 | 1.6624
7 | -0.00040944 | -0.00010032 | 0.00040948 | 9.7966e-05 | 4.6251e-08 | -2.3538e-06 | 0.00062441 | 0.00062359 | 0.00062441 | 0.97443 | -0.18628 | 0.97455 | -0.18541 | 0.23126
8 | 0.00023144 | 5.5711e-05 | -0.00023143 | -5.7227e-05 | 9.4791e-09 | -1.5159e-06 | 0.00035262 | 0.00035315 | 0.00035315 | 0.97443 | -0.18628 | 0.97439 | -0.18659 | 0.1308
9 | -0.0010779 | -0.00026048 | 0.0010781 | 0.00025868 | 2.5601e-07 | -1.7979e-06 | 0.0016424 | 0.0016417 | 0.0016424 | 0.97455 | -0.18541 | 0.97479 | -0.18356 | 0.60829
10 | 0.0006684 | 0.00016251 | -0.00066839 | -0.00016273 | 1.1456e-08 | -2.1596e-07 | 0.0010188 | 0.0010189 | 0.0010189 | 0.97455 | -0.18541 | 0.97453 | -0.18554 | 0.37736
11 | 7.2079e-05 | 1.7288e-05 | -7.2078e-05 | -1.8065e-05 | 4.7005e-10 | -7.7618e-07 | 0.0001098 | 0.00011007 | 0.00011007 | 0.97439 | -0.18659 | 0.97439 | -0.18664 | 0.040768
12 | 0.00059477 | 0.00014827 | -0.00059474 | -0.00014899 | 3.0232e-08 | -7.2126e-07 | 0.00090763 | 0.0009079 | 0.0009079 | 0.97479 | -0.18356 | 0.97474 | -0.18393 | 0.33626
13 | -0.0029084 | -0.00070455 | 0.0029118 | 0.00070237 | 3.4347e-06 | -2.179e-06 | 0.004431 | 0.0044298 | 0.004431 | 0.97479 | -0.18356 | 0.97598 | -0.17443 | 1.6411
14 | 0.0012355 | 0.00029759 | -0.0012354 | -0.00029816 | 1.0776e-07 | -5.6642e-07 | 0.0018817 | 0.0018819 | 0.0018819 | 0.97479 | -0.18356 | 0.9747 | -0.18423 | 0.69701
15 | 0.00066839 | 0.00016273 | -0.00066827 | -0.00016489 | 1.1449e-07 | -2.1561e-06 | 0.0010189 | 0.0010196 | 0.0010196 | 0.97453 | -0.18554 | 0.97436 | -0.18683 | 0.37765
16 | 0.00019335 | 4.8397e-05 | -0.00019335 | -4.8459e-05 | 2.6781e-10 | -6.1298e-08 | 0.00029515 | 0.00029517 | 0.00029517 | 0.97474 | -0.18393 | 0.97473 | -0.18394 | 0.10932
17 | -0.0030015 | -0.00072486 | 0.0030016 | 0.00072483 | 4.2463e-08 | -2.4447e-08 | 0.0045666 | 0.0045666 | 0.0045666 | 0.97598 | -0.17443 | 0.97599 | -0.17432 | 1.6913
18 | 0.001184 | 0.00028528 | -0.0011837 | -0.00028685 | 2.7353e-07 | -1.5737e-06 | 0.0018035 | 0.001804 | 0.001804 | 0.9747 | -0.18423 | 0.97447 | -0.18602 | 0.66816
19 | 0.00061837 | 0.00015238 | -0.00061834 | -0.00015304 | 2.9961e-08 | -6.6015e-07 | 0.00094343 | 0.00094367 | 0.00094367 | 0.97436 | -0.18683 | 0.97431 | -0.18719 | 0.34951
20 | 0.00091686 | 0.00022788 | -0.00091685 | -0.00022793 | 5.3438e-09 | -5.1698e-08 | 0.0014041 | 0.0014041 | 0.0014041 | 0.9712 | -0.20942 | 0.9712 | -0.20946 | 0.52003
21 | -0.001147 | -0.00028557 | 0.001147 | 0.00028556 | 1.0037e-09 | -6.0651e-09 | 0.0017567 | 0.0017567 | 0.0017567 | 0.9712 | -0.20942 | 0.9712 | -0.20941 | 0.65064
22 | 0.00082178 | 0.0002041 | -0.00082168 | -0.00020533 | 1.0095e-07 | -1.2246e-06 | 0.0012584 | 0.0012589 | 0.0012589 | 0.9712 | -0.20946 | 0.97107 | -0.21036 | 0.46625
23 | -0.0013301 | -0.00033145 | 0.0013306 | 0.00032945 | 4.5616e-07 | -2.0057e-06 | 0.0020373 | 0.0020365 | 0.0020373 | 0.9712 | -0.20941 | 0.97155 | -0.20689 | 0.75454
24 | 0.00071596 | 0.00017883 | -0.00071595 | -0.00017896 | 8.0598e-09 | -1.2971e-07 | 0.0010969 | 0.0010969 | 0.0010969 | 0.97107 | -0.21036 | 0.97106 | -0.21044 | 0.40627
25 | -0.0013306 | -0.00032945 | 0.0013309 | 0.00032791 | 3.5026e-07 | -1.5422e-06 | 0.0020365 | 0.0020359 | 0.0020365 | 0.97155 | -0.20689 | 0.97181 | -0.20494 | 0.75426
26 | 0.0001806 | 4.4793e-05 | -0.0001806 | -4.5263e-05 | 1.8178e-09 | -4.7012e-07 | 0.00027658 | 0.00027675 | 0.00027675 | 0.97106 | -0.21044 | 0.97105 | -0.21052 | 0.1025
27 | -0.0043963 | -0.0010927 | 0.0043977 | 0.0010926 | 1.3606e-06 | -7.3686e-08 | 0.0067282 | 0.006728 | 0.0067282 | 0.97181 | -0.20494 | 0.97212 | -0.20266 | 2.4919
28 | 0.0030654 | 0.00076477 | -0.003065 | -0.00076495 | 3.4663e-07 | -1.7923e-07 | 0.0046924 | 0.0046925 | 0.0046925 | 0.97181 | -0.20494 | 0.9717 | -0.20576 | 1.738
29 | -0.0044737 | -0.0011117 | 0.0044763 | 0.0011116 | 2.5709e-06 | -1.0226e-07 | 0.0068445 | 0.0068441 | 0.0068445 | 0.97212 | -0.20266 | 0.9727 | -0.19844 | 2.535
30 | 0.0027899 | 0.00069599 | -0.0027896 | -0.00069619 | 2.8682e-07 | -2.0176e-07 | 0.0042711 | 0.0042712 | 0.0042712 | 0.9717 | -0.20576 | 0.97159 | -0.20651 | 1.5819
31 | 0.0026826 | 0.00066939 | -0.0026806 | -0.00067102 | 2.0599e-06 | -1.6286e-06 | 0.0041075 | 0.0041083 | 0.0041083 | 0.97159 | -0.20651 | 0.97082 | -0.21209 | 1.5216
32 | 0.00017594 | 4.3636e-05 | -0.00017594 | -4.4094e-05 | 1.6794e-09 | -4.5727e-07 | 0.0002695 | 0.00026966 | 0.00026966 | 0.97082 | -0.21209 | 0.97081 | -0.21216 | 0.099876
33 | 0.0025046 | 0.00062738 | -0.0025045 | -0.00062752 | 1.4091e-07 | -1.3527e-07 | 0.0038388 | 0.0038389 | 0.0038389 | 0.97082 | -0.21209 | 0.97077 | -0.2125 | 1.4218
34 | 0.0018069 | 0.00045267 | -0.0018068 | -0.00045282 | 6.8834e-08 | -1.5132e-07 | 0.0027695 | 0.0027696 | 0.0027696 | 0.97077 | -0.2125 | 0.97073 | -0.21277 | 1.0258
35 | -0.004554 | -0.001131 | 0.0045587 | 0.0011309 | 4.7193e-06 | -1.2348e-07 | 0.0069629 | 0.0069622 | 0.0069629 | 0.9727 | -0.19844 | 0.97374 | -0.19082 | 2.5788
36 | -0.0050534 | -0.0012547 | 0.0050595 | 0.001255 | 6.0795e-06 | 3.0105e-07 | 0.0077181 | 0.0077174 | 0.0077181 | 0.97374 | -0.19082 | 0.97495 | -0.18196 | 2.8586
37 | 0.00038091 | 9.531e-05 | -0.0003809 | -9.5463e-05 | 2.6326e-09 | -1.5389e-07 | 0.00058203 | 0.00058208 | 0.00058208 | 0.97374 | -0.19082 | 0.97373 | -0.19087 | 0.21559
38 | -0.00034658 | -8.655e-05 | 0.00034658 | 8.634e-05 | 2.9474e-09 | -2.0949e-07 | 0.00052886 | 0.00052879 | 0.00052886 | 0.97494 | -0.18202 | 0.97495 | -0.18196 | 0.19588
39 | 0.00021329 | 5.3143e-05 | -0.00021328 | -5.3454e-05 | 1.6528e-09 | -3.1116e-07 | 0.00032542 | 0.00032553 | 0.00032553 | 0.97494 | -0.18202 | 0.97493 | -0.18207 | 0.12057
40 | -0.00048621 | -0.00012133 | 0.00048622 | 0.00012104 | 8.1063e-09 | -2.9125e-07 | 0.0007419 | 0.00074179 | 0.0007419 | 0.97495 | -0.18196 | 0.97496 | -0.18183 | 0.27478
41 | 0.0052266 | 0.0012966 | -0.0052265 | -0.0012966 | 9.1257e-08 | 6.4045e-09 | 0.0079723 | 0.0079723 | 0.0079723 | 0.97496 | -0.18183 | 0.97495 | -0.18196 | 2.9527
42 | -0.0057129 | -0.0014177 | 0.0057187 | 0.0014184 | 5.8303e-06 | 7.0627e-07 | 0.0087141 | 0.0087135 | 0.0087141 | 0.97496 | -0.18183 | 0.97599 | -0.17432 | 3.2274
43 | 0.0001671 | 4.1579e-05 | -0.0001671 | -4.1878e-05 | 9.7426e-10 | -2.991e-07 | 0.00025492 | 0.00025503 | 0.00025503 | 0.97495 | -0.18196 | 0.97494 | -0.182 | 0.094456
44 | -0.0087203 | -0.0021432 | 0.0087322 | 0.0021464 | 1.1919e-05 | 3.2288e-06 | 0.01328 | 0.01328 | 0.01328 | 0.97599 | -0.17432 | 0.97737 | -0.16407 | 4.9185
45 | 0.0095209 | 0.0023444 | -0.0095138 | -0.0023424 | 7.0104e-06 | 2.0228e-06 | 0.014467 | 0.014467 | 0.014467 | 0.97829 | -0.15723 | 0.97755 | -0.16274 | 5.3581
46 | -0.00979 | -0.0024118 | 0.0097982 | 0.0024142 | 8.2034e-06 | 2.4086e-06 | 0.014876 | 0.014876 | 0.014876 | 0.97829 | -0.15723 | 0.97914 | -0.15098 | 5.5097
47 | 0.0089243 | 0.0021946 | -0.0089227 | -0.0021942 | 1.5885e-06 | 4.3768e-07 | 0.01357 | 0.01357 | 0.01357 | 0.97755 | -0.16274 | 0.97737 | -0.16407 | 5.0258
48 | 0.00021403 | 5.228e-05 | -0.00021402 | -5.3639e-05 | 7.1389e-09 | -1.3593e-06 | 0.00032479 | 0.00032527 | 0.00032527 | 0.97914 | -0.15098 | 0.9791 | -0.15122 | 0.12047
49 | -0.010012 | -0.0024665 | 0.010022 | 0.0024695 | 9.8946e-06 | 2.9416e-06 | 0.015201 | 0.0152 | 0.015201 | 0.97914 | -0.15098 | 0.98014 | -0.1436 | 5.6299
50 | -0.010565 | -0.002604 | 0.010607 | 0.002617 | 4.2505e-05 | 1.299e-05 | 0.016023 | 0.016022 | 0.016023 | 0.98014 | -0.1436 | 0.98421 | -0.11367 | 5.9346
51 | 0.00054252 | 0.00013454 | -0.00054247 | -0.00013588 | 4.5746e-08 | -1.3452e-06 | 0.00082312 | 0.00082361 | 0.00082361 | 0.98014 | -0.1436 | 0.98005 | -0.14422 | 0.30504
52 | -0.011836 | -0.0029228 | 0.011851 | 0.0029275 | 1.4862e-05 | 4.7679e-06 | 0.017879 | 0.017879 | 0.017879 | 0.98421 | -0.11367 | 0.98548 | -0.10434 | 6.622
53 | 0.0012289 | 0.00030576 | -0.0012285 | -0.00030773 | 3.5726e-07 | -1.9707e-06 | 0.0018571 | 0.0018579 | 0.0018579 | 0.98421 | -0.11367 | 0.98391 | -0.11579 | 0.68809
54 | 0.00015279 | 3.8218e-05 | -0.00015279 | -3.8293e-05 | 2.0081e-10 | -7.5284e-08 | 0.00023196 | 0.00023198 | 0.00023198 | 0.98005 | -0.14422 | 0.98005 | -0.14423 | 0.08592
55 | -0.00090419 | -0.00022649 | 0.00090419 | 0.00022645 | 3.8307e-09 | -4.0226e-08 | 0.0013674 | 0.0013674 | 0.0013674 | 0.98391 | -0.11582 | 0.98391 | -0.11579 | 0.50645
56 | 7.5456e-05 | 1.8792e-05 | -7.5456e-05 | -1.8911e-05 | 7.622e-11 | -1.1915e-07 | 0.00011407 | 0.00011412 | 0.00011412 | 0.98391 | -0.11582 | 0.9839 | -0.11582 | 0.042265
57 | -0.012568 | -0.0031066 | 0.01259 | 0.0031137 | 2.1655e-05 | 7.0969e-06 | 0.018962 | 0.018961 | 0.018962 | 0.98548 | -0.10434 | 0.98723 | -0.091574 | 7.0229
58 | 0.00071728 | 0.00017903 | -0.00071726 | -0.00017952 | 2.8724e-08 | -4.8908e-07 | 0.0010828 | 0.001083 | 0.001083 | 0.98548 | -0.10434 | 0.98544 | -0.10463 | 0.4011
59 | -0.012664 | -0.0031323 | 0.012703 | 0.003145 | 3.8656e-05 | 1.2683e-05 | 0.019074 | 0.019073 | 0.019074 | 0.98723 | -0.091574 | 0.99034 | -0.069006 | 7.0643
60 | 0.00015574 | 3.8794e-05 | -0.00015574 | -3.9032e-05 | 6.4508e-10 | -2.3799e-07 | 0.00023508 | 0.00023517 | 0.00023517 | 0.98544 | -0.10463 | 0.98544 | -0.10466 | 0.087098
61 | -0.0011104 | -0.00027775 | 0.0011106 | 0.00027674 | 1.3939e-07 | -1.0111e-06 | 0.0016558 | 0.0016554 | 0.0016558 | 0.99782 | -0.015579 | 0.99795 | -0.014665 | 0.61324
62 | 0.0011104 | 0.00027775 | -0.0011104 | -0.00027811 | 4.8975e-08 | -3.5507e-07 | 0.0016558 | 0.0016559 | 0.0016559 | 0.99782 | -0.015579 | 0.99778 | -0.015898 | 0.61329
63 | 0.0057801 | 0.0014313 | -0.0057673 | -0.00143 | 1.2829e-05 | 1.3215e-06 | 0.0086125 | 0.0086137 | 0.0086137 | 0.99795 | -0.014665 | 0.99567 | -0.031076 | 3.1903
64 | -0.0068907 | -0.001708 | 0.0069044 | 0.0017106 | 1.3698e-05 | 2.5421e-06 | 0.010268 | 0.010267 | 0.010268 | 0.99795 | -0.014665 | 1 | 0 | 3.8029
65 | 0.00071352 | 0.00017864 | -0.00071351 | -0.00017882 | 9.9555e-09 | -1.8021e-07 | 0.001064 | 0.0010641 | 0.0010641 | 0.99778 | -0.015898 | 0.99776 | -0.015999 | 0.39411
66 | -0.012703 | -0.003145 | 0.012714 | 0.0031487 | 1.1178e-05 | 3.6649e-06 | 0.019073 | 0.019073 | 0.019073 | 0.99034 | -0.069006 | 0.99124 | -0.062501 | 7.0641
67 | -0.012714 | -0.0031487 | 0.012742 | 0.0031577 | 2.7636e-05 | 9.0564e-06 | 0.019073 | 0.019072 | 0.019073 | 0.99124 | -0.062501 | 0.99347 | -0.046457 | 7.064
68 | -0.012909 | -0.0031997 | 0.012919 | 0.003203 | 1.0132e-05 | 3.3334e-06 | 0.019323 | 0.019323 | 0.019323 | 0.99347 | -0.046457 | 0.99427 | -0.040667 | 7.1566
69 | 0.024377 | 0.0060926 | -0.02436 | -0.0060862 | 1.7445e-05 | 6.4308e-06 | 0.036268 | 0.036268 | 0.036268 | 1 | 0 | 0.99926 | -0.0052013 | 13.4326
70 | 0.024156 | 0.0060351 | -0.024096 | -0.0060128 | 6.0757e-05 | 2.2385e-05 | 0.035965 | 0.035965 | 0.035965 | 0.99926 | -0.0052013 | 0.99667 | -0.023528 | 13.3205
71 | 0.024096 | 0.0060128 | -0.024074 | -0.0060049 | 2.1281e-05 | 7.8418e-06 | 0.035965 | 0.035965 | 0.035965 | 0.99667 | -0.023528 | 0.99576 | -0.029968 | 13.3205
72 | 0.0018792 | 0.00046447 | -0.0018788 | -0.00046525 | 3.4315e-07 | -7.7601e-07 | 0.0028062 | 0.0028065 | 0.0028065 | 0.99567 | -0.031076 | 0.99548 | -0.032429 | 1.0394
73 | 0.003322 | 0.00082564 | -0.0033207 | -0.0008262 | 1.2167e-06 | -5.6145e-07 | 0.0049622 | 0.0049626 | 0.0049626 | 0.99567 | -0.031076 | 0.99529 | -0.033764 | 1.838
74 | 0.00056611 | 0.00013987 | -0.0005661 | -0.00014011 | 8.1727e-09 | -2.352e-07 | 0.00084535 | 0.00084543 | 0.00084543 | 0.99567 | -0.031076 | 0.99565 | -0.031183 | 0.31312
75 | 0.010699 | 0.0026861 | -0.010684 | -0.0026816 | 1.5098e-05 | 4.5777e-06 | 0.01599 | 0.015991 | 0.015991 | 0.99576 | -0.029968 | 0.99431 | -0.040136 | 5.9224
76 | 0.013375 | 0.0033188 | -0.013363 | -0.0033149 | 1.1721e-05 | 3.8963e-06 | 0.019975 | 0.019976 | 0.019976 | 0.99576 | -0.029968 | 0.99486 | -0.036428 | 7.3984
77 | -0.0030031 | -0.00074719 | 0.0030034 | 0.00074699 | 3.0201e-07 | -1.9605e-07 | 0.0044883 | 0.0044882 | 0.0044883 | 0.99519 | -0.034501 | 0.99529 | -0.033764 | 1.6623
78 | 0.00031738 | 7.9204e-05 | -0.00031737 | -7.9541e-05 | 3.6514e-09 | -3.3644e-07 | 0.00047438 | 0.00047449 | 0.00047449 | 0.99529 | -0.033764 | 0.99528 | -0.033847 | 0.17574
79 | 0.0011395 | 0.00028341 | -0.0011393 | -0.00028411 | 1.0238e-07 | -6.9638e-07 | 0.0017025 | 0.0017027 | 0.0017027 | 0.99548 | -0.032429 | 0.99539 | -0.033087 | 0.63064
80 | 0.00073939 | 0.00018183 | -0.00073938 | -0.00018195 | 7.1971e-09 | -1.2025e-07 | 0.001104 | 0.001104 | 0.001104 | 0.99548 | -0.032429 | 0.99547 | -0.032502 | 0.40891
81 | 0.00036149 | 8.8829e-05 | -0.00036147 | -9.0593e-05 | 2.4799e-08 | -1.7632e-06 | 0.00053964 | 0.00054026 | 0.00054026 | 0.99565 | -0.031183 | 0.99558 | -0.031689 | 0.2001
82 | 0.010684 | 0.0026816 | -0.010682 | -0.002681 | 1.6933e-06 | 5.1366e-07 | 0.015991 | 0.015991 | 0.015991 | 0.99431 | -0.040136 | 0.99415 | -0.041278 | 5.9224
83 | 0.012927 | 0.0032055 | -0.012919 | -0.003203 | 7.4261e-06 | 2.4425e-06 | 0.019322 | 0.019323 | 0.019323 | 0.99486 | -0.036428 | 0.99427 | -0.040667 | 7.1565
84 | 0.009998 | 0.0025095 | -0.00997 | -0.0025013 | 2.8034e-05 | 8.1893e-06 | 0.014966 | 0.014967 | 0.014967 | 0.99415 | -0.041278 | 0.99127 | -0.061509 | 5.5434
85 | 0.00997 | 0.0025013 | -0.0099081 | -0.0024832 | 6.1866e-05 | 1.8126e-05 | 0.014967 | 0.014969 | 0.014969 | 0.99127 | -0.061509 | 0.98493 | -0.10643 | 5.5441
86 | 0.0049098 | 0.0012305 | -0.0049097 | -0.0012305 | 1.2452e-07 | 1.7369e-09 | 0.0074177 | 0.0074177 | 0.0074177 | 0.98493 | -0.10643 | 0.9849 | -0.10661 | 2.7473
87 | -0.00030674 | -7.6876e-05 | 0.00030677 | 7.353e-05 | 3.3827e-08 | -3.3468e-06 | 0.00045856 | 0.0004574 | 0.00045856 | 0.99536 | -0.033333 | 0.99547 | -0.032502 | 0.16984
88 | 0.00082425 | 0.00020514 | -0.00082414 | -0.00020655 | 1.0575e-07 | -1.4107e-06 | 0.0012317 | 0.0012322 | 0.0012322 | 0.99539 | -0.033087 | 0.99526 | -0.03402 | 0.45636
89 | 0.00050084 | 0.00012531 | -0.00050083 | -0.00012544 | 4.0816e-09 | -1.3761e-07 | 0.00076492 | 0.00076497 | 0.00076497 | 0.97418 | -0.1881 | 0.97418 | -0.18816 | 0.28332
90 | -0.00061826 | -0.00015474 | 0.00061834 | 0.00015304 | 7.7131e-08 | -1.6976e-06 | 0.00094429 | 0.00094367 | 0.00094429 | 0.97418 | -0.1881 | 0.97431 | -0.18719 | 0.34974
91 | 0.00033094 | 8.2865e-05 | -0.00033094 | -8.294e-05 | 9.7629e-10 | -7.5862e-08 | 0.00050547 | 0.00050549 | 0.00050549 | 0.97418 | -0.18816 | 0.97417 | -0.18818 | 0.18722
92 | 5.0166e-05 | 1.2426e-05 | -5.0166e-05 | -1.2573e-05 | 4.305e-11 | -1.4651e-07 | 7.6555e-05 | 7.6608e-05 | 7.6608e-05 | 0.97442 | -0.18635 | 0.97442 | -0.18636 | 0.028373
93 | -0.00024539 | -6.1353e-05 | 0.0002454 | 5.9801e-05 | 1.0927e-08 | -1.5521e-06 | 0.00037467 | 0.00037412 | 0.00037467 | 0.97442 | -0.18635 | 0.97447 | -0.18602 | 0.13877
94 | 0.0009383 | 0.00022705 | -0.00093826 | -0.00022746 | 4.3853e-08 | -4.1125e-07 | 0.0014299 | 0.0014301 | 0.0014301 | 0.97447 | -0.18602 | 0.97442 | -0.18638 | 0.52966
95 | 0.00093826 | 0.00022746 | -0.00093823 | -0.00022775 | 3.1039e-08 | -2.9101e-07 | 0.0014301 | 0.0014302 | 0.0014302 | 0.97442 | -0.18638 | 0.97439 | -0.18664 | 0.52969
96 | 0.00074011 | 0.0001781 | -0.00074011 | -0.00017817 | 4.4783e-09 | -6.8576e-08 | 0.0011276 | 0.0011277 | 0.0011277 | 0.97439 | -0.18664 | 0.97438 | -0.18668 | 0.41765
97 | 0.0006865 | 0.00016473 | -0.00068647 | -0.00016536 | 3.5121e-08 | -6.2731e-07 | 0.0010458 | 0.001046 | 0.001046 | 0.97438 | -0.18668 | 0.97433 | -0.18708 | 0.38742
98 | 0.00068647 | 0.00016536 | -0.00068636 | -0.00016725 | 1.0592e-07 | -1.8899e-06 | 0.001046 | 0.0010467 | 0.0010467 | 0.97433 | -0.18708 | 0.97417 | -0.18827 | 0.38766
99 | 5.0811e-05 | 1.0001e-05 | -5.0811e-05 | -1.0418e-05 | 1.2314e-10 | -4.1663e-07 | 7.6728e-05 | 7.685e-05 | 7.685e-05 | 0.97417 | -0.18827 | 0.97417 | -0.1883 | 0.028463
100 | 0.00063555 | 0.00015725 | -0.00063547 | -0.00015898 | 8.3036e-08 | -1.7274e-06 | 0.00097005 | 0.00097068 | 0.00097068 | 0.97417 | -0.18827 | 0.97404 | -0.18923 | 0.35951
101 | 5.0811e-05 | 1.0418e-05 | -5.081e-05 | -1.2734e-05 | 6.922e-10 | -2.3163e-06 | 7.685e-05 | 7.7612e-05 | 7.7612e-05 | 0.97417 | -0.1883 | 0.97416 | -0.18841 | 0.028745
102 | 0.00020312 | 5.0621e-05 | -0.00020312 | -5.0906e-05 | 1.3759e-09 | -2.8461e-07 | 0.00031019 | 0.0003103 | 0.0003103 | 0.97404 | -0.18923 | 0.97404 | -0.18928 | 0.11492

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.032215 | 0.0078367

## res_load
| p_mw | q_mvar
0 | 0.00031532 | 7.9026e-05
1 | 0.00015555 | 3.8984e-05
2 | 0.0016093 | 0.00040332
3 | 0.00020913 | 5.2413e-05
4 | 0.00070874 | 0.00017763
5 | 0.00017799 | 4.4609e-05
6 | 0.00015936 | 3.9938e-05
7 | 7.2078e-05 | 1.8065e-05
8 | 0.00040139 | 0.0001006
9 | 8.9721e-05 | 2.2486e-05
10 | 5.1402e-05 | 1.2883e-05
11 | 4.9903e-05 | 1.2507e-05
12 | 0.00023017 | 5.7686e-05
13 | 9.5076e-05 | 2.3828e-05
14 | 0.00018311 | 4.5892e-05
15 | 0.00010572 | 2.6495e-05
16 | 0.00053535 | 0.00013417
17 | 0.0001806 | 4.5263e-05
18 | 7.6086e-05 | 1.9069e-05
19 | 0.00027515 | 6.8959e-05
20 | 0.00010693 | 2.68e-05
21 | 0.00017594 | 4.4094e-05
22 | 0.00069764 | 0.00017485
23 | 7.7654e-05 | 1.9462e-05
24 | 0.0018068 | 0.00045282
25 | 0.00011377 | 2.8514e-05
26 | 0.00013329 | 3.3407e-05
27 | 0.00013963 | 3.4994e-05
28 | 0.00021328 | 5.3454e-05
29 | 0.0003809 | 9.5463e-05
30 | 0.0001671 | 4.1878e-05
31 | 0.00026914 | 6.7453e-05
32 | 0.00058952 | 0.00014775
33 | 0.00019054 | 4.7754e-05
34 | 0.00021402 | 5.3639e-05
35 | 0.00038968 | 9.7663e-05
36 | 0.00082873 | 0.0002077
37 | 0.0003243 | 8.1278e-05
38 | 7.5456e-05 | 1.8911e-05
39 | 7.4551e-05 | 1.8684e-05
40 | 0.00056152 | 0.00014073
41 | 0.00039686 | 9.9463e-05
42 | 0.00015574 | 3.9032e-05
43 | 0.00016732 | 4.1934e-05
44 | 0.00013331 | 3.341e-05
45 | 0.00020355 | 5.1015e-05
46 | 0.00020461 | 5.128e-05
47 | 0.00043667 | 0.00010944
48 | 0.00036147 | 9.0593e-05
49 | 0.00068444 | 0.00017154
50 | 0.0049983 | 0.0012527
51 | 0.00071351 | 0.00017882
52 | 0.00030674 | 7.6876e-05
53 | 0.00043261 | 0.00010842
54 | 0.0003151 | 7.8972e-05
55 | 0.00031737 | 7.9541e-05
56 | 0.00082414 | 0.00020655
57 | 0.00011743 | 2.943e-05
58 | 0.0001699 | 4.258e-05
59 | 0.00033094 | 8.294e-05
60 | 0.00019522 | 4.8927e-05
61 | 5.0166e-05 | 1.2573e-05
62 | 0.00019811 | 4.9652e-05
63 | 5.3609e-05 | 1.3436e-05
64 | 0.00043235 | 0.00010836
65 | 0.00020312 | 5.0906e-05
66 | 5.081e-05 | 1.2734e-05
67 | 0.0049097 | 0.0012305
68 | 0.00015279 | 3.8293e-05
69 | 0.00019335 | 4.8459e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1