## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-20_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1008-20_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1008-20_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1008-20_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1008-20_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1008-20_0_3_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_1008-20_0_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1008-20_0_3_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1008-20_0_3_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1008-20_0_3_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1008-20_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1008-20_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1008-20_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1008-20_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1008-20_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1008-20_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1008-20_0_3_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1008-20_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1008-20_0_3_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1008-20_0_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1008-20_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1008-20_0_3_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_1008-20_0_3_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_1008-20_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1008-20_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1008-20_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1008-20_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1008-20_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1008-20_0_3_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1008-20_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1008-20_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1008-20_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1008-20_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1008-20_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1008-20_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_MV_125_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-20_0_3_load_0 | 0 | 0.0007789 | 0.00019521 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-20_0_3_load_1 | 1 | 0.0053186 | 0.001333 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-20_0_3_load_2 | 2 | 0.00032041 | 8.0303e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-20_0_3_load_22 | 6 | 0.00061047 | 0.000153 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-20_0_3_load_19 | 7 | 0.017696 | 0.0044349 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-20_0_3_load_29 | 8 | 0.024417 | 0.0061194 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-20_0_3_load_23 | 9 | 0.026102 | 0.0065417 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-20_0_3_load_5 | 10 | 0.0011878 | 0.00029769 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-20_0_3_load_24 | 15 | 0.00090388 | 0.00022653 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-20_0_3_load_33 | 16 | 0.00024787 | 6.2122e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-20_0_3_load_26 | 19 | 0.0011883 | 0.00029782 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-20_0_3_load_34 | 21 | 0.00036184 | 9.0685e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-20_0_3_load_25 | 22 | 0.021203 | 0.0053141 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-20_0_3_load_11 | 23 | 0.020145 | 0.0050487 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-20_0_3_load_12 | 24 | 0.046349 | 0.011616 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-20_0_3_load_13 | 25 | 0.0045877 | 0.0011498 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-20_0_3_load_15 | 26 | 0.023926 | 0.0059965 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-20_0_3_load_16 | 27 | 0.00029249 | 7.3304e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-20_0_3_load_18 | 29 | 0.0010412 | 0.00026095 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-20_0_3_load_31 | 30 | 0.00054817 | 0.00013739 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1008-20_0_3_load_32 | 31 | 0.0013633 | 0.00034169 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1008-20_0_3_load_27 | 32 | 0.00067083 | 0.00016813 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1008-20_0_3_load_28 | 33 | 0.02509 | 0.0062881 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1008-20_0_3_load_30 | 34 | 0.0009167 | 0.00022975 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-20_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0084559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-20_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.026725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-20_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.047317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-20_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.001714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1008-20_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.064539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-20_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.036299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1008-20_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.10635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-20_0_3_line_7 | NAYY 4x150 SE | 6 | 31 | 0.13204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-20_0_3_line_8 | NAYY 4x150 SE | 7 | 18 | 0.020115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-20_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.032663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-20_0_3_line_10 | NAYY 4x150 SE | 9 | 20 | 0.014103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1008-20_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.057442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-20_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.0065659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-20_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.009071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-20_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.019861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-20_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.02306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-20_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0077447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-20_0_3_line_17 | NAYY 4x150 SE | 15 | 20 | 0.032613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-20_0_3_line_18 | NAYY 4x150 SE | 16 | 21 | 0.014931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-20_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.018326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1008-20_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.013467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-20_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.005112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-20_0_3_line_22 | NAYY 4x150 SE | 19 | 22 | 0.0010733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-20_0_3_line_23 | NAYY 4x150 SE | 20 | 24 | 0.018919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-20_0_3_line_24 | NAYY 4x150 SE | 22 | 32 | 0.02008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-20_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.014215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-20_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.018982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-20_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0015216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-20_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.026051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-20_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.031739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1008-20_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.028495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1008-20_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.0068288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1008-20_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0044842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1008-20_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.013527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-20_0_3_trafo_23 | 0.25 MVA 20/0.4 kV | 35 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2642949.3082 | 1199213.6844 | 2642955.4968 | 1199207.9221
1 | 2642975.0502 | 1199189.7035 | 2642960.8797 | 1199202.91 | 2642955.4968 | 1199207.9221
2 | 2643003.6401 | 1199153.1337 | 2643002.0645 | 1199159.4148 | 2642999.9696 | 1199163.8022 | 2642985.7385 | 1199179.7422 | 2642975.0502 | 1199189.7035
3 | 2643004.9275 | 1199151.9979 | 2643003.6401 | 1199153.1337
4 | 2643004.9275 | 1199151.9979 | 2643008.5952 | 1199149.1338 | 2643019.4969 | 1199158.8843 | 2643029.8749 | 1199167.3526 | 2643041.4925 | 1199176.0188 | 2643056.1509 | 1199185.3406
5 | 2643056.1509 | 1199185.3406 | 2643061.7916 | 1199172.8297 | 2643071.0299 | 1199152.2308
6 | 2643056.1509 | 1199185.3406 | 2643071.7743 | 1199193.88 | 2643084.7121 | 1199199.9989 | 2643100.9525 | 1199206.375 | 2643114.2815 | 1199211.0292 | 2643124.7501 | 1199214.2953 | 2643143.5267 | 1199219.5003 | 2643147.2046 | 1199220.5052 | 2643155.31 | 1199222.7087
7 | 2643060.3651 | 1199031.5291 | 2643056.3798 | 1199074.2466 | 2643056.1716 | 1199103.1613 | 2643060.9323 | 1199121.9283 | 2643069.9007 | 1199125.2503 | 2643078.374 | 1199139.1524 | 2643072.1687 | 1199149.6914 | 2643071.0299 | 1199152.2308
8 | 2643174.7209 | 1199227.9857 | 2643155.31 | 1199222.7087
9 | 2643128.1937 | 1199220.0144 | 2643159.6018 | 1199228.9827
10 | 2643173.1629 | 1199232.8549 | 2643159.6018 | 1199228.9827
11 | 2643234.8926 | 1199252.4228 | 2643247.0955 | 1199257.9919 | 2643258.0677 | 1199265.2864 | 2643270.6658 | 1199275.172 | 2643279.1915 | 1199284.8947 | 2643280.112 | 1199286.566
12 | 2643283.2797 | 1199292.3173 | 2643280.112 | 1199286.566
13 | 2643226.2872 | 1199249.4812 | 2643234.8926 | 1199252.4228
14 | 2643283.2797 | 1199292.3173 | 2643282.6339 | 1199297.3932 | 2643282.8784 | 1199301.4862 | 2643283.8166 | 1199306.5069 | 2643285.2016 | 1199311.8644
15 | 2643226.2872 | 1199249.4812 | 2643218.5705 | 1199246.8462 | 2643210.6487 | 1199244.143 | 2643204.3903 | 1199242.2584
16 | 2643285.2016 | 1199311.8644 | 2643277.9967 | 1199314.705
17 | 2643173.1629 | 1199232.8549 | 2643204.3903 | 1199242.2584
18 | 2643277.9967 | 1199314.705 | 2643268.9758 | 1199318.2617 | 2643264.565 | 1199321.0793
19 | 2643174.7209 | 1199227.9857 | 2643192.4103 | 1199232.9606
20 | 2643192.4103 | 1199232.9606 | 2643195.3053 | 1199219.808
21 | 2643173.1629 | 1199232.8549 | 2643174.7209 | 1199227.9857
22 | 2643195.536 | 1199218.7598 | 2643195.3053 | 1199219.808
23 | 2643173.1629 | 1199232.8549 | 2643170.2317 | 1199251.5455
24 | 2643195.536 | 1199218.7598 | 2643198.3618 | 1199205.9217 | 2643199.1645 | 1199199.1459 | 2643199.1775 | 1199199.0351
25 | 2643169.2512 | 1199265.6859 | 2643169.0921 | 1199262.0086 | 2643169.5074 | 1199256.1638 | 2643170.2317 | 1199251.5455
26 | 2643169.2512 | 1199265.6859 | 2643169.3009 | 1199266.835 | 2643170.0267 | 1199272.8214 | 2643171.2144 | 1199280.2119 | 2643171.4823 | 1199284.5202
27 | 2643171.4823 | 1199284.5202 | 2643171.5767 | 1199286.0389
28 | 2643170.3621 | 1199312.0122 | 2643171.9716 | 1199292.3908 | 2643171.5767 | 1199286.0389
29 | 2643167.7718 | 1199343.6449 | 2643168.891 | 1199329.9452 | 2643170.3621 | 1199312.0122
30 | 2643167.7718 | 1199343.6449 | 2643196.179 | 1199345.884
31 | 2643196.179 | 1199345.884 | 2643202.9867 | 1199346.4206
32 | 2643199.6988 | 1199194.5813 | 2643199.1775 | 1199199.0351
33 | 2643199.6988 | 1199194.5813 | 2643201.2715 | 1199181.146

## bus_geodata
| x | y | coords
0 | 2642949.3082 | 1199213.6844
1 | 2642955.4968 | 1199207.9221
2 | 2642975.0502 | 1199189.7035
3 | 2643003.6401 | 1199153.1337
4 | 2643004.9275 | 1199151.9979
5 | 2643056.1509 | 1199185.3406
6 | 2643071.0299 | 1199152.2308
7 | 2643155.31 | 1199222.7087
8 | 2643128.1937 | 1199220.0144
9 | 2643159.6018 | 1199228.9827
10 | 2643280.112 | 1199286.566
11 | 2643234.8926 | 1199252.4228
12 | 2643283.2797 | 1199292.3173
13 | 2643226.2872 | 1199249.4812
14 | 2643285.2016 | 1199311.8644
15 | 2643204.3903 | 1199242.2584
16 | 2643277.9967 | 1199314.705
17 | 2643192.4103 | 1199232.9606
18 | 2643174.7209 | 1199227.9857
19 | 2643195.3053 | 1199219.808
20 | 2643173.1629 | 1199232.8549
21 | 2643264.565 | 1199321.0793
22 | 2643195.536 | 1199218.7598
23 | 2643169.2512 | 1199265.6859
24 | 2643170.2317 | 1199251.5455
25 | 2643171.4823 | 1199284.5202
26 | 2643171.5767 | 1199286.0389
27 | 2643170.3621 | 1199312.0122
28 | 2643167.7718 | 1199343.6449
29 | 2643196.179 | 1199345.884
30 | 2643202.9867 | 1199346.4206
31 | 2643060.3651 | 1199031.5291
32 | 2643199.1775 | 1199199.0351
33 | 2643199.6988 | 1199194.5813
34 | 2643201.2715 | 1199181.146
35 | 2643173.1629 | 1199232.8549

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99437 | -0.039531 | 0.0007789 | 0.00019521
1 | 0.99438 | -0.039465 | 0.0053186 | 0.001333
2 | 0.99461 | -0.03782 | 0.00032041 | 8.0303e-05
3 | 0.99505 | -0.034755 | 0 | 0
4 | 0.99506 | -0.034644 | 0 | 0
5 | 0.99566 | -0.030464 | 0 | 0
6 | 0.99555 | -0.031191 | 0.00061047 | 0.000153
7 | 0.99693 | -0.021452 | 0.017696 | 0.0044349
8 | 0.99886 | -0.0079692 | 0.024417 | 0.0061194
9 | 1 | 0 | -0.20083 | -0.050237
10 | 0.99788 | -0.014835 | 0.0011878 | 0.00029769
11 | 0.99803 | -0.013796 | 0 | 0
12 | 0.99787 | -0.014875 | 0 | 0
13 | 0.99805 | -0.013631 | 0 | 0
14 | 0.99786 | -0.014997 | 0 | 0
15 | 0.99811 | -0.013213 | 0.00090388 | 0.00022653
16 | 0.99785 | -0.015045 | 0.00024787 | 6.2122e-05
17 | 0.9964 | -0.025208 | 0 | 0
18 | 0.99768 | -0.016178 | 0 | 0
19 | 0.99545 | -0.031858 | 0.0011883 | 0.00029782
20 | 0.99823 | -0.012326 | 0 | 0
21 | 0.99784 | -0.015099 | 0.00036184 | 9.0685e-05
22 | 0.99538 | -0.032375 | 0.021203 | 0.0053141
23 | 0.99458 | -0.037979 | 0.020145 | 0.0050487
24 | 0.99561 | -0.030736 | 0.046349 | 0.011616
25 | 0.99375 | -0.043807 | 0.0045877 | 0.0011498
26 | 0.99369 | -0.044204 | 0.023926 | 0.0059965
27 | 0.99362 | -0.044702 | 0.00029249 | 7.3304e-05
28 | 0.99355 | -0.045213 | 0 | 0
29 | 0.99349 | -0.045672 | 0.0010412 | 0.00026095
30 | 0.99348 | -0.045709 | 0.00054817 | 0.00013739
31 | 0.9953 | -0.033012 | 0.0013633 | 0.00034169
32 | 0.99461 | -0.037776 | 0.00067083 | 0.00016813
33 | 0.99444 | -0.038953 | 0.02509 | 0.0062881
34 | 0.99442 | -0.039078 | 0.0009167 | 0.00022975
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0007789 | -0.00019521 | 0.0007789 | 0.0001951 | 7.1683e-09 | -1.0693e-07 | 0.0011656 | 0.0011655 | 0.0011656 | 0.99437 | -0.039531 | 0.99438 | -0.039465 | 0.4317
1 | -0.0060975 | -0.0015281 | 0.0060989 | 0.0015282 | 1.3884e-06 | 1.8723e-07 | 0.0091244 | 0.0091243 | 0.0091244 | 0.99438 | -0.039465 | 0.99461 | -0.03782 | 3.3794
2 | -0.0064193 | -0.0016086 | 0.006422 | 0.001609 | 2.7231e-06 | 4.3298e-07 | 0.0096036 | 0.0096034 | 0.0096036 | 0.99461 | -0.03782 | 0.99505 | -0.034755 | 3.5569
3 | -0.006422 | -0.001609 | 0.0064221 | 0.001609 | 9.8639e-08 | 1.5673e-08 | 0.0096034 | 0.0096034 | 0.0096034 | 0.99505 | -0.034755 | 0.99506 | -0.034644 | 3.5568
4 | -0.0064221 | -0.001609 | 0.0064258 | 0.0016096 | 3.714e-06 | 5.8961e-07 | 0.0096034 | 0.0096031 | 0.0096034 | 0.99506 | -0.034644 | 0.99566 | -0.030464 | 3.5568
5 | 0.0019744 | 0.0004927 | -0.0019742 | -0.0004931 | 1.9712e-07 | -3.9623e-07 | 0.0029499 | 0.0029501 | 0.0029501 | 0.99566 | -0.030464 | 0.99555 | -0.031191 | 1.0926
6 | -0.0084002 | -0.0021023 | 0.0084106 | 0.0021049 | 1.0456e-05 | 2.6369e-06 | 0.012553 | 0.012553 | 0.012553 | 0.99566 | -0.030464 | 0.99693 | -0.021452 | 4.6493
7 | 0.0013637 | 0.0003401 | -0.0013633 | -0.00034169 | 3.422e-07 | -1.5848e-06 | 0.0020377 | 0.0020383 | 0.0020383 | 0.99555 | -0.031191 | 0.9953 | -0.033012 | 0.75491
8 | -0.026106 | -0.0065399 | 0.026125 | 0.0065469 | 1.9057e-05 | 7.0672e-06 | 0.038965 | 0.038965 | 0.038965 | 0.99693 | -0.021452 | 0.99768 | -0.016178 | 14.4315
9 | -0.024417 | -0.0061194 | 0.024444 | 0.0061293 | 2.6966e-05 | 9.9436e-06 | 0.036374 | 0.036374 | 0.036374 | 0.99886 | -0.0079692 | 1 | 0 | 13.4718
10 | 0.17559 | 0.044107 | -0.17529 | -0.043992 | 0.00030046 | 0.00011519 | 0.26131 | 0.26131 | 0.26131 | 1 | 0 | 0.99823 | -0.012326 | 48.391
11 | -0.0017975 | -0.00044986 | 0.0017978 | 0.00044921 | 2.5746e-07 | -6.515e-07 | 0.0026802 | 0.0026799 | 0.0026802 | 0.99788 | -0.014835 | 0.99803 | -0.013796 | 0.99266
12 | 0.00060973 | 0.00015217 | -0.00060972 | -0.00015226 | 3.3854e-09 | -8.4473e-08 | 0.00090899 | 0.00090902 | 0.00090902 | 0.99788 | -0.014835 | 0.99787 | -0.014875 | 0.33667
13 | -0.0017978 | -0.00044921 | 0.0017978 | 0.0004491 | 4.0651e-08 | -1.029e-07 | 0.0026799 | 0.0026799 | 0.0026799 | 0.99803 | -0.013796 | 0.99805 | -0.013631 | 0.99256
14 | 0.00060972 | 0.00015226 | -0.00060971 | -0.00015251 | 1.0242e-08 | -2.5551e-07 | 0.00090902 | 0.00090911 | 0.00090911 | 0.99787 | -0.014875 | 0.99786 | -0.014997 | 0.33671
15 | -0.0017978 | -0.0004491 | 0.0017979 | 0.00044884 | 1.0334e-07 | -2.6163e-07 | 0.0026799 | 0.0026798 | 0.0026799 | 0.99805 | -0.013631 | 0.99811 | -0.013213 | 0.99255
16 | 0.00060971 | 0.00015251 | -0.00060971 | -0.00015261 | 3.9942e-09 | -9.9632e-08 | 0.00090911 | 0.00090914 | 0.00090914 | 0.99786 | -0.014997 | 0.99785 | -0.015045 | 0.33672
17 | -0.0027018 | -0.00067538 | 0.0027021 | 0.00067508 | 3.3005e-07 | -2.9935e-07 | 0.0040273 | 0.0040272 | 0.0040273 | 0.99811 | -0.013213 | 0.99823 | -0.012326 | 1.4916
18 | 0.00036184 | 9.0491e-05 | -0.00036184 | -9.0685e-05 | 2.7122e-09 | -1.9399e-07 | 0.00053952 | 0.00053958 | 0.00053958 | 0.99785 | -0.015045 | 0.99784 | -0.015099 | 0.19985
19 | -0.049142 | -0.012325 | 0.049204 | 0.012349 | 6.1595e-05 | 2.3451e-05 | 0.073392 | 0.073392 | 0.073392 | 0.9964 | -0.025208 | 0.99768 | -0.016178 | 27.1822
20 | 0.049142 | 0.012325 | -0.049097 | -0.012308 | 4.5265e-05 | 1.7234e-05 | 0.073392 | 0.073392 | 0.073392 | 0.9964 | -0.025208 | 0.99545 | -0.031858 | 27.1822
21 | -0.075329 | -0.018896 | 0.075369 | 0.018911 | 4.0269e-05 | 1.5421e-05 | 0.11236 | 0.11236 | 0.11236 | 0.99768 | -0.016178 | 0.99823 | -0.012326 | 41.6136
22 | 0.047908 | 0.01201 | -0.047905 | -0.012009 | 3.435e-06 | 1.3072e-06 | 0.071616 | 0.071616 | 0.071616 | 0.99545 | -0.031858 | 0.99538 | -0.032375 | 26.5243
23 | 0.097215 | 0.024406 | -0.096967 | -0.024311 | 0.00024796 | 9.5123e-05 | 0.14493 | 0.14493 | 0.14493 | 0.99823 | -0.012326 | 0.99561 | -0.030736 | 53.6769
24 | 0.026702 | 0.0066948 | -0.026682 | -0.0066874 | 1.9966e-05 | 7.4184e-06 | 0.039918 | 0.039918 | 0.039918 | 0.99538 | -0.032375 | 0.99461 | -0.037776 | 14.7845
25 | -0.050567 | -0.012675 | 0.050617 | 0.012695 | 5.077e-05 | 1.9342e-05 | 0.075655 | 0.075655 | 0.075655 | 0.99458 | -0.037979 | 0.99561 | -0.030736 | 28.0203
26 | 0.030422 | 0.0076265 | -0.030398 | -0.0076173 | 2.4539e-05 | 9.1921e-06 | 0.045516 | 0.045516 | 0.045516 | 0.99458 | -0.037979 | 0.99375 | -0.043807 | 16.8578
27 | 0.02581 | 0.0064675 | -0.025808 | -0.006467 | 1.4181e-06 | 5.2573e-07 | 0.038647 | 0.038647 | 0.038647 | 0.99375 | -0.043807 | 0.99369 | -0.044204 | 14.3135
28 | 0.0018822 | 0.00047056 | -0.0018821 | -0.00047085 | 1.2911e-07 | -2.878e-07 | 0.0028181 | 0.0028182 | 0.0028182 | 0.99369 | -0.044204 | 0.99362 | -0.044702 | 1.0438
29 | 0.0015896 | 0.00039755 | -0.0015895 | -0.00039791 | 1.1221e-07 | -3.6791e-07 | 0.0023802 | 0.0023803 | 0.0023803 | 0.99362 | -0.044702 | 0.99355 | -0.045213 | 0.88161
30 | 0.0015895 | 0.00039791 | -0.0015894 | -0.00039824 | 1.0075e-07 | -3.3026e-07 | 0.0023803 | 0.0023805 | 0.0023805 | 0.99355 | -0.045213 | 0.99349 | -0.045672 | 0.88166
31 | 0.00054818 | 0.0001373 | -0.00054817 | -0.00013739 | 2.8724e-09 | -8.7321e-08 | 0.00082101 | 0.00082104 | 0.00082104 | 0.99349 | -0.045672 | 0.99348 | -0.045709 | 0.30409
32 | 0.026011 | 0.0065193 | -0.026007 | -0.0065177 | 4.2374e-06 | 1.5716e-06 | 0.038914 | 0.038914 | 0.038914 | 0.99461 | -0.037776 | 0.99444 | -0.038953 | 14.4128
33 | 0.00091672 | 0.00022958 | -0.0009167 | -0.00022975 | 1.5882e-08 | -1.6939e-07 | 0.0013717 | 0.0013717 | 0.0013717 | 0.99444 | -0.038953 | 0.99442 | -0.039078 | 0.50804

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22693 | 0.056778

## res_load
| p_mw | q_mvar
0 | 0.0007789 | 0.00019521
1 | 0.0053186 | 0.001333
2 | 0.00032041 | 8.0303e-05
3 | 0.00061047 | 0.000153
4 | 0.017696 | 0.0044349
5 | 0.024417 | 0.0061194
6 | 0.026102 | 0.0065417
7 | 0.0011878 | 0.00029769
8 | 0.00090388 | 0.00022653
9 | 0.00024787 | 6.2122e-05
10 | 0.0011883 | 0.00029782
11 | 0.00036184 | 9.0685e-05
12 | 0.021203 | 0.0053141
13 | 0.020145 | 0.0050487
14 | 0.046349 | 0.011616
15 | 0.0045877 | 0.0011498
16 | 0.023926 | 0.0059965
17 | 0.00029249 | 7.3304e-05
18 | 0.0010412 | 0.00026095
19 | 0.00054817 | 0.00013739
20 | 0.0013633 | 0.00034169
21 | 0.00067083 | 0.00016813
22 | 0.02509 | 0.0062881
23 | 0.0009167 | 0.00022975

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1