## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-3_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1008-3_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1008-3_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1008-3_0_7_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1008-3_0_7_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_1008-3_0_7_node_54 | 0.4 | n |  | TRUE
6 | bus_LV_1008-3_0_7_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1008-3_0_7_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1008-3_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1008-3_0_7_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1008-3_0_7_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1008-3_0_7_node_39 | 0.4 | n |  | TRUE
12 | bus_LV_1008-3_0_7_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_1008-3_0_7_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1008-3_0_7_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1008-3_0_7_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1008-3_0_7_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1008-3_0_7_node_38 | 0.4 | n |  | TRUE
18 | bus_LV_1008-3_0_7_node_119 | 0.4 | n |  | TRUE
19 | bus_LV_1008-3_0_7_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_1008-3_0_7_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_1008-3_0_7_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1008-3_0_7_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1008-3_0_7_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1008-3_0_7_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1008-3_0_7_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1008-3_0_7_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1008-3_0_7_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1008-3_0_7_node_52 | 0.4 | n |  | TRUE
29 | bus_LV_1008-3_0_7_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1008-3_0_7_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1008-3_0_7_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1008-3_0_7_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1008-3_0_7_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1008-3_0_7_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1008-3_0_7_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1008-3_0_7_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1008-3_0_7_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1008-3_0_7_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1008-3_0_7_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1008-3_0_7_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1008-3_0_7_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1008-3_0_7_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1008-3_0_7_node_60 | 0.4 | n |  | TRUE
44 | bus_LV_1008-3_0_7_node_57 | 0.4 | n |  | TRUE
45 | bus_LV_1008-3_0_7_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_1008-3_0_7_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_1008-3_0_7_node_78 | 0.4 | n |  | TRUE
48 | bus_LV_1008-3_0_7_node_58 | 0.4 | n |  | TRUE
49 | bus_LV_1008-3_0_7_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1008-3_0_7_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_1008-3_0_7_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_1008-3_0_7_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_1008-3_0_7_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_1008-3_0_7_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_1008-3_0_7_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1008-3_0_7_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_1008-3_0_7_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_1008-3_0_7_node_118 | 0.4 | n |  | TRUE
59 | bus_LV_1008-3_0_7_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_1008-3_0_7_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_1008-3_0_7_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1008-3_0_7_node_77 | 0.4 | n |  | TRUE
63 | bus_LV_1008-3_0_7_node_70 | 0.4 | n |  | TRUE
64 | bus_LV_1008-3_0_7_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_1008-3_0_7_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_1008-3_0_7_node_72 | 0.4 | n |  | TRUE
67 | bus_LV_1008-3_0_7_node_81 | 0.4 | n |  | TRUE
68 | bus_LV_1008-3_0_7_node_73 | 0.4 | n |  | TRUE
69 | bus_LV_1008-3_0_7_node_74 | 0.4 | n |  | TRUE
70 | bus_LV_1008-3_0_7_node_75 | 0.4 | n |  | TRUE
71 | bus_LV_1008-3_0_7_node_84 | 0.4 | n |  | TRUE
72 | bus_LV_1008-3_0_7_node_85 | 0.4 | n |  | TRUE
73 | bus_LV_1008-3_0_7_node_117 | 0.4 | n |  | TRUE
74 | bus_LV_1008-3_0_7_node_95 | 0.4 | n |  | TRUE
75 | bus_LV_1008-3_0_7_node_93 | 0.4 | n |  | TRUE
76 | bus_LV_1008-3_0_7_node_116 | 0.4 | n |  | TRUE
77 | bus_LV_1008-3_0_7_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_1008-3_0_7_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_1008-3_0_7_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_1008-3_0_7_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_1008-3_0_7_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_1008-3_0_7_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_1008-3_0_7_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_1008-3_0_7_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_1008-3_0_7_node_90 | 0.4 | n |  | TRUE
86 | bus_LV_1008-3_0_7_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_1008-3_0_7_node_99 | 0.4 | n |  | TRUE
88 | bus_LV_1008-3_0_7_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_1008-3_0_7_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_1008-3_0_7_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_1008-3_0_7_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_1008-3_0_7_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_1008-3_0_7_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_1008-3_0_7_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_1008-3_0_7_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_1008-3_0_7_node_112 | 0.4 | n |  | TRUE
97 | bus_LV_1008-3_0_7_node_101 | 0.4 | n |  | TRUE
98 | bus_LV_1008-3_0_7_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_1008-3_0_7_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_1008-3_0_7_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_1008-3_0_7_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_1008-3_0_7_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1008-3_0_7_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1008-3_0_7_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_1008-3_0_7_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_1008-3_0_7_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_1008-3_0_7_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_1008-3_0_7_node_105 | 0.4 | n |  | TRUE
109 | bus_LV_1008-3_0_7_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_1008-3_0_7_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_1008-3_0_7_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_1008-3_0_7_node_109 | 0.4 | n |  | TRUE
113 | bus_LV_1008-3_0_7_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_1008-3_0_7_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_1008-3_0_7_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_1008-3_0_7_node_113 | 0.4 | n |  | TRUE
117 | bus_MV_125_0_node_102 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-3_0_7_load_0 | 0 | 0.022372 | 0.005607 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-3_0_7_load_1 | 1 | 0.004972 | 0.0012461 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-3_0_7_load_22 | 4 | 0.0011602 | 0.00029078 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-3_0_7_load_54 | 5 | 0.0035465 | 0.00088885 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-3_0_7_load_6 | 8 | 0.0064824 | 0.0016246 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-3_0_7_load_21 | 9 | 0.0022022 | 0.00055192 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-3_0_7_load_32 | 10 | 0.0071248 | 0.0017857 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-3_0_7_load_37 | 12 | 0.00073612 | 0.00018449 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-3_0_7_load_7 | 13 | 0.011764 | 0.0029482 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-3_0_7_load_8 | 14 | 0.0063854 | 0.0016003 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-3_0_7_load_10 | 15 | 0.013934 | 0.0034922 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-3_0_7_load_119 | 18 | 0.0063542 | 0.0015925 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-3_0_7_load_47 | 19 | 0.0010614 | 0.000266 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-3_0_7_load_44 | 20 | 0.0029138 | 0.00073026 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-3_0_7_load_16 | 21 | 0.00087321 | 0.00021885 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-3_0_7_load_12 | 22 | 0.0071179 | 0.0017839 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-3_0_7_load_13 | 23 | 0.0068355 | 0.0017131 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-3_0_7_load_18 | 26 | 0.017341 | 0.004346 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-3_0_7_load_52 | 28 | 0.011146 | 0.0027934 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-3_0_7_load_14 | 29 | 0.0012438 | 0.00031174 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1008-3_0_7_load_15 | 30 | 0.0012466 | 0.00031243 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1008-3_0_7_load_43 | 32 | 0.012233 | 0.0030658 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1008-3_0_7_load_28 | 33 | 0.0017579 | 0.00044057 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1008-3_0_7_load_20 | 35 | 0.0031699 | 0.00079445 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1008-3_0_7_load_23 | 36 | 0.0034024 | 0.00085271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1008-3_0_7_load_24 | 37 | 0.0033248 | 0.00083327 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1008-3_0_7_load_25 | 38 | 0.00048601 | 0.00012181 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1008-3_0_7_load_31 | 40 | 0.003261 | 0.00081729 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1008-3_0_7_load_34 | 41 | 0.0019631 | 0.000492 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1008-3_0_7_load_57 | 44 | 0.00078282 | 0.00019619 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1008-3_0_7_load_29 | 45 | 0.0024577 | 0.00061597 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1008-3_0_7_load_35 | 46 | 0.0021623 | 0.00054192 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1008-3_0_7_load_78 | 47 | 0.0012093 | 0.00030309 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1008-3_0_7_load_36 | 49 | 0.0021569 | 0.00054057 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1008-3_0_7_load_49 | 51 | 0.0024345 | 0.00061013 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1008-3_0_7_load_50 | 52 | 0.00086738 | 0.00021738 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1008-3_0_7_load_45 | 53 | 0.0010815 | 0.00027105 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1008-3_0_7_load_40 | 54 | 0.0026078 | 0.00065358 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1008-3_0_7_load_41 | 55 | 0.009828 | 0.0024631 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1008-3_0_7_load_46 | 56 | 0.00091391 | 0.00022905 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1008-3_0_7_load_51 | 57 | 0.00072531 | 0.00018178 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1008-3_0_7_load_118 | 58 | 0.0016499 | 0.00041351 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1008-3_0_7_load_59 | 59 | 0.00090176 | 0.000226 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1008-3_0_7_load_55 | 60 | 0.0021091 | 0.00052858 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1008-3_0_7_load_56 | 61 | 0.00050767 | 0.00012723 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1008-3_0_7_load_77 | 62 | 0.0011977 | 0.00030016 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1008-3_0_7_load_69 | 64 | 0.00062353 | 0.00015627 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1008-3_0_7_load_72 | 66 | 0.00041177 | 0.0001032 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1008-3_0_7_load_73 | 68 | 0.00084577 | 0.00021197 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1008-3_0_7_load_74 | 69 | 0.000369 | 9.2481e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1008-3_0_7_load_84 | 71 | 0.00084726 | 0.00021234 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1008-3_0_7_load_95 | 74 | 0.00021981 | 5.509e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1008-3_0_7_load_93 | 75 | 0.00020309 | 5.09e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1008-3_0_7_load_116 | 76 | 0.00016688 | 4.1824e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1008-3_0_7_load_102 | 77 | 0.00087405 | 0.00021906 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1008-3_0_7_load_61 | 78 | 0.00066442 | 0.00016652 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1008-3_0_7_load_62 | 79 | 0.00024433 | 6.1236e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1008-3_0_7_load_65 | 82 | 0.0003809 | 9.5462e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1008-3_0_7_load_66 | 84 | 0.0006846 | 0.00017158 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1008-3_0_7_load_67 | 86 | 0.00026959 | 6.7565e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1008-3_0_7_load_99 | 87 | 0.00035464 | 8.8882e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1008-3_0_7_load_83 | 88 | 0.00019884 | 4.9833e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1008-3_0_7_load_79 | 89 | 0.0014577 | 0.00036533 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1008-3_0_7_load_80 | 90 | 0.0009631 | 0.00024137 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1008-3_0_7_load_86 | 92 | 0.00074886 | 0.00018768 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1008-3_0_7_load_87 | 93 | 0.00047817 | 0.00011984 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1008-3_0_7_load_112 | 96 | 0.0020164 | 0.00050537 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1008-3_0_7_load_91 | 98 | 0.00067689 | 0.00016964 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1008-3_0_7_load_92 | 99 | 0.00027107 | 6.7937e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1008-3_0_7_load_94 | 100 | 0.00010997 | 2.7562e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1008-3_0_7_load_97 | 102 | 0.00022048 | 5.5258e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1008-3_0_7_load_98 | 103 | 0.00044843 | 0.00011239 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1008-3_0_7_load_100 | 105 | 0.00066542 | 0.00016677 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1008-3_0_7_load_104 | 107 | 0.0015291 | 0.00038323 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1008-3_0_7_load_105 | 108 | 0.00063612 | 0.00015943 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1008-3_0_7_load_106 | 109 | 0.0012095 | 0.00030313 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1008-3_0_7_load_107 | 110 | 0.00080913 | 0.00020279 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1008-3_0_7_load_115 | 113 | 0.0008603 | 0.00021561 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1008-3_0_7_load_110 | 114 | 0.00249 | 0.00062406 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1008-3_0_7_load_111 | 115 | 0.0010448 | 0.00026186 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1008-3_0_7_load_113 | 116 | 0.00048829 | 0.00012238 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-3_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.031937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-3_0_7_line_1 | NAYY 4x150 SE | 0 | 2 | 0.037669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-3_0_7_line_2 | NAYY 4x150 SE | 2 | 3 | 0.048368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-3_0_7_line_3 | NAYY 4x150 SE | 3 | 4 | 0.026833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1008-3_0_7_line_4 | NAYY 4x150 SE | 3 | 5 | 0.031648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-3_0_7_line_5 | NAYY 4x150 SE | 4 | 9 | 0.035674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1008-3_0_7_line_6 | NAYY 4x150 SE | 5 | 10 | 0.030434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-3_0_7_line_7 | NAYY 4x150 SE | 6 | 7 | 0.059121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-3_0_7_line_8 | NAYY 4x150 SE | 6 | 8 | 0.049297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-3_0_7_line_9 | NAYY 4x150 SE | 7 | 11 | 0.086122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-3_0_7_line_10 | NAYY 4x150 SE | 7 | 12 | 0.042285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-3_0_7_line_11 | NAYY 4x150 SE | 8 | 13 | 0.0063136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-3_0_7_line_12 | NAYY 4x150 SE | 9 | 35 | 0.099744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-3_0_7_line_13 | NAYY 4x150 SE | 10 | 31 | 0.0028039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-3_0_7_line_14 | NAYY 4x150 SE | 11 | 19 | 0.031332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-3_0_7_line_15 | NAYY 4x150 SE | 11 | 20 | 0.0088237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-3_0_7_line_16 | NAYY 4x150 SE | 11 | 17 | 0.055566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-3_0_7_line_17 | NAYY 4x150 SE | 12 | 21 | 0.014637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-3_0_7_line_18 | NAYY 4x150 SE | 13 | 14 | 0.018055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-3_0_7_line_19 | NAYY 4x150 SE | 14 | 15 | 0.0095057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1008-3_0_7_line_20 | NAYY 4x150 SE | 15 | 16 | 0.043813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-3_0_7_line_21 | NAYY 4x150 SE | 16 | 22 | 0.014576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-3_0_7_line_22 | NAYY 4x150 SE | 16 | 23 | 0.0013889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-3_0_7_line_23 | NAYY 4x150 SE | 17 | 18 | 0.045636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-3_0_7_line_24 | NAYY 4x150 SE | 20 | 53 | 0.0042712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-3_0_7_line_25 | NAYY 4x150 SE | 21 | 30 | 0.016411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-3_0_7_line_26 | NAYY 4x150 SE | 22 | 24 | 0.030383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1008-3_0_7_line_27 | NAYY 4x150 SE | 23 | 25 | 0.018303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-3_0_7_line_28 | NAYY 4x150 SE | 24 | 26 | 0.01738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-3_0_7_line_29 | NAYY 4x150 SE | 24 | 27 | 0.014533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1008-3_0_7_line_30 | NAYY 4x150 SE | 25 | 28 | 0.03583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1008-3_0_7_line_31 | NAYY 4x150 SE | 27 | 31 | 0.059921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1008-3_0_7_line_32 | NAYY 4x150 SE | 27 | 32 | 0.03254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1008-3_0_7_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0055514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1008-3_0_7_line_34 | NAYY 4x150 SE | 31 | 33 | 0.015402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1008-3_0_7_line_35 | NAYY 4x150 SE | 32 | 34 | 0.028798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1008-3_0_7_line_36 | NAYY 4x150 SE | 33 | 45 | 0.0097203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1008-3_0_7_line_37 | NAYY 4x150 SE | 34 | 54 | 0.093941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1008-3_0_7_line_38 | NAYY 4x150 SE | 36 | 37 | 0.025359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1008-3_0_7_line_39 | NAYY 4x150 SE | 36 | 38 | 0.066506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1008-3_0_7_line_40 | NAYY 4x150 SE | 37 | 39 | 0.0215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1008-3_0_7_line_41 | NAYY 4x150 SE | 39 | 40 | 0.005407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1008-3_0_7_line_42 | NAYY 4x150 SE | 39 | 41 | 0.015374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1008-3_0_7_line_43 | NAYY 4x150 SE | 40 | 45 | 0.025121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1008-3_0_7_line_44 | NAYY 4x150 SE | 41 | 46 | 0.002136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1008-3_0_7_line_45 | NAYY 4x150 SE | 42 | 43 | 0.16863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1008-3_0_7_line_46 | NAYY 4x150 SE | 42 | 44 | 0.090807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1008-3_0_7_line_47 | NAYY 4x150 SE | 43 | 47 | 0.062009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1008-3_0_7_line_48 | NAYY 4x150 SE | 44 | 48 | 0.015977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1008-3_0_7_line_49 | NAYY 4x150 SE | 46 | 49 | 0.014815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1008-3_0_7_line_50 | NAYY 4x150 SE | 47 | 62 | 0.13599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1008-3_0_7_line_51 | NAYY 4x150 SE | 48 | 59 | 0.016398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1008-3_0_7_line_52 | NAYY 4x150 SE | 48 | 51 | 0.015789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1008-3_0_7_line_53 | NAYY 4x150 SE | 49 | 50 | 0.025727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1008-3_0_7_line_54 | NAYY 4x150 SE | 50 | 51 | 0.010133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1008-3_0_7_line_55 | NAYY 4x150 SE | 50 | 52 | 0.011678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1008-3_0_7_line_56 | NAYY 4x150 SE | 52 | 58 | 0.020724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1008-3_0_7_line_57 | NAYY 4x150 SE | 53 | 56 | 0.017074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1008-3_0_7_line_58 | NAYY 4x150 SE | 54 | 55 | 0.02087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1008-3_0_7_line_59 | NAYY 4x150 SE | 56 | 57 | 0.0055356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1008-3_0_7_line_60 | NAYY 4x150 SE | 59 | 78 | 0.016881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1008-3_0_7_line_61 | NAYY 4x150 SE | 60 | 61 | 0.010287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1008-3_0_7_line_62 | NAYY 4x150 SE | 61 | 62 | 0.01559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1008-3_0_7_line_63 | NAYY 4x150 SE | 61 | 63 | 0.37133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1008-3_0_7_line_64 | NAYY 4x150 SE | 63 | 64 | 0.05761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1008-3_0_7_line_65 | NAYY 4x150 SE | 64 | 65 | 0.01694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1008-3_0_7_line_66 | NAYY 4x150 SE | 65 | 66 | 0.010556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1008-3_0_7_line_67 | NAYY 4x150 SE | 66 | 67 | 0.20116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1008-3_0_7_line_68 | NAYY 4x150 SE | 67 | 91 | 0.056357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1008-3_0_7_line_69 | NAYY 4x150 SE | 67 | 89 | 0.073038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1008-3_0_7_line_70 | NAYY 4x150 SE | 68 | 69 | 0.034808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1008-3_0_7_line_71 | NAYY 4x150 SE | 68 | 70 | 0.015387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1008-3_0_7_line_72 | NAYY 4x150 SE | 70 | 71 | 0.29409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1008-3_0_7_line_73 | NAYY 4x150 SE | 71 | 72 | 0.018008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1008-3_0_7_line_74 | NAYY 4x150 SE | 72 | 73 | 0.23318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1008-3_0_7_line_75 | NAYY 4x150 SE | 73 | 76 | 0.079462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1008-3_0_7_line_76 | NAYY 4x150 SE | 74 | 75 | 0.15143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1008-3_0_7_line_77 | NAYY 4x150 SE | 75 | 100 | 0.0097701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1008-3_0_7_line_78 | NAYY 4x150 SE | 75 | 99 | 0.018433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1008-3_0_7_line_79 | NAYY 4x150 SE | 76 | 77 | 0.18759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
80 | LV_1008-3_0_7_line_80 | NAYY 4x150 SE | 77 | 105 | 0.045212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_1008-3_0_7_line_81 | NAYY 4x150 SE | 79 | 80 | 0.087813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1008-3_0_7_line_82 | NAYY 4x150 SE | 80 | 81 | 0.084743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1008-3_0_7_line_83 | NAYY 4x150 SE | 80 | 82 | 0.13577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1008-3_0_7_line_84 | NAYY 4x150 SE | 81 | 83 | 0.072874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1008-3_0_7_line_85 | NAYY 4x150 SE | 81 | 84 | 0.13425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1008-3_0_7_line_86 | NAYY 4x150 SE | 82 | 85 | 0.023432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1008-3_0_7_line_87 | NAYY 4x150 SE | 83 | 88 | 0.041501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1008-3_0_7_line_88 | NAYY 4x150 SE | 84 | 86 | 0.042466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1008-3_0_7_line_89 | NAYY 4x150 SE | 85 | 98 | 0.016456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1008-3_0_7_line_90 | NAYY 4x150 SE | 86 | 87 | 0.22276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1008-3_0_7_line_91 | NAYY 4x150 SE | 87 | 102 | 0.027984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_1008-3_0_7_line_92 | NAYY 4x150 SE | 88 | 91 | 0.016092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_1008-3_0_7_line_93 | NAYY 4x150 SE | 89 | 90 | 0.0020891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1008-3_0_7_line_94 | NAYY 4x150 SE | 92 | 93 | 0.0010517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1008-3_0_7_line_95 | NAYY 4x150 SE | 92 | 94 | 0.018392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1008-3_0_7_line_96 | NAYY 4x150 SE | 93 | 95 | 0.029009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1008-3_0_7_line_97 | NAYY 4x150 SE | 94 | 96 | 0.17296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1008-3_0_7_line_98 | NAYY 4x150 SE | 95 | 97 | 0.092252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1008-3_0_7_line_99 | NAYY 4x150 SE | 96 | 115 | 0.050027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1008-3_0_7_line_100 | NAYY 4x150 SE | 97 | 106 | 0.059464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1008-3_0_7_line_101 | NAYY 4x150 SE | 97 | 105 | 0.030954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1008-3_0_7_line_102 | NAYY 4x150 SE | 100 | 101 | 0.03154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1008-3_0_7_line_103 | NAYY 4x150 SE | 101 | 102 | 0.061089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1008-3_0_7_line_104 | NAYY 4x150 SE | 101 | 103 | 0.10469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_1008-3_0_7_line_105 | NAYY 4x150 SE | 103 | 104 | 0.092195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1008-3_0_7_line_106 | NAYY 4x150 SE | 104 | 116 | 0.087696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_1008-3_0_7_line_107 | NAYY 4x150 SE | 106 | 107 | 0.0075313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1008-3_0_7_line_108 | NAYY 4x150 SE | 107 | 108 | 0.012001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1008-3_0_7_line_109 | NAYY 4x150 SE | 109 | 110 | 0.063609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_1008-3_0_7_line_110 | NAYY 4x150 SE | 109 | 111 | 0.094371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_1008-3_0_7_line_111 | NAYY 4x150 SE | 110 | 112 | 0.0039969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_1008-3_0_7_line_112 | NAYY 4x150 SE | 111 | 113 | 0.13931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
113 | LV_1008-3_0_7_line_113 | NAYY 4x150 SE | 112 | 114 | 0.016983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_1008-3_0_7_line_114 | NAYY 4x150 SE | 113 | 116 | 0.020199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_1008-3_0_7_line_115 | NAYY 4x150 SE | 114 | 115 | 0.024632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-3_0_7_trafo_48 | 0.25 MVA 20/0.4 kV | 117 | 50 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2643810.8798 | 1199998.8213 | 2643826.4316 | 1200018.4801 | 2643830.5921 | 1200023.9477
1 | 2643787.5089 | 1199969.2784 | 2643810.8798 | 1199998.8213
2 | 2643769.8744 | 1199925.9694 | 2643769.5861 | 1199938.3187 | 2643772.6982 | 1199946.8574 | 2643777.1761 | 1199954.9836 | 2643783.2394 | 1199963.8886 | 2643787.5089 | 1199969.2784
3 | 2643769.8744 | 1199925.9694 | 2643753.7402 | 1199921.0597 | 2643746.5654 | 1199918.3724 | 2643744.5253 | 1199917.2963
4 | 2643769.8744 | 1199925.9694 | 2643771.4253 | 1199920.033 | 2643773.8949 | 1199914.4257 | 2643776.3065 | 1199910.5189 | 2643779.1648 | 1199906.9378 | 2643782.4316 | 1199903.7043 | 2643785.8086 | 1199901.0276 | 2643786.9316 | 1199900.3592
5 | 2643718.8505 | 1199893.0222 | 2643729.0885 | 1199905.5041 | 2643735.5004 | 1199911.521 | 2643740.9231 | 1199915.3961 | 2643744.5253 | 1199917.2963
6 | 2643816.2654 | 1199896.6379 | 2643812.8588 | 1199895.7337 | 2643805.2868 | 1199895.3114 | 2643801.2891 | 1199895.4266 | 2643797.3334 | 1199896.0313 | 2643793.4808 | 1199897.126 | 2643789.5172 | 1199898.8201 | 2643786.9316 | 1199900.3592
7 | 2643982.8643 | 1200020.396 | 2643952.6306 | 1200044.554 | 2643937.9994 | 1200058.9324
8 | 2643937.9994 | 1200058.9324 | 2643933.9857 | 1200055.0229 | 2643903.2463 | 1200023.9711
9 | 2643982.8643 | 1200020.396 | 2644013.8999 | 1199996.9555 | 2644017.6306 | 1199991.7467 | 2644021.054 | 1199983.8007 | 2644024.3302 | 1199978.2884 | 2644008.5689 | 1199957.9165
10 | 2643982.8643 | 1200020.396 | 2643954.6937 | 1199988.8614
11 | 2643903.2463 | 1200023.9711 | 2643901.0377 | 1200021.7401 | 2643898.7812 | 1200019.5077
12 | 2643718.8505 | 1199893.0222 | 2643669.8077 | 1199833.2303 | 2643654.9337 | 1199816.4655
13 | 2643818.9755 | 1199897.3572 | 2643816.2654 | 1199896.6379
14 | 2644008.5689 | 1199957.9165 | 2643982.455 | 1199975.2295
15 | 2644008.5689 | 1199957.9165 | 2644003.0599 | 1199951.0238
16 | 2644008.5689 | 1199957.9165 | 2644024.3302 | 1199978.2884 | 2644047.1054 | 1199959.0564
17 | 2643954.6937 | 1199988.8614 | 2643944.9425 | 1199977.9457
18 | 2643885.9458 | 1200006.8095 | 2643898.7812 | 1200019.5077
19 | 2643885.9458 | 1200006.8095 | 2643879.1882 | 1200000.1242
20 | 2643846.9965 | 1199970.4259 | 2643868.296 | 1199989.3483 | 2643879.1882 | 1200000.1242
21 | 2643846.9965 | 1199970.4259 | 2643850.9315 | 1199956.3915
22 | 2643846.9965 | 1199970.4259 | 2643845.8598 | 1199969.6278
23 | 2644047.1054 | 1199959.0564 | 2644018.8359 | 1199923.1725
24 | 2644003.0599 | 1199951.0238 | 2644000.3933 | 1199947.6873
25 | 2643944.9425 | 1199977.9457 | 2643934.0096 | 1199965.7072
26 | 2643867.706 | 1199932.801 | 2643864.826 | 1199935.1701 | 2643854.2178 | 1199943.9084 | 2643852.3749 | 1199951.2434 | 2643850.9315 | 1199956.3915
27 | 2643830.8635 | 1199959.1347 | 2643838.3242 | 1199964.3367 | 2643845.8598 | 1199969.6278
28 | 2643881.1996 | 1199942.7278 | 2643873.2652 | 1199939.8346 | 2643867.706 | 1199932.801
29 | 2643858.6768 | 1199921.3951 | 2643867.706 | 1199932.801
30 | 2643830.8635 | 1199959.1347 | 2643820.9844 | 1199953.5703 | 2643811.7319 | 1199948.7331 | 2643803.4983 | 1199945.1152 | 2643798.7766 | 1199943.3032
31 | 2643818.9755 | 1199897.3572 | 2643826.7513 | 1199901.1274 | 2643833.1738 | 1199906.7221 | 2643838.0442 | 1199914.2731 | 2643841.2486 | 1199922.668 | 2643842.1992 | 1199929.0452 | 2643849.9274 | 1199926.8451 | 2643858.6768 | 1199921.3951
32 | 2643858.6768 | 1199921.3951 | 2643885.1163 | 1199902.4274
33 | 2643930.3111 | 1199961.5672 | 2643934.0096 | 1199965.7072
34 | 2643818.9755 | 1199897.3572 | 2643828.487 | 1199885.2432
35 | 2643908.5159 | 1199885.6406 | 2643885.1163 | 1199902.4274
36 | 2643828.487 | 1199885.2432 | 2643834.4898 | 1199877.5978
37 | 2643908.5159 | 1199885.6406 | 2643965.4379 | 1199841.3337 | 2643981.6981 | 1199826.8023
38 | 2643807.8514 | 1199840.1094 | 2643828.3775 | 1199848.5764 | 2643831.507 | 1199848.9794
39 | 2643807.8514 | 1199840.1094 | 2643797.5914 | 1199835.8771 | 2643783.1831 | 1199822.9199 | 2643768.8173 | 1199811.4306 | 2643768.4308 | 1199805.9913 | 2643770.2432 | 1199805.9268 | 2643769.7899 | 1199795.5687
40 | 2643852.5772 | 1199853.0897 | 2643840.4635 | 1199850.1326 | 2643831.507 | 1199848.9794
41 | 2643852.5772 | 1199853.0897 | 2643850.1763 | 1199857.6191 | 2643850.003 | 1199857.8398
42 | 2643852.5772 | 1199853.0897 | 2643854.2669 | 1199840.6951 | 2643854.4512 | 1199837.8366
43 | 2643850.003 | 1199857.8398 | 2643834.4898 | 1199877.5978
44 | 2643854.4512 | 1199837.8366 | 2643854.5887 | 1199835.7051
45 | 2643774.8622 | 1199528.5935 | 2643770.9798 | 1199532.6896 | 2643766.3376 | 1199542.7947 | 2643760.6651 | 1199562.6199 | 2643761.3889 | 1199578.145 | 2643768.8979 | 1199604.915 | 2643773.0777 | 1199628.8257 | 2643775.6964 | 1199682.942 | 2643777.8065 | 1199692.1404
46 | 2643777.8065 | 1199692.1404 | 2643782.7834 | 1199698.6916 | 2643823.7436 | 1199754.7564 | 2643826.7005 | 1199758.5024 | 2643826.3407 | 1199766.8688
47 | 2643774.8622 | 1199528.5935 | 2643783.1616 | 1199530.5998 | 2643829.3328 | 1199557.5691
48 | 2643825.6543 | 1199782.8306 | 2643826.3407 | 1199766.8688
49 | 2643853.7925 | 1199821.0043 | 2643854.2857 | 1199822.5628 | 2643854.9369 | 1199830.3053 | 2643854.5887 | 1199835.7051
50 | 2643950.8405 | 1199607.9454 | 2643946.7566 | 1199608.0874 | 2643934.2482 | 1199611.1083 | 2643925.0145 | 1199610.9182 | 2643916.2929 | 1199608.3638 | 2643829.3328 | 1199557.5691
51 | 2643825.6543 | 1199782.8306 | 2643822.4384 | 1199784.2856 | 2643820.3492 | 1199786.8051 | 2643816.5049 | 1199795.5962
52 | 2643825.6543 | 1199782.8306 | 2643830.0393 | 1199782.8628 | 2643836.8325 | 1199785.6808 | 2643840.2579 | 1199787.8404
53 | 2643844.278 | 1199797.1418 | 2643851.0415 | 1199812.311 | 2643853.7925 | 1199821.0043
54 | 2643844.278 | 1199797.1418 | 2643840.2579 | 1199787.8404
55 | 2643844.278 | 1199797.1418 | 2643840.1391 | 1199799.8908 | 2643836.4411 | 1199805.4893
56 | 2643825.0188 | 1199822.7818 | 2643836.4411 | 1199805.4893
57 | 2643989.7335 | 1199934.3499 | 2644000.3933 | 1199947.6873
58 | 2643981.6981 | 1199826.8023 | 2643992.5824 | 1199817.0752 | 2643996.7095 | 1199812.3518
59 | 2643986.2775 | 1199930.0257 | 2643989.7335 | 1199934.3499
60 | 2643809.7412 | 1199811.0633 | 2643816.5049 | 1199795.5962
61 | 2643970.9507 | 1199618.6098 | 2643969.9534 | 1199614.5059 | 2643967.0206 | 1199610.5822 | 2643965.9397 | 1199610.1481
62 | 2643950.8405 | 1199607.9454 | 2643959.6876 | 1199607.6377 | 2643965.9397 | 1199610.1481
63 | 2643965.9397 | 1199610.1481 | 2644191.2609 | 1199314.9904
64 | 2644191.2609 | 1199314.9904 | 2644182.4325 | 1199300.0723 | 2644180.5953 | 1199296.2455 | 2644176.0004 | 1199288.5072 | 2644166.7839 | 1199282.8138 | 2644159.9652 | 1199268.122
65 | 2644156.3547 | 1199251.6415 | 2644158.9295 | 1199265.8907 | 2644159.9652 | 1199268.122
66 | 2644154.4746 | 1199241.2551 | 2644156.3547 | 1199251.6415
67 | 2644154.4746 | 1199241.2551 | 2643965.1813 | 1199173.2005
68 | 2643965.1813 | 1199173.2005 | 2643963.3366 | 1199167.2836 | 2643960.7982 | 1199160.4278 | 2643958.0923 | 1199153.5707 | 2643953.8696 | 1199145.8909 | 2643946.3326 | 1199133.3285 | 2643940.0737 | 1199122.9878
69 | 2643965.1813 | 1199173.2005 | 2643955.6179 | 1199173.2191 | 2643949.0192 | 1199172.8593 | 2643936.8271 | 1199171.0577 | 2643930.4864 | 1199169.7659 | 2643919.9377 | 1199168.132 | 2643892.5497 | 1199167.4589
70 | 2644499.4239 | 1199172.4635 | 2644506.1598 | 1199185.6187 | 2644513.9077 | 1199187.0772 | 2644519.482 | 1199197.8664
71 | 2644491.5159 | 1199159.295 | 2644496.3883 | 1199166.5353 | 2644499.4239 | 1199172.4635
72 | 2644463.6157 | 1198866.5354 | 2644491.5159 | 1199159.295
73 | 2644451.2384 | 1198853.935 | 2644458.8732 | 1198859.3948 | 2644461.3718 | 1198862.3261 | 2644463.6157 | 1198866.5354
74 | 2644451.2384 | 1198853.935 | 2644451.8221 | 1198620.7528
75 | 2644451.8221 | 1198620.7528 | 2644409.2881 | 1198612.2655 | 2644402.7173 | 1198610.1044 | 2644398.6985 | 1198607.8177 | 2644395.9638 | 1198604.8624 | 2644394.0025 | 1198601.3459 | 2644393.007 | 1198596.9694 | 2644393.1672 | 1198590.7782 | 2644394.659 | 1198585.1586
76 | 2644130.9152 | 1198667.8706 | 2644222.6053 | 1198788.3833
77 | 2644130.9152 | 1198667.8706 | 2644122.8787 | 1198673.4266
78 | 2644144.7873 | 1198655.7904 | 2644142.0401 | 1198658.6138 | 2644134.1298 | 1198665.6483 | 2644130.9152 | 1198667.8706
79 | 2644218.5691 | 1198520.4903 | 2644394.659 | 1198585.1586
80 | 2644218.5691 | 1198520.4903 | 2644201.3926 | 1198505.6995 | 2644197.2632 | 1198499.799 | 2644195.6971 | 1198496.3633 | 2644196.5828 | 1198492.9457 | 2644200.0756 | 1198485.7078
81 | 2643790.1305 | 1198969.9136 | 2643851.7287 | 1198925.4843 | 2643854.9191 | 1198914.0574
82 | 2643790.1305 | 1198969.9136 | 2643854.9375 | 1199024.7302
83 | 2643790.1305 | 1198969.9136 | 2643764.7265 | 1198953.6297 | 2643756.6087 | 1198947.5002 | 2643748.6618 | 1198940.9273 | 2643744.4067 | 1198936.5715 | 2643740.1563 | 1198931.5932 | 2643736.8282 | 1198926.466 | 2643732.496 | 1198918.0852 | 2643729.8875 | 1198911.3957 | 2643727.6742 | 1198903.7752 | 2643726.1443 | 1198895.3593 | 2643725.1962 | 1198886.5252 | 2643724.5176 | 1198872.0677 | 2643724.651 | 1198862.1708
84 | 2643906.0133 | 1199076.6562 | 2643903.1222 | 1199073.2331 | 2643881.2048 | 1199049.8814 | 2643854.9375 | 1199024.7302
85 | 2643854.9375 | 1199024.7302 | 2643872.6401 | 1199010.2741 | 2643925.7696 | 1198974.3882 | 2643931.0065 | 1198972.5479 | 2643934.3979 | 1198972.1392 | 2643937.3789 | 1198972.6614 | 2643940.4603 | 1198974.0181 | 2643952.5648 | 1198985.7247 | 2643954.5363 | 1198986.8398 | 2643956.9923 | 1198987.3026 | 2643960.2993 | 1198986.9711 | 2643965.0383 | 1198985.5496 | 2643966.9217 | 1198984.7465
86 | 2643724.9669 | 1198838.7412 | 2643724.651 | 1198862.1708
87 | 2643906.0133 | 1199076.6562 | 2643913.5212 | 1199084.9048 | 2643927.3846 | 1199103.8283 | 2643931.1883 | 1199109.5716
88 | 2643974.3812 | 1198956.5353 | 2643982.173 | 1198961.3953 | 2643984.0582 | 1198962.8656 | 2643984.8207 | 1198964.7833 | 2643984.8419 | 1198968.1187 | 2643983.9064 | 1198971.069 | 2643982.2376 | 1198974.3475 | 2643979.4586 | 1198977.4288 | 2643971.1642 | 1198982.9376 | 2643966.9217 | 1198984.7465
89 | 2643724.9669 | 1198838.7412 | 2643716.9197 | 1198838.56 | 2643709.1359 | 1198841.7363
90 | 2644026.2426 | 1198739.8963 | 2643974.3812 | 1198956.5353
91 | 2644026.2426 | 1198739.8963 | 2644050.8794 | 1198726.6248
92 | 2643940.0737 | 1199122.9878 | 2643931.1883 | 1199109.5716
93 | 2643892.5497 | 1199167.4589 | 2643890.4612 | 1199167.4076
94 | 2644143.4438 | 1198364.8589 | 2644143.5182 | 1198365.908
95 | 2644141.1062 | 1198346.6986 | 2644142.0165 | 1198349.24 | 2644142.6328 | 1198353.4358 | 2644143.4438 | 1198364.8589
96 | 2644159.5334 | 1198386.0789 | 2644149.0113 | 1198381.6876 | 2644145.999 | 1198379.1862 | 2644144.171 | 1198375.1038 | 2644143.5182 | 1198365.908
97 | 2644141.1062 | 1198346.6986 | 2643968.5249 | 1198335.2881
98 | 2644211.309 | 1198457.0455 | 2644211.0137 | 1198450.6397 | 2644210.4137 | 1198447.3334 | 2644208.323 | 1198441.7259 | 2644197.6864 | 1198420.9023 | 2644191.9423 | 1198410.921 | 2644186.274 | 1198403.0413 | 2644181.1402 | 1198398.0673 | 2644176.3096 | 1198394.2962 | 2644165.7738 | 1198388.6819 | 2644159.5334 | 1198386.0789
99 | 2643968.5249 | 1198335.2881 | 2643972.0097 | 1198313.9351 | 2643972.4323 | 1198307.2122 | 2643971.531 | 1198303.4368 | 2643969.347 | 1198299.085 | 2643966.7831 | 1198295.6531 | 2643959.7038 | 1198290.7334
100 | 2644211.309 | 1198457.0455 | 2644175.4011 | 1198454.401 | 2644155.8952 | 1198453.9012 | 2644152.0166 | 1198455.2844
101 | 2644211.309 | 1198457.0455 | 2644210.5414 | 1198461.9981 | 2644207.1621 | 1198471.0227 | 2644200.0756 | 1198485.7078
102 | 2644095.9477 | 1198689.658 | 2644107.0968 | 1198684.3372 | 2644122.8787 | 1198673.4266
103 | 2644095.9477 | 1198689.658 | 2644092.8506 | 1198699.7075 | 2644090.5046 | 1198703.9259 | 2644084.5544 | 1198708.4846 | 2644050.8794 | 1198726.6248
104 | 2644095.9477 | 1198689.658 | 2644085.3397 | 1198636.0497 | 2644083.283 | 1198627.8856 | 2644080.1246 | 1198621.4587 | 2644075.0116 | 1198613.6611 | 2644058.2766 | 1198594.8973
105 | 2643991.6954 | 1198531.2461 | 2644013.4129 | 1198550.928 | 2644044.6811 | 1198579.652 | 2644058.064 | 1198594.6589 | 2644058.2766 | 1198594.8973
106 | 2643991.6954 | 1198531.2461 | 2643988.3833 | 1198535.3352 | 2643983.8647 | 1198540.9273 | 2643980.019 | 1198543.0224 | 2643976.1803 | 1198544.1615 | 2643970.4306 | 1198544.2304 | 2643944.0617 | 1198539.8898 | 2643923.2193 | 1198535.8123 | 2643914.6224 | 1198532.6696 | 2643911.0878 | 1198530.8066
107 | 2644152.0166 | 1198455.2844 | 2644149.3382 | 1198459.1224 | 2644148.1015 | 1198461.6914
108 | 2644142.8961 | 1198472.5046 | 2644148.1015 | 1198461.6914
109 | 2643889.1647 | 1198304.3123 | 2643904.3345 | 1198270.2804 | 2643907.1176 | 1198266.6877 | 2643910.7408 | 1198263.8015 | 2643915.8372 | 1198261.4709 | 2643919.6188 | 1198260.865 | 2643927.3561 | 1198260.9952
110 | 2643846.6809 | 1198388.5239 | 2643871.8869 | 1198341.7936 | 2643880.2006 | 1198324.4226 | 2643889.1647 | 1198304.3123
111 | 2643931.3525 | 1198261.0624 | 2643927.3561 | 1198260.9952
112 | 2643894.4949 | 1198519.37 | 2643846.6809 | 1198388.5239
113 | 2643931.3525 | 1198261.0624 | 2643934.5526 | 1198267.0448 | 2643940.6839 | 1198275.1944
114 | 2643894.4949 | 1198519.37 | 2643906.6652 | 1198528.4755 | 2643911.0878 | 1198530.8066
115 | 2643940.6839 | 1198275.1944 | 2643940.6839 | 1198275.1944 | 2643949.7739 | 1198283.8327 | 2643959.7038 | 1198290.7334

## bus_geodata
| x | y | coords
0 | 2643810.8798 | 1199998.8213
1 | 2643830.5921 | 1200023.9477
2 | 2643787.5089 | 1199969.2784
3 | 2643769.8744 | 1199925.9694
4 | 2643744.5253 | 1199917.2963
5 | 2643786.9316 | 1199900.3592
6 | 2643937.9994 | 1200058.9324
7 | 2643982.8643 | 1200020.396
8 | 2643903.2463 | 1200023.9711
9 | 2643718.8505 | 1199893.0222
10 | 2643816.2654 | 1199896.6379
11 | 2644008.5689 | 1199957.9165
12 | 2643954.6937 | 1199988.8614
13 | 2643898.7812 | 1200019.5077
14 | 2643885.9458 | 1200006.8095
15 | 2643879.1882 | 1200000.1242
16 | 2643846.9965 | 1199970.4259
17 | 2644047.1054 | 1199959.0564
18 | 2644018.8359 | 1199923.1725
19 | 2643982.455 | 1199975.2295
20 | 2644003.0599 | 1199951.0238
21 | 2643944.9425 | 1199977.9457
22 | 2643850.9315 | 1199956.3915
23 | 2643845.8598 | 1199969.6278
24 | 2643867.706 | 1199932.801
25 | 2643830.8635 | 1199959.1347
26 | 2643881.1996 | 1199942.7278
27 | 2643858.6768 | 1199921.3951
28 | 2643798.7766 | 1199943.3032
29 | 2643930.3111 | 1199961.5672
30 | 2643934.0095 | 1199965.7072
31 | 2643818.9755 | 1199897.3572
32 | 2643885.1163 | 1199902.4274
33 | 2643828.487 | 1199885.2432
34 | 2643908.5159 | 1199885.6406
35 | 2643654.9337 | 1199816.4655
36 | 2643807.8514 | 1199840.1094
37 | 2643831.507 | 1199848.9794
38 | 2643769.7899 | 1199795.5687
39 | 2643852.5772 | 1199853.0897
40 | 2643850.003 | 1199857.8398
41 | 2643854.4512 | 1199837.8366
42 | 2643777.8065 | 1199692.1403
43 | 2643774.8622 | 1199528.5935
44 | 2643826.3407 | 1199766.8688
45 | 2643834.4898 | 1199877.5978
46 | 2643854.5887 | 1199835.7051
47 | 2643829.3328 | 1199557.5691
48 | 2643825.6543 | 1199782.8306
49 | 2643853.7925 | 1199821.0043
50 | 2643844.278 | 1199797.1418
51 | 2643840.2579 | 1199787.8404
52 | 2643836.4411 | 1199805.4893
53 | 2644000.3933 | 1199947.6873
54 | 2643981.6981 | 1199826.8023
55 | 2643996.7095 | 1199812.3518
56 | 2643989.7335 | 1199934.3499
57 | 2643986.2775 | 1199930.0257
58 | 2643825.0188 | 1199822.7818
59 | 2643816.5049 | 1199795.5962
60 | 2643970.9507 | 1199618.6098
61 | 2643965.9397 | 1199610.1481
62 | 2643950.8405 | 1199607.9454
63 | 2644191.2609 | 1199314.9904
64 | 2644159.9652 | 1199268.122
65 | 2644156.3547 | 1199251.6415
66 | 2644154.4746 | 1199241.2551
67 | 2643965.1813 | 1199173.2005
68 | 2644499.4239 | 1199172.4635
69 | 2644519.482 | 1199197.8664
70 | 2644491.5159 | 1199159.295
71 | 2644463.6157 | 1198866.5354
72 | 2644451.2384 | 1198853.935
73 | 2644451.8221 | 1198620.7528
74 | 2644222.6053 | 1198788.3833
75 | 2644130.9152 | 1198667.8706
76 | 2644394.659 | 1198585.1586
77 | 2644218.5691 | 1198520.4903
78 | 2643809.7412 | 1199811.0633
79 | 2643854.9191 | 1198914.0574
80 | 2643790.1305 | 1198969.9136
81 | 2643854.9375 | 1199024.7302
82 | 2643724.651 | 1198862.1708
83 | 2643906.0133 | 1199076.6562
84 | 2643966.9217 | 1198984.7465
85 | 2643724.9669 | 1198838.7412
86 | 2643974.3812 | 1198956.5353
87 | 2644026.2426 | 1198739.8963
88 | 2643931.1883 | 1199109.5716
89 | 2643892.5497 | 1199167.4589
90 | 2643890.4612 | 1199167.4076
91 | 2643940.0737 | 1199122.9878
92 | 2644143.4438 | 1198364.8589
93 | 2644143.5182 | 1198365.908
94 | 2644141.1062 | 1198346.6986
95 | 2644159.5334 | 1198386.0789
96 | 2643968.5249 | 1198335.2881
97 | 2644211.309 | 1198457.0455
98 | 2643709.1359 | 1198841.7363
99 | 2644144.7873 | 1198655.7904
100 | 2644122.8787 | 1198673.4266
101 | 2644095.9477 | 1198689.658
102 | 2644050.8794 | 1198726.6248
103 | 2644058.2766 | 1198594.8973
104 | 2643991.6954 | 1198531.2461
105 | 2644200.0756 | 1198485.7078
106 | 2644152.0166 | 1198455.2844
107 | 2644148.1015 | 1198461.6914
108 | 2644142.8961 | 1198472.5046
109 | 2643889.1647 | 1198304.3123
110 | 2643927.3561 | 1198260.9952
111 | 2643846.6809 | 1198388.5239
112 | 2643931.3525 | 1198261.0624
113 | 2643894.4949 | 1198519.37
114 | 2643940.6839 | 1198275.1944
115 | 2643959.7038 | 1198290.7334
116 | 2643911.0878 | 1198530.8066
117 | 2643825.6543 | 1199782.8306

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9834 | -0.11625 | 0.022372 | 0.005607
1 | 0.98317 | -0.11789 | 0.004972 | 0.0012461
2 | 0.98489 | -0.10564 | 0 | 0
3 | 0.98681 | -0.092051 | 0 | 0
4 | 0.98656 | -0.093852 | 0.0011602 | 0.00029078
5 | 0.98836 | -0.081071 | 0.0035465 | 0.00088885
6 | 0.9757 | -0.17095 | 0 | 0
7 | 0.97421 | -0.18162 | 0 | 0
8 | 0.97693 | -0.16208 | 0.0064824 | 0.0016246
9 | 0.98628 | -0.095821 | 0.0022022 | 0.00055192
10 | 0.99001 | -0.069445 | 0.0071248 | 0.0017857
11 | 0.97256 | -0.19347 | 0 | 0
12 | 0.97396 | -0.18344 | 0.00073612 | 0.00018449
13 | 0.97715 | -0.16052 | 0.011764 | 0.0029482
14 | 0.97809 | -0.15384 | 0.0063854 | 0.0016003
15 | 0.97867 | -0.14969 | 0.013934 | 0.0034922
16 | 0.98223 | -0.12433 | 0 | 0
17 | 0.97204 | -0.19721 | 0 | 0
18 | 0.97162 | -0.20027 | 0.0063542 | 0.0015925
19 | 0.97251 | -0.19383 | 0.0010614 | 0.000266
20 | 0.97249 | -0.194 | 0.0029138 | 0.00073026
21 | 0.97388 | -0.18396 | 0.00087321 | 0.00021885
22 | 0.9838 | -0.11322 | 0.0071179 | 0.0017839
23 | 0.9822 | -0.12458 | 0.0068355 | 0.0017131
24 | 0.98559 | -0.10058 | 0 | 0
25 | 0.9819 | -0.1267 | 0 | 0
26 | 0.98515 | -0.10368 | 0.017341 | 0.004346
27 | 0.98663 | -0.093252 | 0 | 0
28 | 0.98132 | -0.13083 | 0.011146 | 0.0027934
29 | 0.97381 | -0.18447 | 0.0012438 | 0.00031174
30 | 0.97382 | -0.18439 | 0.0012466 | 0.00031243
31 | 0.99019 | -0.068172 | 0 | 0
32 | 0.98546 | -0.1015 | 0.012233 | 0.0030658
33 | 0.99144 | -0.059429 | 0.0017579 | 0.00044057
34 | 0.98494 | -0.10518 | 0 | 0
35 | 0.98582 | -0.099072 | 0.0031699 | 0.00079445
36 | 0.99442 | -0.0387 | 0.0034024 | 0.00085271
37 | 0.99456 | -0.037703 | 0.0033248 | 0.00083327
38 | 0.99437 | -0.039029 | 0.00048601 | 0.00012181
39 | 0.99478 | -0.036137 | 0 | 0
40 | 0.99432 | -0.039319 | 0.003261 | 0.00081729
41 | 0.99613 | -0.026732 | 0.0019631 | 0.000492
42 | 0.9981 | -0.013518 | 0 | 0
43 | 0.99574 | -0.030326 | 0 | 0
44 | 0.99937 | -0.004488 | 0.00078282 | 0.00019619
45 | 0.99224 | -0.053865 | 0.0024577 | 0.00061597
46 | 0.99632 | -0.025413 | 0.0021623 | 0.00054192
47 | 0.99488 | -0.03652 | 0.0012093 | 0.00030309
48 | 0.9996 | -0.0028592 | 0 | 0
49 | 0.99766 | -0.016172 | 0.0021569 | 0.00054057
50 | 1 | 0 | -0.22902 | -0.057538
51 | 0.99984 | -0.0011675 | 0.0024345 | 0.00061013
52 | 0.99996 | -0.00029371 | 0.00086738 | 0.00021738
53 | 0.97247 | -0.19412 | 0.0010815 | 0.00027105
54 | 0.98325 | -0.11723 | 0.0026078 | 0.00065358
55 | 0.98295 | -0.11935 | 0.009828 | 0.0024631
56 | 0.97243 | -0.19442 | 0.00091391 | 0.00022905
57 | 0.97243 | -0.19446 | 0.00072531 | 0.00018178
58 | 0.99991 | -0.00063524 | 0.0016499 | 0.00041351
59 | 0.99956 | -0.0031161 | 0.00090176 | 0.000226
60 | 0.99283 | -0.051228 | 0.0021091 | 0.00052858
61 | 0.99286 | -0.051009 | 0.00050767 | 0.00012723
62 | 0.99306 | -0.049573 | 0.0011977 | 0.00030016
63 | 0.98856 | -0.081987 | 0 | 0
64 | 0.9879 | -0.086805 | 0.00062353 | 0.00015627
65 | 0.9877 | -0.088186 | 0 | 0
66 | 0.98759 | -0.089047 | 0.00041177 | 0.0001032
67 | 0.98536 | -0.10519 | 0 | 0
68 | 0.97123 | -0.20849 | 0.00084577 | 0.00021197
69 | 0.97121 | -0.20863 | 0.000369 | 9.2481e-05
70 | 0.97126 | -0.2083 | 0 | 0
71 | 0.97178 | -0.20446 | 0.00084726 | 0.00021234
72 | 0.97183 | -0.20406 | 0 | 0
73 | 0.97254 | -0.19888 | 0 | 0
74 | 0.97912 | -0.15065 | 0.00021981 | 5.509e-05
75 | 0.97917 | -0.1503 | 0.00020309 | 5.09e-05
76 | 0.97278 | -0.1971 | 0.00016688 | 4.1824e-05
77 | 0.97308 | -0.19482 | 0.00087405 | 0.00021906
78 | 0.99954 | -0.0032283 | 0.00066442 | 0.00016652
79 | 0.98333 | -0.11996 | 0.00024433 | 6.1236e-05
80 | 0.98336 | -0.11973 | 0 | 0
81 | 0.98352 | -0.11857 | 0 | 0
82 | 0.98315 | -0.12123 | 0.0003809 | 9.5462e-05
83 | 0.98423 | -0.11337 | 0 | 0
84 | 0.98229 | -0.12754 | 0.0006846 | 0.00017158
85 | 0.98313 | -0.12139 | 0 | 0
86 | 0.98191 | -0.13028 | 0.00026959 | 6.7565e-05
87 | 0.97997 | -0.14445 | 0.00035464 | 8.8882e-05
88 | 0.98464 | -0.11041 | 0.00019884 | 4.9833e-05
89 | 0.9851 | -0.10701 | 0.0014577 | 0.00036533
90 | 0.9851 | -0.10703 | 0.0009631 | 0.00024137
91 | 0.9848 | -0.10925 | 0 | 0
92 | 0.97356 | -0.19127 | 0.00074886 | 0.00018768
93 | 0.97356 | -0.1913 | 0.00047817 | 0.00011984
94 | 0.97363 | -0.1908 | 0 | 0
95 | 0.97348 | -0.19192 | 0 | 0
96 | 0.97423 | -0.18634 | 0.0020164 | 0.00050537
97 | 0.97321 | -0.19388 | 0 | 0
98 | 0.98311 | -0.12151 | 0.00067689 | 0.00016964
99 | 0.97916 | -0.15035 | 0.00027107 | 6.7937e-05
100 | 0.97918 | -0.15022 | 0.00010997 | 2.7562e-05
101 | 0.97921 | -0.14995 | 0 | 0
102 | 0.97973 | -0.14619 | 0.00022048 | 5.5258e-05
103 | 0.97837 | -0.15611 | 0.00044843 | 0.00011239
104 | 0.97765 | -0.16138 | 0 | 0
105 | 0.97315 | -0.19431 | 0.00066542 | 0.00016677
106 | 0.97302 | -0.19524 | 0 | 0
107 | 0.973 | -0.19542 | 0.0015291 | 0.00038323
108 | 0.97299 | -0.1955 | 0.00063612 | 0.00015943
109 | 0.97513 | -0.17978 | 0.0012095 | 0.00030313
110 | 0.97471 | -0.18284 | 0.00080913 | 0.00020279
111 | 0.97581 | -0.17483 | 0 | 0
112 | 0.97468 | -0.18302 | 0 | 0
113 | 0.97681 | -0.16752 | 0.0008603 | 0.00021561
114 | 0.97458 | -0.18379 | 0.00249 | 0.00062406
115 | 0.97446 | -0.18469 | 0.0010448 | 0.00026186
116 | 0.97696 | -0.1664 | 0.00048829 | 0.00012238
117 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0049731 | 0.0012461 | -0.004972 | -0.0012461 | 1.1285e-06 | 2.8925e-08 | 0.0075249 | 0.007525 | 0.007525 | 0.9834 | -0.11625 | 0.98317 | -0.11789 | 2.7871
1 | -0.027345 | -0.0068531 | 0.027385 | 0.0068681 | 4.0242e-05 | 1.4999e-05 | 0.041377 | 0.041377 | 0.041377 | 0.9834 | -0.11625 | 0.98489 | -0.10564 | 15.3247
2 | -0.027385 | -0.0068681 | 0.027437 | 0.0068873 | 5.1672e-05 | 1.9257e-05 | 0.041377 | 0.041376 | 0.041377 | 0.98489 | -0.10564 | 0.98681 | -0.092051 | 15.3247
3 | 0.0065368 | 0.0016368 | -0.0065352 | -0.0016365 | 1.6266e-06 | 2.8291e-07 | 0.0098563 | 0.0098565 | 0.0098565 | 0.98681 | -0.092051 | 0.98656 | -0.093852 | 3.6505
4 | -0.033974 | -0.0085242 | 0.034026 | 0.0085437 | 5.1836e-05 | 1.9532e-05 | 0.051233 | 0.051233 | 0.051233 | 0.98681 | -0.092051 | 0.98836 | -0.081071 | 18.9751
5 | 0.005375 | 0.0013457 | -0.0053735 | -0.0013456 | 1.4629e-06 | 1.0726e-07 | 0.0081065 | 0.0081067 | 0.0081067 | 0.98656 | -0.093852 | 0.98628 | -0.095821 | 3.0025
6 | -0.037572 | -0.0094325 | 0.037633 | 0.0094555 | 6.0778e-05 | 2.2985e-05 | 0.056572 | 0.056572 | 0.056572 | 0.98836 | -0.081071 | 0.99001 | -0.069445 | 20.9526
7 | 0.017205 | 0.0043144 | -0.017179 | -0.0043053 | 2.54e-05 | 9.0321e-06 | 0.026239 | 0.02624 | 0.02624 | 0.9757 | -0.17095 | 0.97421 | -0.18162 | 9.7184
8 | -0.017205 | -0.0043144 | 0.017226 | 0.0043219 | 2.1179e-05 | 7.5293e-06 | 0.026239 | 0.026239 | 0.026239 | 0.9757 | -0.17095 | 0.97693 | -0.16208 | 9.7183
9 | 0.013078 | 0.0032783 | -0.013057 | -0.0032711 | 2.1444e-05 | 7.1773e-06 | 0.019976 | 0.019976 | 0.019976 | 0.97421 | -0.18162 | 0.97256 | -0.19347 | 7.3986
10 | 0.0041012 | 0.0010271 | -0.0041002 | -0.0010272 | 1.0353e-06 | -1.2816e-07 | 0.0062639 | 0.0062641 | 0.0062641 | 0.97421 | -0.18162 | 0.97396 | -0.18344 | 2.32
11 | -0.023708 | -0.0059465 | 0.023713 | 0.0059484 | 5.1379e-06 | 1.897e-06 | 0.036113 | 0.036113 | 0.036113 | 0.97693 | -0.16208 | 0.97715 | -0.16052 | 13.3751
12 | 0.0031713 | 0.00079372 | -0.0031699 | -0.00079445 | 1.4247e-06 | -7.2435e-07 | 0.0047842 | 0.0047847 | 0.0047847 | 0.98628 | -0.095821 | 0.98582 | -0.099072 | 1.7721
13 | -0.044758 | -0.011241 | 0.044766 | 0.011244 | 7.9201e-06 | 3.0101e-06 | 0.067281 | 0.067281 | 0.067281 | 0.99001 | -0.069445 | 0.99019 | -0.068172 | 24.9188
14 | 0.0010614 | 0.00026564 | -0.0010614 | -0.000266 | 5.1557e-08 | -3.6895e-07 | 0.0016238 | 0.001624 | 0.001624 | 0.97256 | -0.19347 | 0.97251 | -0.19383 | 0.60147
15 | 0.005635 | 0.0014119 | -0.0056346 | -0.0014118 | 4.0925e-07 | 4.7918e-08 | 0.0086214 | 0.0086214 | 0.0086214 | 0.97256 | -0.19347 | 0.97249 | -0.194 | 3.1931
16 | 0.0063602 | 0.0015936 | -0.0063569 | -0.001593 | 3.2833e-06 | 5.7366e-07 | 0.0097309 | 0.0097312 | 0.0097312 | 0.97256 | -0.19347 | 0.97204 | -0.19721 | 3.6041
17 | 0.0033641 | 0.00084271 | -0.0033638 | -0.0008428 | 2.4126e-07 | -8.9349e-08 | 0.0051395 | 0.0051395 | 0.0051395 | 0.97396 | -0.18344 | 0.97388 | -0.18396 | 1.9035
18 | -0.035477 | -0.0088967 | 0.03551 | 0.0089091 | 3.2885e-05 | 1.2422e-05 | 0.054026 | 0.054026 | 0.054026 | 0.97715 | -0.16052 | 0.97809 | -0.15384 | 20.0098
19 | -0.041895 | -0.010509 | 0.041919 | 0.010519 | 2.4099e-05 | 9.1495e-06 | 0.063741 | 0.063741 | 0.063741 | 0.97809 | -0.15384 | 0.97867 | -0.14969 | 23.6077
20 | -0.055853 | -0.014011 | 0.056051 | 0.014086 | 0.00019719 | 7.5288e-05 | 0.084927 | 0.084927 | 0.084927 | 0.97867 | -0.14969 | 0.98223 | -0.12433 | 31.4544
21 | -0.074042 | -0.018596 | 0.074157 | 0.01864 | 0.00011446 | 4.384e-05 | 0.11218 | 0.11218 | 0.11218 | 0.98223 | -0.12433 | 0.9838 | -0.11322 | 41.5493
22 | 0.017992 | 0.0045098 | -0.017991 | -0.0045096 | 6.4388e-07 | 2.3007e-07 | 0.027256 | 0.027256 | 0.027256 | 0.98223 | -0.12433 | 0.9822 | -0.12458 | 10.095
23 | 0.0063569 | 0.001593 | -0.0063542 | -0.0015925 | 2.6967e-06 | 4.7174e-07 | 0.0097312 | 0.0097314 | 0.0097314 | 0.97204 | -0.19721 | 0.97162 | -0.20027 | 3.6042
24 | 0.0027208 | 0.00068158 | -0.0027208 | -0.00068162 | 4.6191e-08 | -3.5228e-08 | 0.004163 | 0.0041631 | 0.0041631 | 0.97249 | -0.194 | 0.97247 | -0.19412 | 1.5419
25 | 0.0024906 | 0.00062395 | -0.0024905 | -0.0006241 | 1.4829e-07 | -1.4715e-07 | 0.0038054 | 0.0038054 | 0.0038054 | 0.97388 | -0.18396 | 0.97382 | -0.18439 | 1.4094
26 | -0.081275 | -0.020424 | 0.081418 | 0.020478 | 0.00014329 | 5.434e-05 | 0.12295 | 0.12295 | 0.12295 | 0.9838 | -0.11322 | 0.98559 | -0.10058 | 22.7683
27 | 0.011155 | 0.0027964 | -0.011152 | -0.0027954 | 3.2622e-06 | 1.0231e-06 | 0.016901 | 0.016901 | 0.016901 | 0.9822 | -0.12458 | 0.9819 | -0.1267 | 6.2595
28 | 0.017348 | 0.0043486 | -0.017341 | -0.004346 | 7.44e-06 | 2.6401e-06 | 0.026192 | 0.026192 | 0.026192 | 0.98559 | -0.10058 | 0.98515 | -0.10368 | 9.7007
29 | -0.098766 | -0.024827 | 0.098867 | 0.024865 | 0.00010086 | 3.842e-05 | 0.14914 | 0.14914 | 0.14914 | 0.98559 | -0.10058 | 0.98663 | -0.093252 | 27.6187
30 | 0.011152 | 0.0027954 | -0.011146 | -0.0027934 | 6.3862e-06 | 2.0033e-06 | 0.016901 | 0.016901 | 0.016901 | 0.9819 | -0.1267 | 0.98132 | -0.13083 | 6.2596
31 | -0.12359 | -0.031068 | 0.12403 | 0.031232 | 0.00043321 | 0.00016431 | 0.18643 | 0.18643 | 0.18643 | 0.98663 | -0.093252 | 0.99019 | -0.068172 | 23.0167
32 | 0.024727 | 0.0062026 | -0.024698 | -0.0061922 | 2.8241e-05 | 1.0447e-05 | 0.037294 | 0.037295 | 0.037295 | 0.98663 | -0.093252 | 0.98546 | -0.1015 | 13.8128
33 | -0.0012438 | -0.00031174 | 0.0012439 | 0.00031167 | 1.2514e-08 | -6.4254e-08 | 0.0019006 | 0.0019006 | 0.0019006 | 0.97381 | -0.18447 | 0.97382 | -0.18439 | 0.70394
34 | -0.16879 | -0.042476 | 0.169 | 0.042555 | 0.00020622 | 7.872e-05 | 0.25371 | 0.25371 | 0.25371 | 0.99019 | -0.068172 | 0.99144 | -0.059429 | 31.3228
35 | 0.012466 | 0.0031264 | -0.012459 | -0.0031243 | 6.3674e-06 | 2.0823e-06 | 0.018824 | 0.018824 | 0.018824 | 0.98546 | -0.1015 | 0.98494 | -0.10518 | 6.9718
36 | -0.17076 | -0.042995 | 0.17089 | 0.043046 | 0.00013287 | 5.0727e-05 | 0.25635 | 0.25635 | 0.25635 | 0.99144 | -0.059429 | 0.99224 | -0.053865 | 31.6485
37 | 0.012459 | 0.0031243 | -0.012439 | -0.0031175 | 2.0771e-05 | 6.7954e-06 | 0.018824 | 0.018824 | 0.018824 | 0.98494 | -0.10518 | 0.98325 | -0.11723 | 6.972
38 | -0.0038884 | -0.00097366 | 0.0038889 | 0.00097354 | 5.3566e-07 | -1.2302e-07 | 0.0058182 | 0.0058181 | 0.0058182 | 0.99442 | -0.0387 | 0.99456 | -0.037703 | 2.1549
39 | 0.00048603 | 0.00012095 | -0.00048601 | -0.00012181 | 2.1942e-08 | -8.5431e-07 | 0.00072698 | 0.00072728 | 0.00072728 | 0.99442 | -0.0387 | 0.99437 | -0.039029 | 0.26936
40 | -0.0072137 | -0.0018068 | 0.0072153 | 0.0018071 | 1.5626e-06 | 3.2195e-07 | 0.010792 | 0.010792 | 0.010792 | 0.99456 | -0.037703 | 0.99478 | -0.036137 | 3.9972
41 | 0.17704 | 0.044644 | -0.17696 | -0.044614 | 7.893e-05 | 3.0147e-05 | 0.26492 | 0.26492 | 0.26492 | 0.99478 | -0.036137 | 0.99432 | -0.039319 | 32.706
42 | -0.18426 | -0.046452 | 0.1845 | 0.046545 | 0.00024308 | 9.2892e-05 | 0.27571 | 0.27571 | 0.27571 | 0.99478 | -0.036137 | 0.99613 | -0.026732 | 34.0384
43 | 0.1737 | 0.043797 | -0.17335 | -0.043662 | 0.00035332 | 0.00013492 | 0.26004 | 0.26004 | 0.26004 | 0.99432 | -0.039319 | 0.99224 | -0.053865 | 32.1035
44 | -0.18646 | -0.047037 | 0.1865 | 0.04705 | 3.4495e-05 | 1.3184e-05 | 0.27864 | 0.27864 | 0.27864 | 0.99613 | -0.026732 | 0.99632 | -0.025413 | 34.4004
45 | 0.029364 | 0.0073005 | -0.029297 | -0.0072813 | 6.7159e-05 | 1.9234e-05 | 0.043757 | 0.043759 | 0.043759 | 0.9981 | -0.013518 | 0.99574 | -0.030326 | 5.4023
46 | -0.029364 | -0.0073005 | 0.0294 | 0.0073109 | 3.6163e-05 | 1.0344e-05 | 0.043757 | 0.043755 | 0.043757 | 0.9981 | -0.013518 | 0.99937 | -0.004488 | 5.4021
47 | 0.029297 | 0.0072813 | -0.029272 | -0.0072742 | 2.4698e-05 | 7.0815e-06 | 0.043759 | 0.04376 | 0.04376 | 0.99574 | -0.030326 | 0.99488 | -0.03652 | 5.4024
48 | -0.030183 | -0.0075071 | 0.03019 | 0.007509 | 6.7057e-06 | 1.951e-06 | 0.044921 | 0.044921 | 0.044921 | 0.99937 | -0.004488 | 0.9996 | -0.0028592 | 5.5458
49 | -0.18866 | -0.047592 | 0.1889 | 0.047685 | 0.00024484 | 9.359e-05 | 0.28187 | 0.28187 | 0.28187 | 0.99632 | -0.025413 | 0.99766 | -0.016172 | 34.7991
50 | 0.028063 | 0.0069711 | -0.028013 | -0.0069573 | 4.9781e-05 | 1.3859e-05 | 0.041951 | 0.041953 | 0.041953 | 0.99488 | -0.03652 | 0.99306 | -0.049573 | 5.1794
51 | 0.0015663 | 0.00039211 | -0.0015662 | -0.00039231 | 5.5618e-08 | -1.9355e-07 | 0.0023314 | 0.0023315 | 0.0023315 | 0.9996 | -0.0028592 | 0.99956 | -0.0031161 | 0.86351
52 | -0.031756 | -0.0079011 | 0.031763 | 0.0079033 | 7.3326e-06 | 2.1992e-06 | 0.047252 | 0.047252 | 0.047252 | 0.9996 | -0.0028592 | 0.99984 | -0.0011675 | 5.8336
53 | -0.19106 | -0.048226 | 0.1915 | 0.048392 | 0.00043492 | 0.00016627 | 0.28509 | 0.28509 | 0.28509 | 0.99766 | -0.016172 | 1 | 0 | 35.1962
54 | 0.034203 | 0.0085152 | -0.034198 | -0.0085135 | 5.4552e-06 | 1.6994e-06 | 0.050875 | 0.050875 | 0.050875 | 1 | 0 | 0.99984 | -0.0011675 | 6.2809
55 | 0.0025175 | 0.00063054 | -0.0025174 | -0.00063066 | 1.0226e-07 | -1.1387e-07 | 0.0037459 | 0.003746 | 0.003746 | 1 | 0 | 0.99996 | -0.00029371 | 1.3874
56 | 0.00165 | 0.00041327 | -0.0016499 | -0.00041351 | 7.7962e-08 | -2.4187e-07 | 0.0024553 | 0.0024554 | 0.0024554 | 0.99996 | -0.00029371 | 0.99991 | -0.00063524 | 0.90939
57 | 0.0016393 | 0.00041057 | -0.0016392 | -0.00041076 | 6.703e-08 | -1.8604e-07 | 0.0025082 | 0.0025083 | 0.0025083 | 0.97247 | -0.19412 | 0.97243 | -0.19442 | 0.92901
58 | 0.0098309 | 0.002464 | -0.009828 | -0.0024631 | 2.8826e-06 | 8.4406e-07 | 0.014878 | 0.014878 | 0.014878 | 0.98325 | -0.11723 | 0.98295 | -0.11935 | 5.5103
59 | 0.00072531 | 0.00018171 | -0.00072531 | -0.00018178 | 4.2549e-09 | -6.7037e-08 | 0.0011099 | 0.0011099 | 0.0011099 | 0.97243 | -0.19442 | 0.97243 | -0.19446 | 0.41107
60 | 0.00066443 | 0.0001663 | -0.00066442 | -0.00016652 | 1.0305e-08 | -2.1731e-07 | 0.00098904 | 0.00098912 | 0.00098912 | 0.99956 | -0.0031161 | 0.99954 | -0.0032283 | 0.36634
61 | -0.0021091 | -0.00052858 | 0.0021091 | 0.00052848 | 6.4138e-08 | -1.0836e-07 | 0.003161 | 0.003161 | 0.003161 | 0.99283 | -0.051228 | 0.99286 | -0.051009 | 1.1707
62 | -0.02681 | -0.0066557 | 0.026815 | 0.0066571 | 5.2294e-06 | 1.4063e-06 | 0.040158 | 0.040158 | 0.040158 | 0.99286 | -0.051009 | 0.99306 | -0.049573 | 4.9578
63 | 0.024193 | 0.006 | -0.024092 | -0.0059753 | 0.00010143 | 2.4668e-05 | 0.036237 | 0.036242 | 0.036242 | 0.99286 | -0.051009 | 0.98856 | -0.081987 | 4.4743
64 | 0.024092 | 0.0059753 | -0.024076 | -0.0059715 | 1.5739e-05 | 3.8392e-06 | 0.036242 | 0.036242 | 0.036242 | 0.98856 | -0.081987 | 0.9879 | -0.086805 | 4.4744
65 | 0.023453 | 0.0058152 | -0.023448 | -0.0058142 | 4.3915e-06 | 1.0385e-06 | 0.035303 | 0.035304 | 0.035304 | 0.9879 | -0.086805 | 0.9877 | -0.088186 | 4.3585
66 | 0.023448 | 0.0058142 | -0.023445 | -0.0058135 | 2.7365e-06 | 6.4725e-07 | 0.035304 | 0.035304 | 0.035304 | 0.9877 | -0.088186 | 0.98759 | -0.089047 | 4.3585
67 | 0.023034 | 0.0057103 | -0.022983 | -0.0056987 | 5.0335e-05 | 1.1655e-05 | 0.034683 | 0.034686 | 0.034686 | 0.98759 | -0.089047 | 0.98536 | -0.10519 | 4.2822
68 | 0.020562 | 0.0050927 | -0.020551 | -0.0050905 | 1.1287e-05 | 2.1887e-06 | 0.03103 | 0.03103 | 0.03103 | 0.98536 | -0.10519 | 0.9848 | -0.10925 | 3.8309
69 | 0.0024214 | 0.00060598 | -0.0024208 | -0.00060668 | 6.0934e-07 | -6.9575e-07 | 0.0036563 | 0.0036566 | 0.0036566 | 0.98536 | -0.10519 | 0.9851 | -0.10701 | 1.3543
70 | 0.00036901 | 9.2053e-05 | -0.000369 | -9.2481e-05 | 6.9405e-09 | -4.2807e-07 | 0.00056521 | 0.00056536 | 0.00056536 | 0.97123 | -0.20849 | 0.97121 | -0.20863 | 0.20939
71 | -0.0012148 | -0.00030402 | 0.0012148 | 0.00030385 | 3.3253e-08 | -1.7764e-07 | 0.001861 | 0.0018609 | 0.001861 | 0.97123 | -0.20849 | 0.97126 | -0.2083 | 0.68926
72 | -0.0012148 | -0.00030385 | 0.0012155 | 0.00030045 | 6.3507e-07 | -3.3973e-06 | 0.0018609 | 0.0018596 | 0.0018609 | 0.97126 | -0.2083 | 0.97178 | -0.20446 | 0.68924
73 | -0.0020627 | -0.00051279 | 0.0020628 | 0.00051261 | 1.1199e-07 | -1.8004e-07 | 0.003157 | 0.0031569 | 0.003157 | 0.97178 | -0.20446 | 0.97183 | -0.20406 | 1.1693
74 | -0.0020628 | -0.00051261 | 0.0020643 | 0.00051028 | 1.4496e-06 | -2.3338e-06 | 0.0031569 | 0.0031559 | 0.0031569 | 0.97183 | -0.20406 | 0.97254 | -0.19888 | 1.1692
75 | -0.0020643 | -0.00051028 | 0.0020648 | 0.00050948 | 4.9378e-07 | -7.9634e-07 | 0.0031559 | 0.0031555 | 0.0031559 | 0.97254 | -0.19888 | 0.97278 | -0.1971 | 1.1688
76 | -0.00021981 | -5.509e-05 | 0.00021982 | 5.3189e-05 | 1.0523e-08 | -1.9006e-06 | 0.00033406 | 0.00033339 | 0.00033406 | 0.97912 | -0.15065 | 0.97917 | -0.1503 | 0.12372
77 | -0.00069399 | -0.00017179 | 0.00069399 | 0.00017167 | 6.7708e-09 | -1.2029e-07 | 0.0010539 | 0.0010538 | 0.0010539 | 0.97917 | -0.1503 | 0.97918 | -0.15022 | 0.39032
78 | 0.00027107 | 6.7706e-05 | -0.00027107 | -6.7937e-05 | 1.9515e-09 | -2.311e-07 | 0.00041186 | 0.00041194 | 0.00041194 | 0.97917 | -0.1503 | 0.97916 | -0.15035 | 0.15257
79 | -0.0022316 | -0.00055131 | 0.0022323 | 0.00054691 | 6.8055e-07 | -4.3975e-06 | 0.0034108 | 0.0034091 | 0.0034108 | 0.97278 | -0.1971 | 0.97308 | -0.19482 | 0.63163
80 | -0.0031064 | -0.00076596 | 0.0031066 | 0.00076436 | 2.1177e-07 | -1.6036e-06 | 0.0047457 | 0.0047451 | 0.0047457 | 0.97308 | -0.19482 | 0.97315 | -0.19431 | 0.58589
81 | -0.00024433 | -6.1236e-05 | 0.00024434 | 6.0125e-05 | 7.4828e-09 | -1.1111e-06 | 0.00036974 | 0.00036934 | 0.00036974 | 0.98333 | -0.11996 | 0.98336 | -0.11973 | 0.13694
82 | -0.0013024 | -0.0003231 | 0.0013026 | 0.0003221 | 2.0509e-07 | -9.9637e-07 | 0.0019696 | 0.0019692 | 0.0019696 | 0.98336 | -0.11973 | 0.98352 | -0.11857 | 0.72947
83 | 0.001058 | 0.00026297 | -0.0010578 | -0.00026461 | 2.1702e-07 | -1.6386e-06 | 0.0016002 | 0.0016008 | 0.0016008 | 0.98336 | -0.11973 | 0.98315 | -0.12123 | 0.5929
84 | -0.020326 | -0.0050358 | 0.02034 | 0.0050385 | 1.4315e-05 | 2.7294e-06 | 0.030732 | 0.030731 | 0.030732 | 0.98352 | -0.11857 | 0.98423 | -0.11337 | 3.794
85 | 0.019024 | 0.0047137 | -0.019 | -0.0047099 | 2.3103e-05 | 3.7809e-06 | 0.028762 | 0.028764 | 0.028764 | 0.98352 | -0.11857 | 0.98229 | -0.12754 | 3.5511
86 | 0.00067691 | 0.00016915 | -0.0006769 | -0.00016944 | 1.5343e-08 | -2.9123e-07 | 0.0010243 | 0.0010244 | 0.0010244 | 0.98315 | -0.12123 | 0.98313 | -0.12139 | 0.37943
87 | -0.02034 | -0.0050385 | 0.020349 | 0.00504 | 8.1519e-06 | 1.5524e-06 | 0.030731 | 0.03073 | 0.030731 | 0.98423 | -0.11337 | 0.98464 | -0.11041 | 3.7939
88 | 0.018316 | 0.0045383 | -0.018309 | -0.0045373 | 6.7908e-06 | 9.998e-07 | 0.027727 | 0.027728 | 0.027728 | 0.98229 | -0.12754 | 0.98191 | -0.13028 | 3.4232
89 | 0.0006769 | 0.00016944 | -0.00067689 | -0.00016964 | 1.0778e-08 | -2.0452e-07 | 0.0010244 | 0.0010245 | 0.0010245 | 0.98313 | -0.12139 | 0.98311 | -0.12151 | 0.37945
90 | 0.018039 | 0.0044697 | -0.018005 | -0.0044649 | 3.4585e-05 | 4.8655e-06 | 0.027319 | 0.027322 | 0.027322 | 0.98191 | -0.13028 | 0.97997 | -0.14445 | 3.3731
91 | 0.01765 | 0.004376 | -0.017646 | -0.0043754 | 4.1756e-06 | 5.4856e-07 | 0.026784 | 0.026784 | 0.026784 | 0.97997 | -0.14445 | 0.97973 | -0.14619 | 3.3067
92 | -0.020547 | -0.0050899 | 0.020551 | 0.0050905 | 3.2229e-06 | 6.2544e-07 | 0.031031 | 0.03103 | 0.031031 | 0.98464 | -0.11041 | 0.9848 | -0.10925 | 3.8309
93 | 0.0009631 | 0.00024135 | -0.0009631 | -0.00024137 | 2.7589e-09 | -2.5536e-08 | 0.0014548 | 0.0014548 | 0.0014548 | 0.9851 | -0.10701 | 0.9851 | -0.10703 | 0.53881
94 | 0.0064182 | 0.001588 | -0.0064181 | -0.001588 | 2.1019e-08 | -3.1149e-08 | 0.0098023 | 0.0098023 | 0.0098023 | 0.97356 | -0.19127 | 0.97356 | -0.1913 | 1.2102
95 | -0.007167 | -0.0017757 | 0.0071675 | 0.0017752 | 4.5842e-07 | -5.0984e-07 | 0.010947 | 0.010947 | 0.010947 | 0.97356 | -0.19127 | 0.97363 | -0.1908 | 1.3515
96 | 0.00594 | 0.0014682 | -0.0059395 | -0.0014691 | 4.9656e-07 | -8.9108e-07 | 0.0090715 | 0.0090719 | 0.0090719 | 0.97356 | -0.1913 | 0.97348 | -0.19192 | 1.12
97 | -0.0071675 | -0.0017752 | 0.0071718 | 0.0017704 | 4.31e-06 | -4.7993e-06 | 0.010947 | 0.010944 | 0.010947 | 0.97363 | -0.1908 | 0.97423 | -0.18634 | 1.3514
98 | 0.0059395 | 0.0014691 | -0.0059379 | -0.0014719 | 1.5794e-06 | -2.8324e-06 | 0.0090719 | 0.0090731 | 0.0090731 | 0.97348 | -0.19192 | 0.97321 | -0.19388 | 1.1201
99 | -0.0091882 | -0.0022757 | 0.0091903 | 0.0022747 | 2.0465e-06 | -1.0821e-06 | 0.014024 | 0.014024 | 0.014024 | 0.97423 | -0.18634 | 0.97446 | -0.18469 | 1.7314
100 | 0.0021657 | 0.00054185 | -0.0021653 | -0.00054244 | 4.068e-07 | -5.8228e-07 | 0.003311 | 0.0033112 | 0.0033112 | 0.97321 | -0.19388 | 0.97302 | -0.19524 | 1.2264
101 | 0.0037722 | 0.00093006 | -0.003772 | -0.00093113 | 2.1378e-07 | -1.0716e-06 | 0.0057621 | 0.0057625 | 0.0057625 | 0.97321 | -0.19388 | 0.97315 | -0.19431 | 0.71143
102 | -0.00080397 | -0.00019924 | 0.000804 | 0.00019885 | 2.9335e-08 | -3.8546e-07 | 0.001221 | 0.0012208 | 0.001221 | 0.97918 | -0.15022 | 0.97921 | -0.14995 | 0.4522
103 | -0.017417 | -0.0043191 | 0.017426 | 0.0043202 | 8.8892e-06 | 1.1123e-06 | 0.02645 | 0.026449 | 0.02645 | 0.97921 | -0.14995 | 0.97973 | -0.14619 | 3.2654
104 | 0.016613 | 0.0041202 | -0.016599 | -0.0041188 | 1.3862e-05 | 1.3839e-06 | 0.025229 | 0.025231 | 0.025231 | 0.97921 | -0.14995 | 0.97837 | -0.15611 | 3.1149
105 | 0.01615 | 0.0040064 | -0.016139 | -0.0040055 | 1.1557e-05 | 9.7427e-07 | 0.024549 | 0.02455 | 0.02455 | 0.97837 | -0.15611 | 0.97765 | -0.16138 | 3.0309
106 | 0.016139 | 0.0040055 | -0.016128 | -0.0040045 | 1.0994e-05 | 9.3189e-07 | 0.02455 | 0.024551 | 0.024551 | 0.97765 | -0.16138 | 0.97696 | -0.1664 | 3.031
107 | 0.0021653 | 0.00054244 | -0.0021652 | -0.00054251 | 5.1527e-08 | -7.3725e-08 | 0.0033112 | 0.0033113 | 0.0033113 | 0.97302 | -0.19524 | 0.973 | -0.19542 | 1.2264
108 | 0.00063612 | 0.00015928 | -0.00063612 | -0.00015943 | 7.0868e-09 | -1.4633e-07 | 0.00097278 | 0.00097283 | 0.00097283 | 0.973 | -0.19542 | 0.97299 | -0.1955 | 0.36031
109 | 0.013543 | 0.0033626 | -0.013537 | -0.0033628 | 5.6446e-06 | -2.0851e-07 | 0.020655 | 0.020655 | 0.020655 | 0.97513 | -0.17978 | 0.97471 | -0.18284 | 2.5501
110 | -0.014752 | -0.0036657 | 0.014762 | 0.003666 | 9.9369e-06 | 2.8764e-07 | 0.0225 | 0.022499 | 0.0225 | 0.97513 | -0.17978 | 0.97581 | -0.17483 | 2.7778
111 | 0.012728 | 0.00316 | -0.012728 | -0.00316 | 3.1354e-07 | -2.8856e-08 | 0.01942 | 0.01942 | 0.01942 | 0.97471 | -0.18284 | 0.97468 | -0.18302 | 2.3976
112 | -0.014762 | -0.003666 | 0.014777 | 0.0036664 | 1.4667e-05 | 4.1485e-07 | 0.022499 | 0.022497 | 0.022499 | 0.97581 | -0.17483 | 0.97681 | -0.16752 | 2.7776
113 | 0.012728 | 0.00316 | -0.012726 | -0.0031601 | 1.3323e-06 | -1.2252e-07 | 0.01942 | 0.01942 | 0.01942 | 0.97468 | -0.18302 | 0.97458 | -0.18379 | 2.3976
114 | -0.015637 | -0.003882 | 0.01564 | 0.0038822 | 2.3813e-06 | 1.5724e-07 | 0.023808 | 0.023807 | 0.023808 | 0.97681 | -0.16752 | 0.97696 | -0.1664 | 2.9392
115 | 0.010236 | 0.0025361 | -0.010235 | -0.0025365 | 1.2499e-06 | -4.3997e-07 | 0.015619 | 0.015619 | 0.015619 | 0.97458 | -0.18379 | 0.97446 | -0.18469 | 1.9283

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22902 | 0.057538

## res_load
| p_mw | q_mvar
0 | 0.022372 | 0.005607
1 | 0.004972 | 0.0012461
2 | 0.0011602 | 0.00029078
3 | 0.0035465 | 0.00088885
4 | 0.0064824 | 0.0016246
5 | 0.0022022 | 0.00055192
6 | 0.0071248 | 0.0017857
7 | 0.00073612 | 0.00018449
8 | 0.011764 | 0.0029482
9 | 0.0063854 | 0.0016003
10 | 0.013934 | 0.0034922
11 | 0.0063542 | 0.0015925
12 | 0.0010614 | 0.000266
13 | 0.0029138 | 0.00073026
14 | 0.00087321 | 0.00021885
15 | 0.0071179 | 0.0017839
16 | 0.0068355 | 0.0017131
17 | 0.017341 | 0.004346
18 | 0.011146 | 0.0027934
19 | 0.0012438 | 0.00031174
20 | 0.0012466 | 0.00031243
21 | 0.012233 | 0.0030658
22 | 0.0017579 | 0.00044057
23 | 0.0031699 | 0.00079445
24 | 0.0034024 | 0.00085271
25 | 0.0033248 | 0.00083327
26 | 0.00048601 | 0.00012181
27 | 0.003261 | 0.00081729
28 | 0.0019631 | 0.000492
29 | 0.00078282 | 0.00019619
30 | 0.0024577 | 0.00061597
31 | 0.0021623 | 0.00054192
32 | 0.0012093 | 0.00030309
33 | 0.0021569 | 0.00054057
34 | 0.0024345 | 0.00061013
35 | 0.00086738 | 0.00021738
36 | 0.0010815 | 0.00027105
37 | 0.0026078 | 0.00065358
38 | 0.009828 | 0.0024631
39 | 0.00091391 | 0.00022905
40 | 0.00072531 | 0.00018178
41 | 0.0016499 | 0.00041351
42 | 0.00090176 | 0.000226
43 | 0.0021091 | 0.00052858
44 | 0.00050767 | 0.00012723
45 | 0.0011977 | 0.00030016
46 | 0.00062353 | 0.00015627
47 | 0.00041177 | 0.0001032
48 | 0.00084577 | 0.00021197
49 | 0.000369 | 9.2481e-05
50 | 0.00084726 | 0.00021234
51 | 0.00021981 | 5.509e-05
52 | 0.00020309 | 5.09e-05
53 | 0.00016688 | 4.1824e-05
54 | 0.00087405 | 0.00021906
55 | 0.00066442 | 0.00016652
56 | 0.00024433 | 6.1236e-05
57 | 0.0003809 | 9.5462e-05
58 | 0.0006846 | 0.00017158
59 | 0.00026959 | 6.7565e-05
60 | 0.00035464 | 8.8882e-05
61 | 0.00019884 | 4.9833e-05
62 | 0.0014577 | 0.00036533
63 | 0.0009631 | 0.00024137
64 | 0.00074886 | 0.00018768
65 | 0.00047817 | 0.00011984
66 | 0.0020164 | 0.00050537
67 | 0.00067689 | 0.00016964
68 | 0.00027107 | 6.7937e-05
69 | 0.00010997 | 2.7562e-05
70 | 0.00022048 | 5.5258e-05
71 | 0.00044843 | 0.00011239
72 | 0.00066542 | 0.00016677
73 | 0.0015291 | 0.00038323
74 | 0.00063612 | 0.00015943
75 | 0.0012095 | 0.00030313
76 | 0.00080913 | 0.00020279
77 | 0.0008603 | 0.00021561
78 | 0.00249 | 0.00062406
79 | 0.0010448 | 0.00026186
80 | 0.00048829 | 0.00012238

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1