## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-6_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_1008-6_1_2_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_1008-6_1_2_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_1008-6_1_2_node_48 | 0.4 | n |  | TRUE
4 | bus_LV_1008-6_1_2_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1008-6_1_2_node_102 | 0.4 | n |  | TRUE
6 | bus_LV_1008-6_1_2_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1008-6_1_2_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1008-6_1_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1008-6_1_2_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_1008-6_1_2_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1008-6_1_2_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1008-6_1_2_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_1008-6_1_2_node_55 | 0.4 | n |  | TRUE
14 | bus_LV_1008-6_1_2_node_57 | 0.4 | n |  | TRUE
15 | bus_LV_1008-6_1_2_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_1008-6_1_2_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_1008-6_1_2_node_41 | 0.4 | n |  | TRUE
18 | bus_LV_1008-6_1_2_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_1008-6_1_2_node_87 | 0.4 | n |  | TRUE
20 | bus_LV_1008-6_1_2_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_1008-6_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_1008-6_1_2_node_58 | 0.4 | n |  | TRUE
23 | bus_LV_1008-6_1_2_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_1008-6_1_2_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_1008-6_1_2_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_1008-6_1_2_node_83 | 0.4 | n |  | TRUE
27 | bus_LV_1008-6_1_2_node_84 | 0.4 | n |  | TRUE
28 | bus_LV_1008-6_1_2_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_1008-6_1_2_node_88 | 0.4 | n |  | TRUE
30 | bus_LV_1008-6_1_2_node_89 | 0.4 | n |  | TRUE
31 | bus_MV_125_0_node_119 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-6_1_2_load_6 | 0 | 0.0013326 | 0.00033399 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-6_1_2_load_48 | 3 | 0.0018589 | 0.00046588 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-6_1_2_load_102 | 5 | 0.0070942 | 0.001778 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-6_1_2_load_13 | 6 | 0.0032533 | 0.00081536 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-6_1_2_load_16 | 9 | 0.0003702 | 9.278e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-6_1_2_load_17 | 10 | 0.00045902 | 0.00011504 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-6_1_2_load_18 | 11 | 0.0026324 | 0.00065973 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-6_1_2_load_19 | 12 | 0.0022207 | 0.00055656 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-6_1_2_load_55 | 13 | 0.00037021 | 9.2782e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-6_1_2_load_57 | 14 | 0.00047407 | 0.00011881 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-6_1_2_load_64 | 16 | 0.0081296 | 0.0020375 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-6_1_2_load_85 | 18 | 0.010377 | 0.0026006 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-6_1_2_load_87 | 19 | 0.0011168 | 0.00027989 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-6_1_2_load_42 | 20 | 0.0040188 | 0.0010072 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-6_1_2_load_58 | 22 | 0.00037927 | 9.5055e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-6_1_2_load_65 | 23 | 0.00037886 | 9.4952e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-6_1_2_load_67 | 24 | 0.010723 | 0.0026875 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-6_1_2_load_66 | 25 | 0.0016612 | 0.00041633 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-6_1_2_load_83 | 26 | 0.014631 | 0.003667 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-6_1_2_load_86 | 28 | 0.004271 | 0.0010704 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-6_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-6_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.045879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-6_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.042139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-6_1_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.011784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1008-6_1_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.053711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-6_1_2_line_5 | NAYY 4x150 SE | 5 | 25 | 0.031168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1008-6_1_2_line_6 | NAYY 4x150 SE | 5 | 30 | 0.072749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-6_1_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.0128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-6_1_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.013399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-6_1_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.011044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-6_1_2_line_10 | NAYY 4x150 SE | 7 | 10 | 0.0086948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-6_1_2_line_11 | NAYY 4x150 SE | 8 | 11 | 0.011824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-6_1_2_line_12 | NAYY 4x150 SE | 8 | 12 | 0.0273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-6_1_2_line_13 | NAYY 4x150 SE | 9 | 13 | 0.0066716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-6_1_2_line_14 | NAYY 4x150 SE | 10 | 14 | 0.021908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-6_1_2_line_15 | NAYY 4x150 SE | 12 | 15 | 0.021881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-6_1_2_line_16 | NAYY 4x150 SE | 12 | 16 | 0.036746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-6_1_2_line_17 | NAYY 4x150 SE | 14 | 22 | 0.02473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-6_1_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.025691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-6_1_2_line_19 | NAYY 4x150 SE | 16 | 24 | 0.018712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1008-6_1_2_line_20 | NAYY 4x150 SE | 17 | 18 | 0.034157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-6_1_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.023065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-6_1_2_line_22 | NAYY 4x150 SE | 18 | 27 | 0.065352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-6_1_2_line_23 | NAYY 4x150 SE | 19 | 29 | 0.010922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-6_1_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.014175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-6_1_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.0054193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-6_1_2_line_26 | NAYY 4x150 SE | 21 | 22 | 0.0020763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-6_1_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.033383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-6_1_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.10344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-6_1_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.095414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-6_1_2_trafo_40 | 0.25 MVA 20/0.4 kV | 31 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2643649.0466 | 1200435.8848 | 2643641.7701 | 1200418.2309
1 | 2643649.0466 | 1200435.8848 | 2643674.4745 | 1200474.1142
2 | 2643674.4745 | 1200474.1142 | 2643697.092 | 1200438.5593
3 | 2643693.6312 | 1200427.7502 | 2643696.9356 | 1200432.8772 | 2643697.092 | 1200438.5593
4 | 2643735.8794 | 1200394.5847 | 2643693.6312 | 1200427.7502
5 | 2643735.8794 | 1200394.5847 | 2643709.8867 | 1200377.385
6 | 2643735.8794 | 1200394.5847 | 2643737.7571 | 1200388.6951 | 2643736.1088 | 1200363.2354 | 2643727.7756 | 1200329.5888 | 2643724.5501 | 1200324.0732
7 | 2643807.4323 | 1200462.7467 | 2643820.227 | 1200463.1067
8 | 2643833.6212 | 1200463.4834 | 2643820.227 | 1200463.1067
9 | 2643807.4323 | 1200462.7467 | 2643807.2254 | 1200473.7888
10 | 2643807.4323 | 1200462.7467 | 2643806.8858 | 1200454.0691
11 | 2643833.6212 | 1200463.4834 | 2643832.7927 | 1200475.2781
12 | 2643833.6212 | 1200463.4834 | 2643835.4576 | 1200442.474 | 2643836.7807 | 1200436.4057
13 | 2643807.2254 | 1200473.7888 | 2643807.1004 | 1200480.4592
14 | 2643804.9148 | 1200432.2554 | 2643806.3208 | 1200445.0953 | 2643806.8858 | 1200454.0691
15 | 2643836.7275 | 1200414.6231 | 2643837.5293 | 1200432.9727 | 2643836.7807 | 1200436.4057
16 | 2643836.7807 | 1200436.4057 | 2643871.0287 | 1200449.7236
17 | 2643804.9148 | 1200432.2554 | 2643802.223 | 1200407.672
18 | 2643826.867 | 1200391.0709 | 2643833.3905 | 1200409.8071 | 2643836.7275 | 1200414.6231
19 | 2643871.0287 | 1200449.7236 | 2643889.6822 | 1200451.2049
20 | 2643861.1157 | 1200391.0664 | 2643842.0321 | 1200390.9264 | 2643834.0706 | 1200390.768 | 2643826.867 | 1200391.0709
21 | 2643826.867 | 1200391.0709 | 2643818.6188 | 1200373.9342 | 2643816.4563 | 1200370.5143
22 | 2643925.966 | 1200385.9728 | 2643913.5593 | 1200389.8839 | 2643907.0124 | 1200390.9475 | 2643861.1157 | 1200391.0664
23 | 2643812.04 | 1200360.6451 | 2643813.5618 | 1200365.9371 | 2643816.4563 | 1200370.5143
24 | 2643801.997 | 1200405.608 | 2643810.036 | 1200404.533 | 2643812.0908 | 1200404.6147 | 2643815.9813 | 1200405.5771
25 | 2643801.997 | 1200405.608 | 2643801.2662 | 1200400.2383
26 | 2643801.997 | 1200405.608 | 2643802.223 | 1200407.672
27 | 2643925.966 | 1200385.9728 | 2643952.2645 | 1200406.5351
28 | 2643925.966 | 1200385.9728 | 2643914.0043 | 1200374.9009 | 2643891.275 | 1200354.9784 | 2643873.9016 | 1200339.6201 | 2643864.3001 | 1200330.5668 | 2643848.5147 | 1200317.4322
29 | 2643812.04 | 1200360.6451 | 2643808.2043 | 1200360.5059 | 2643801.4915 | 1200357.1993 | 2643791.1346 | 1200349.3968 | 2643741.0601 | 1200328.4631 | 2643724.5501 | 1200324.0732

## bus_geodata
| x | y | coords
0 | 2643641.7701 | 1200418.2309
1 | 2643649.0466 | 1200435.8848
2 | 2643674.4745 | 1200474.1142
3 | 2643697.092 | 1200438.5593
4 | 2643693.6312 | 1200427.7502
5 | 2643735.8794 | 1200394.5847
6 | 2643820.227 | 1200463.1067
7 | 2643807.4323 | 1200462.7467
8 | 2643833.6212 | 1200463.4834
9 | 2643807.2254 | 1200473.7888
10 | 2643806.8858 | 1200454.0691
11 | 2643832.7927 | 1200475.2781
12 | 2643836.7808 | 1200436.4057
13 | 2643807.1004 | 1200480.4592
14 | 2643804.9148 | 1200432.2554
15 | 2643836.7275 | 1200414.6231
16 | 2643871.0287 | 1200449.7236
17 | 2643826.867 | 1200391.0709
18 | 2643861.1157 | 1200391.0664
19 | 2643816.4563 | 1200370.5143
20 | 2643815.9813 | 1200405.5771
21 | 2643801.997 | 1200405.608
22 | 2643802.223 | 1200407.672
23 | 2643801.2662 | 1200400.2383
24 | 2643889.6822 | 1200451.2049
25 | 2643709.8867 | 1200377.385
26 | 2643952.2645 | 1200406.5351
27 | 2643925.966 | 1200385.9728
28 | 2643848.5147 | 1200317.4322
29 | 2643812.04 | 1200360.6451
30 | 2643724.5501 | 1200324.0732
31 | 2643826.867 | 1200391.0709

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99444 | -0.039035 | 0.0013326 | 0.00033399
1 | 0.99448 | -0.038778 | 0 | 0
2 | 0.99457 | -0.038159 | 0 | 0
3 | 0.99465 | -0.037589 | 0.0018589 | 0.00046588
4 | 0.9947 | -0.037208 | 0 | 0
5 | 0.99495 | -0.035472 | 0.0070942 | 0.001778
6 | 0.99829 | -0.011985 | 0.0032533 | 0.00081536
7 | 0.99817 | -0.012814 | 0 | 0
8 | 0.99848 | -0.010682 | 0 | 0
9 | 0.99816 | -0.012896 | 0.0003702 | 9.278e-05
10 | 0.9981 | -0.013312 | 0.00045902 | 0.00011504
11 | 0.99843 | -0.010994 | 0.0026324 | 0.00065973
12 | 0.99896 | -0.0073083 | 0.0022207 | 0.00055656
13 | 0.99816 | -0.01292 | 0.00037021 | 9.2782e-05
14 | 0.99794 | -0.014466 | 0.00047407 | 0.00011881
15 | 1 | 0 | -0.076811 | -0.019073
16 | 0.99797 | -0.014245 | 0.0081296 | 0.0020375
17 | 0.99844 | -0.01089 | 0 | 0
18 | 0.99701 | -0.020924 | 0.010377 | 0.0026006
19 | 0.99801 | -0.013917 | 0.0011168 | 0.00027989
20 | 0.99767 | -0.016313 | 0.0040188 | 0.0010072
21 | 0.99775 | -0.015742 | 0 | 0
22 | 0.99777 | -0.015651 | 0.00037927 | 9.5055e-05
23 | 0.99775 | -0.015763 | 0.00037886 | 9.4952e-05
24 | 0.99768 | -0.016257 | 0.010723 | 0.0026875
25 | 0.99487 | -0.035995 | 0.0016612 | 0.00041633
26 | 0.99454 | -0.038285 | 0.014631 | 0.003667
27 | 0.99524 | -0.03336 | 0 | 0
28 | 0.99461 | -0.03782 | 0.004271 | 0.0010704
29 | 0.99782 | -0.015229 | 0 | 0
30 | 0.99619 | -0.026704 | 0 | 0
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013326 | -0.00033399 | 0.0013327 | 0.00033376 | 4.7375e-08 | -2.2952e-07 | 0.001994 | 0.001994 | 0.001994 | 0.99444 | -0.039035 | 0.99448 | -0.038778 | 0.73853
1 | -0.0013327 | -0.00033376 | 0.0013328 | 0.0003332 | 1.1381e-07 | -5.5155e-07 | 0.001994 | 0.0019937 | 0.001994 | 0.99448 | -0.038778 | 0.99457 | -0.038159 | 0.7385
2 | -0.0013328 | -0.0003332 | 0.0013329 | 0.0003327 | 1.0451e-07 | -5.0669e-07 | 0.0019937 | 0.0019936 | 0.0019937 | 0.99457 | -0.038159 | 0.99465 | -0.037589 | 0.73842
3 | -0.0031918 | -0.00079858 | 0.0031919 | 0.00079849 | 1.6762e-07 | -8.8485e-08 | 0.0047745 | 0.0047745 | 0.0047745 | 0.99465 | -0.037589 | 0.9947 | -0.037208 | 1.7683
4 | -0.0031919 | -0.00079849 | 0.0031927 | 0.00079809 | 7.6396e-07 | -4.0354e-07 | 0.0047745 | 0.0047742 | 0.0047745 | 0.9947 | -0.037208 | 0.99495 | -0.035472 | 1.7683
5 | 0.0016613 | 0.00041597 | -0.0016612 | -0.00041633 | 1.2006e-07 | -3.5858e-07 | 0.0024845 | 0.0024846 | 0.0024846 | 0.99495 | -0.035472 | 0.99487 | -0.035995 | 0.92022
6 | -0.011948 | -0.002992 | 0.011963 | 0.0029966 | 1.4494e-05 | 4.6285e-06 | 0.017868 | 0.017868 | 0.017868 | 0.99495 | -0.035472 | 0.99619 | -0.026704 | 6.618
7 | 0.0064536 | 0.0016164 | -0.0064529 | -0.0016163 | 7.3904e-07 | 1.1691e-07 | 0.0096192 | 0.0096192 | 0.0096192 | 0.99829 | -0.011985 | 0.99817 | -0.012814 | 3.5627
8 | -0.0097069 | -0.0024318 | 0.0097087 | 0.0024323 | 1.7503e-06 | 4.9797e-07 | 0.014468 | 0.014468 | 0.014468 | 0.99829 | -0.011985 | 0.99848 | -0.010682 | 5.3587
9 | 0.00074041 | 0.00018533 | -0.0007404 | -0.00018548 | 8.3949e-09 | -1.4113e-07 | 0.0011037 | 0.0011037 | 0.0011037 | 0.99817 | -0.012814 | 0.99816 | -0.012896 | 0.40879
10 | 0.0057125 | 0.001431 | -0.0057121 | -0.001431 | 3.9344e-07 | 3.7676e-08 | 0.0085156 | 0.0085156 | 0.0085156 | 0.99817 | -0.012814 | 0.9981 | -0.013312 | 3.1539
11 | 0.0026325 | 0.00065962 | -0.0026324 | -0.00065973 | 1.1355e-07 | -1.1096e-07 | 0.0039231 | 0.0039231 | 0.0039231 | 0.99848 | -0.010682 | 0.99843 | -0.010994 | 1.453
12 | -0.012341 | -0.0030919 | 0.012347 | 0.0030938 | 5.7621e-06 | 1.859e-06 | 0.018391 | 0.018391 | 0.018391 | 0.99848 | -0.010682 | 0.99896 | -0.0073083 | 6.8117
13 | 0.00037021 | 9.2695e-05 | -0.00037021 | -9.2782e-05 | 1.2679e-09 | -8.6717e-08 | 0.00055186 | 0.00055189 | 0.00055189 | 0.99816 | -0.012896 | 0.99816 | -0.01292 | 0.2044
14 | 0.005253 | 0.0013159 | -0.0052522 | -0.0013159 | 8.3842e-07 | 3.6187e-08 | 0.0078313 | 0.0078314 | 0.0078314 | 0.9981 | -0.013312 | 0.99794 | -0.014466 | 2.9005
15 | -0.033441 | -0.0083827 | 0.033475 | 0.0083954 | 3.388e-05 | 1.2744e-05 | 0.049814 | 0.049814 | 0.049814 | 0.99896 | -0.0073083 | 1 | 0 | 18.4496
16 | 0.018874 | 0.0047323 | -0.018856 | -0.0047258 | 1.8124e-05 | 6.4903e-06 | 0.028115 | 0.028115 | 0.028115 | 0.99896 | -0.0073083 | 0.99797 | -0.014245 | 10.4129
17 | 0.0047781 | 0.0011971 | -0.0047774 | -0.0011971 | 7.833e-07 | -2.1782e-08 | 0.0071245 | 0.0071246 | 0.0071246 | 0.99794 | -0.014466 | 0.99777 | -0.015651 | 2.6387
18 | 0.042535 | 0.010678 | -0.042471 | -0.010653 | 6.4234e-05 | 2.4369e-05 | 0.0633 | 0.0633 | 0.0633 | 1 | 0 | 0.99844 | -0.01089 | 23.4443
19 | 0.010726 | 0.0026884 | -0.010723 | -0.0026875 | 2.9866e-06 | 9.0428e-07 | 0.015993 | 0.015993 | 0.015993 | 0.99797 | -0.014245 | 0.99768 | -0.016257 | 5.9234
20 | 0.029365 | 0.0073681 | -0.029324 | -0.0073528 | 4.0828e-05 | 1.5257e-05 | 0.043767 | 0.043767 | 0.043767 | 0.99844 | -0.01089 | 0.99701 | -0.020924 | 16.2101
21 | 0.013106 | 0.0032851 | -0.013101 | -0.0032833 | 5.4911e-06 | 1.8104e-06 | 0.019533 | 0.019533 | 0.019533 | 0.99844 | -0.01089 | 0.99801 | -0.013917 | 7.2344
22 | 0.018948 | 0.0047522 | -0.018915 | -0.0047405 | 3.2615e-05 | 1.1693e-05 | 0.02828 | 0.028281 | 0.028281 | 0.99701 | -0.020924 | 0.99524 | -0.03336 | 10.4743
23 | 0.011984 | 0.0030034 | -0.011982 | -0.0030027 | 2.1758e-06 | 6.9416e-07 | 0.017868 | 0.017868 | 0.017868 | 0.99801 | -0.013917 | 0.99782 | -0.015229 | 6.6177
24 | -0.0040188 | -0.0010072 | 0.0040192 | 0.0010072 | 3.1779e-07 | -6.2888e-08 | 0.005994 | 0.005994 | 0.005994 | 0.99767 | -0.016313 | 0.99775 | -0.015742 | 2.22
25 | 0.00037887 | 9.4882e-05 | -0.00037886 | -9.4952e-05 | 1.0796e-09 | -7.0363e-08 | 0.000565 | 0.00056503 | 0.00056503 | 0.99775 | -0.015742 | 0.99775 | -0.015763 | 0.20927
26 | -0.004398 | -0.001102 | 0.0043981 | 0.001102 | 5.5738e-08 | -5.6803e-09 | 0.006559 | 0.006559 | 0.006559 | 0.99775 | -0.015742 | 0.99777 | -0.015651 | 2.4293
27 | -0.014631 | -0.003667 | 0.014641 | 0.0036704 | 9.9828e-06 | 3.4061e-06 | 0.021891 | 0.021891 | 0.021891 | 0.99454 | -0.038285 | 0.99524 | -0.03336 | 8.1079
28 | 0.0042737 | 0.0010701 | -0.004271 | -0.0010704 | 2.6354e-06 | -3.2977e-07 | 0.0063894 | 0.0063898 | 0.0063898 | 0.99524 | -0.03336 | 0.99461 | -0.03782 | 2.3666
29 | 0.011982 | 0.0030027 | -0.011963 | -0.0029966 | 1.9008e-05 | 6.0666e-06 | 0.017868 | 0.017868 | 0.017868 | 0.99782 | -0.015229 | 0.99619 | -0.026704 | 6.6178

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.076811 | 0.019073

## res_load
| p_mw | q_mvar
0 | 0.0013326 | 0.00033399
1 | 0.0018589 | 0.00046588
2 | 0.0070942 | 0.001778
3 | 0.0032533 | 0.00081536
4 | 0.0003702 | 9.278e-05
5 | 0.00045902 | 0.00011504
6 | 0.0026324 | 0.00065973
7 | 0.0022207 | 0.00055656
8 | 0.00037021 | 9.2782e-05
9 | 0.00047407 | 0.00011881
10 | 0.0081296 | 0.0020375
11 | 0.010377 | 0.0026006
12 | 0.0011168 | 0.00027989
13 | 0.0040188 | 0.0010072
14 | 0.00037927 | 9.5055e-05
15 | 0.00037886 | 9.4952e-05
16 | 0.010723 | 0.0026875
17 | 0.0016612 | 0.00041633
18 | 0.014631 | 0.003667
19 | 0.004271 | 0.0010704

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1