## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-6_2_3_node_20 | 0.4 | n |  | TRUE
1 | bus_LV_1008-6_2_3_node_21 | 0.4 | n |  | TRUE
2 | bus_LV_1008-6_2_3_node_22 | 0.4 | n |  | TRUE
3 | bus_LV_1008-6_2_3_node_23 | 0.4 | n |  | TRUE
4 | bus_LV_1008-6_2_3_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_1008-6_2_3_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_1008-6_2_3_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_1008-6_2_3_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1008-6_2_3_node_56 | 0.4 | n |  | TRUE
9 | bus_LV_1008-6_2_3_node_38 | 0.4 | n |  | TRUE
10 | bus_LV_1008-6_2_3_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1008-6_2_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1008-6_2_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1008-6_2_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1008-6_2_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1008-6_2_3_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1008-6_2_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1008-6_2_3_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_1008-6_2_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1008-6_2_3_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_1008-6_2_3_node_52 | 0.4 | n |  | TRUE
21 | bus_LV_1008-6_2_3_node_63 | 0.4 | n |  | TRUE
22 | bus_LV_1008-6_2_3_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_1008-6_2_3_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_1008-6_2_3_node_39 | 0.4 | n |  | TRUE
25 | bus_LV_1008-6_2_3_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_1008-6_2_3_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_1008-6_2_3_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_1008-6_2_3_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_1008-6_2_3_node_98 | 0.4 | n |  | TRUE
30 | bus_LV_1008-6_2_3_node_60 | 0.4 | n |  | TRUE
31 | bus_LV_1008-6_2_3_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_1008-6_2_3_node_69 | 0.4 | n |  | TRUE
33 | bus_LV_1008-6_2_3_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_1008-6_2_3_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_1008-6_2_3_node_70 | 0.4 | n |  | TRUE
36 | bus_LV_1008-6_2_3_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_1008-6_2_3_node_79 | 0.4 | n |  | TRUE
38 | bus_LV_1008-6_2_3_node_81 | 0.4 | n |  | TRUE
39 | bus_LV_1008-6_2_3_node_82 | 0.4 | n |  | TRUE
40 | bus_LV_1008-6_2_3_node_99 | 0.4 | n |  | TRUE
41 | bus_MV_125_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-6_2_3_load_20 | 0 | 0.0016236 | 0.00040691 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-6_2_3_load_21 | 1 | 0.0024849 | 0.00062279 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-6_2_3_load_23 | 3 | 0.0016576 | 0.00041544 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-6_2_3_load_25 | 5 | 0.0035884 | 0.00089933 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-6_2_3_load_54 | 6 | 0.00037773 | 9.4667e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-6_2_3_load_44 | 7 | 0.0036209 | 0.00090749 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-6_2_3_load_56 | 8 | 0.0016236 | 0.00040691 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-6_2_3_load_26 | 10 | 0.00063624 | 0.00015946 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-6_2_3_load_27 | 11 | 0.0019325 | 0.00048433 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-6_2_3_load_28 | 12 | 0.00076408 | 0.0001915 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-6_2_3_load_29 | 13 | 0.002278 | 0.00057091 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-6_2_3_load_30 | 14 | 0.0051557 | 0.0012921 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-6_2_3_load_31 | 15 | 0.0070145 | 0.001758 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-6_2_3_load_33 | 17 | 0.0030584 | 0.00076651 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-6_2_3_load_34 | 18 | 0.0045639 | 0.0011438 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-6_2_3_load_63 | 21 | 0.0069786 | 0.001749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-6_2_3_load_47 | 22 | 0.001755 | 0.00043984 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-6_2_3_load_37 | 23 | 0.0029677 | 0.00074377 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-6_2_3_load_39 | 24 | 0.020253 | 0.0050758 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-6_2_3_load_53 | 25 | 0.0021625 | 0.00054198 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1008-6_2_3_load_43 | 26 | 0.002402 | 0.00060201 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1008-6_2_3_load_46 | 28 | 0.0020072 | 0.00050305 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1008-6_2_3_load_98 | 29 | 0.0011051 | 0.00027696 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1008-6_2_3_load_60 | 30 | 0.0017828 | 0.00044681 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1008-6_2_3_load_61 | 31 | 0.0013697 | 0.00034327 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1008-6_2_3_load_69 | 32 | 0.0033804 | 0.0008472 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1008-6_2_3_load_80 | 33 | 0.0019384 | 0.00048581 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1008-6_2_3_load_68 | 34 | 0.0035825 | 0.00089785 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1008-6_2_3_load_71 | 36 | 0.011603 | 0.0029079 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1008-6_2_3_load_79 | 37 | 0.0067888 | 0.0017014 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1008-6_2_3_load_81 | 38 | 0.0017506 | 0.00043874 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1008-6_2_3_load_82 | 39 | 0.0035359 | 0.00088617 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1008-6_2_3_load_99 | 40 | 0.0013489 | 0.00033807 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-6_2_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0051203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-6_2_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0081329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-6_2_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.010214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-6_2_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1008-6_2_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.014802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-6_2_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0085441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1008-6_2_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.02333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-6_2_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.012618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-6_2_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.01458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-6_2_3_line_9 | NAYY 4x150 SE | 7 | 26 | 0.00048632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-6_2_3_line_10 | NAYY 4x150 SE | 8 | 13 | 0.035978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-6_2_3_line_11 | NAYY 4x150 SE | 9 | 24 | 0.040122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-6_2_3_line_12 | NAYY 4x150 SE | 9 | 23 | 0.042042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-6_2_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.021598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-6_2_3_line_14 | NAYY 4x150 SE | 10 | 12 | 0.011414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-6_2_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.021025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-6_2_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.03248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-6_2_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.017219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-6_2_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.020243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-6_2_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.046391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1008-6_2_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.15507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-6_2_3_line_21 | NAYY 4x150 SE | 17 | 20 | 0.0046104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-6_2_3_line_22 | NAYY 4x150 SE | 18 | 21 | 0.039875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-6_2_3_line_23 | NAYY 4x150 SE | 19 | 22 | 0.021328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-6_2_3_line_24 | NAYY 4x150 SE | 20 | 30 | 0.01834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-6_2_3_line_25 | NAYY 4x150 SE | 20 | 31 | 0.019107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-6_2_3_line_26 | NAYY 4x150 SE | 22 | 27 | 0.0096848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-6_2_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.0060753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-6_2_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.020077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-6_2_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.081675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1008-6_2_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.31999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1008-6_2_3_line_31 | NAYY 4x150 SE | 29 | 40 | 0.021762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1008-6_2_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.016148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1008-6_2_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.020827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1008-6_2_3_line_34 | NAYY 4x150 SE | 32 | 34 | 0.033931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1008-6_2_3_line_35 | NAYY 4x150 SE | 33 | 37 | 0.027524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1008-6_2_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.018346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1008-6_2_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.049093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1008-6_2_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.013302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1008-6_2_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.0073089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-6_2_3_trafo_34 | 0.25 MVA 20/0.4 kV | 41 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2643803.0063 | 1200514.628 | 2643801.9739 | 1200519.6432
1 | 2643800.3342 | 1200527.6091 | 2643801.9739 | 1200519.6432
2 | 2643803.0063 | 1200514.628 | 2643805.0656 | 1200504.6237
3 | 2643800.3342 | 1200527.6091 | 2643796.756 | 1200539.0894
4 | 2643800.3342 | 1200527.6091 | 2643814.543 | 1200531.757
5 | 2643806.2845 | 1200496.1874 | 2643806.049 | 1200499.8464 | 2643805.0656 | 1200504.6237
6 | 2643796.756 | 1200539.0894 | 2643788.9994 | 1200561.0921
7 | 2643796.756 | 1200539.0894 | 2643790.3498 | 1200536.5521 | 2643784.899 | 1200534.7923
8 | 2643828.5384 | 1200535.8426 | 2643814.543 | 1200531.757
9 | 2643788.9994 | 1200561.0921 | 2643788.8377 | 1200561.5507
10 | 2643751.4342 | 1200537.828 | 2643752.0317 | 1200538.3172 | 2643755.7658 | 1200539.8453 | 2643759.2592 | 1200539.9265 | 2643763.7626 | 1200538.2807 | 2643771.7207 | 1200533.6808 | 2643775.0325 | 1200532.5822 | 2643778.3355 | 1200532.6731 | 2643784.899 | 1200534.7923
11 | 2643828.5384 | 1200535.8426 | 2643825.5088 | 1200557.6438 | 2643824.7464 | 1200559.8728 | 2643827.4155 | 1200569.5978 | 2643827.3739 | 1200575.269
12 | 2643828.5384 | 1200535.8426 | 2643831.4844 | 1200493.9036
13 | 2643751.7498 | 1200519.2655 | 2643752.7452 | 1200517.7997 | 2643762.9944 | 1200506.9908 | 2643766.0769 | 1200503.1423
14 | 2643771.6436 | 1200493.2575 | 2643768.3415 | 1200500.3151 | 2643766.0769 | 1200503.1423
15 | 2643751.4342 | 1200537.828 | 2643749.4287 | 1200536.1858 | 2643747.8328 | 1200532.6944 | 2643747.3023 | 1200528.2102 | 2643748.9591 | 1200523.3751 | 2643751.7498 | 1200519.2655
16 | 2643938.5351 | 1200553.0936 | 2643925.7119 | 1200561.4476 | 2643911.7406 | 1200571.4381
17 | 2643897.7344 | 1200581.4535 | 2643911.7406 | 1200571.4381
18 | 2643938.5351 | 1200553.0936 | 2643955.4966 | 1200542.0435
19 | 2643897.7344 | 1200581.4535 | 2643885.3276 | 1200569.8893 | 2643866.7072 | 1200547.0977
20 | 2643897.7344 | 1200581.4535 | 2643885.1446 | 1200594.8131 | 2643873.8794 | 1200608.1824 | 2643853.5984 | 1200638.5397 | 2643850.0757 | 1200642.4605 | 2643845.1478 | 1200646.9936 | 2643840.4457 | 1200650.8391 | 2643816.2837 | 1200633.3188 | 2643811.517 | 1200628.3144 | 2643803.7915 | 1200617.8075 | 2643795.8758 | 1200605.2091
21 | 2643959.3596 | 1200539.5269 | 2643955.4966 | 1200542.0435
22 | 2643866.7072 | 1200547.0977 | 2643861.3964 | 1200540.5972 | 2643846.6835 | 1200517.5319 | 2643844.8594 | 1200513.8352
23 | 2643795.8758 | 1200605.2091 | 2643784.5276 | 1200587.1513
24 | 2643959.3596 | 1200539.5269 | 2643964.0097 | 1200536.5594 | 2643974.2684 | 1200528.8655
25 | 2643959.3596 | 1200539.5269 | 2643947.8468 | 1200524.2779
26 | 2643779.3744 | 1200578.9513 | 2643784.5276 | 1200587.1513
27 | 2643822.3364 | 1200577.3108 | 2643827.3672 | 1200576.1901 | 2643827.3739 | 1200575.269
28 | 2643779.3744 | 1200578.9513 | 2643782.5186 | 1200575.7947 | 2643786.5023 | 1200568.1751 | 2643788.8377 | 1200561.5507
29 | 2643779.3744 | 1200578.9513 | 2643772.9888 | 1200573.6126 | 2643764.6075 | 1200567.3922 | 2643757.5199 | 1200564.3609 | 2643742.7078 | 1200558.9606 | 2643734.5034 | 1200555.6098 | 2643727.181 | 1200550.3311 | 2643719.9948 | 1200543.0634 | 2643713.8065 | 1200533.5721
30 | 2643713.8065 | 1200533.5721 | 2643418.5797 | 1200656.9888
31 | 2643418.5797 | 1200656.9888 | 2643417.5253 | 1200668.0639 | 2643416.1484 | 1200673.179 | 2643413.6798 | 1200677.9134
32 | 2643974.2684 | 1200528.8655 | 2643985.7793 | 1200520.2325 | 2643987.1025 | 1200519.0726
33 | 2643947.8468 | 1200524.2779 | 2643943.8294 | 1200518.9567 | 2643935.9389 | 1200507.2
34 | 2644011.4083 | 1200495.4628 | 2644007.1558 | 1200500.4452 | 2643997.2873 | 1200510.1448 | 2643987.1025 | 1200519.0726
35 | 2643921.478 | 1200483.9395 | 2643922.324 | 1200486.914 | 2643935.9389 | 1200507.2
36 | 2644023.3193 | 1200481.509 | 2644021.0925 | 1200484.1163 | 2644011.4083 | 1200495.4628
37 | 2644023.3193 | 1200481.509 | 2644026.7189 | 1200492.2623 | 2644028.3507 | 1200499.1338 | 2644027.8473 | 1200529.882
38 | 2643921.478 | 1200483.9395 | 2643921.478 | 1200483.9395 | 2643922.7673 | 1200480.447 | 2643929.7743 | 1200473.9161
39 | 2643929.7743 | 1200473.9161 | 2643935.1209 | 1200468.9327

## bus_geodata
| x | y | coords
0 | 2643801.9739 | 1200519.6432
1 | 2643803.0063 | 1200514.628
2 | 2643800.3342 | 1200527.6091
3 | 2643805.0656 | 1200504.6237
4 | 2643796.756 | 1200539.0894
5 | 2643814.543 | 1200531.757
6 | 2643806.2845 | 1200496.1874
7 | 2643788.9993 | 1200561.0921
8 | 2643784.899 | 1200534.7923
9 | 2643828.5384 | 1200535.8426
10 | 2643766.0769 | 1200503.1423
11 | 2643751.7498 | 1200519.2655
12 | 2643771.6436 | 1200493.2575
13 | 2643751.4342 | 1200537.828
14 | 2643911.7406 | 1200571.4381
15 | 2643938.535 | 1200553.0936
16 | 2643897.7344 | 1200581.4535
17 | 2643955.4966 | 1200542.0435
18 | 2643866.7072 | 1200547.0977
19 | 2643795.8758 | 1200605.2091
20 | 2643959.3596 | 1200539.5269
21 | 2643844.8594 | 1200513.8352
22 | 2643784.5276 | 1200587.1513
23 | 2643831.4844 | 1200493.9036
24 | 2643827.374 | 1200575.269
25 | 2643822.3364 | 1200577.3108
26 | 2643788.8377 | 1200561.5507
27 | 2643779.3744 | 1200578.9513
28 | 2643713.8065 | 1200533.5721
29 | 2643418.5797 | 1200656.9888
30 | 2643974.2684 | 1200528.8655
31 | 2643947.8468 | 1200524.2779
32 | 2643987.1025 | 1200519.0726
33 | 2643935.9389 | 1200507.2
34 | 2644011.4083 | 1200495.4628
35 | 2644023.3193 | 1200481.509
36 | 2644027.8473 | 1200529.882
37 | 2643921.478 | 1200483.9395
38 | 2643929.7743 | 1200473.9161
39 | 2643935.1209 | 1200468.9327
40 | 2643413.6798 | 1200677.9134
41 | 2643897.7344 | 1200581.4535

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97809 | -0.15368 | 0.0016236 | 0.00040691
1 | 0.97805 | -0.15392 | 0.0024849 | 0.00062279
2 | 0.97816 | -0.15316 | 0 | 0
3 | 0.97802 | -0.15414 | 0.0016576 | 0.00041544
4 | 0.97878 | -0.14876 | 0 | 0
5 | 0.97753 | -0.15764 | 0.0035884 | 0.00089933
6 | 0.97802 | -0.15417 | 0.00037773 | 9.4667e-05
7 | 0.98022 | -0.13847 | 0.0036209 | 0.00090749
8 | 0.97864 | -0.14971 | 0.0016236 | 0.00040691
9 | 0.97699 | -0.16151 | 0 | 0
10 | 0.9782 | -0.15286 | 0.00063624 | 0.00015946
11 | 0.97825 | -0.15255 | 0.0019325 | 0.00048433
12 | 0.97819 | -0.15295 | 0.00076408 | 0.0001915
13 | 0.97835 | -0.15182 | 0.002278 | 0.00057091
14 | 0.99519 | -0.033385 | 0.0051557 | 0.0012921
15 | 0.99305 | -0.048418 | 0.0070145 | 0.001758
16 | 0.99645 | -0.024549 | 0 | 0
17 | 0.99192 | -0.056379 | 0.0030584 | 0.00076651
18 | 1 | 0 | -0.11499 | -0.028825
19 | 0.98411 | -0.11083 | 0 | 0
20 | 0.99168 | -0.058051 | 0 | 0
21 | 0.9996 | -0.0027791 | 0.0069786 | 0.001749
22 | 0.98241 | -0.12286 | 0.001755 | 0.00043984
23 | 0.97681 | -0.16281 | 0.0029677 | 0.00074377
24 | 0.97568 | -0.17092 | 0.020253 | 0.0050758
25 | 0.97566 | -0.17106 | 0.0021625 | 0.00054198
26 | 0.98025 | -0.13824 | 0.002402 | 0.00060201
27 | 0.98167 | -0.12816 | 0 | 0
28 | 0.98114 | -0.13197 | 0.0020072 | 0.00050305
29 | 0.98 | -0.14018 | 0.0011051 | 0.00027696
30 | 0.99115 | -0.061843 | 0.0017828 | 0.00044681
31 | 0.99126 | -0.061037 | 0.0013697 | 0.00034327
32 | 0.99071 | -0.064892 | 0.0033804 | 0.0008472
33 | 0.99084 | -0.064004 | 0.0019384 | 0.00048581
34 | 0.98997 | -0.070138 | 0.0035825 | 0.00089785
35 | 0.98966 | -0.072307 | 0 | 0
36 | 0.98884 | -0.078117 | 0.011603 | 0.0029079
37 | 0.99036 | -0.067385 | 0.0067888 | 0.0017014
38 | 0.99026 | -0.068101 | 0.0017506 | 0.00043874
39 | 0.99022 | -0.068364 | 0.0035359 | 0.00088617
40 | 0.97995 | -0.14048 | 0.0013489 | 0.00033807
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0045205 | 0.0011327 | -0.0045203 | -0.0011327 | 1.5111e-07 | -6.1402e-09 | 0.0068772 | 0.0068772 | 0.0068772 | 0.97809 | -0.15368 | 0.97805 | -0.15392 | 2.5471
1 | -0.0061441 | -0.0015396 | 0.0061445 | 0.0015396 | 4.434e-07 | 6.8457e-08 | 0.0093472 | 0.0093472 | 0.0093472 | 0.97809 | -0.15368 | 0.97816 | -0.15316 | 3.4619
2 | 0.0020354 | 0.00050989 | -0.0020353 | -0.00051 | 6.1116e-08 | -1.0467e-07 | 0.0030966 | 0.0030966 | 0.0030966 | 0.97805 | -0.15392 | 0.97802 | -0.15414 | 1.1469
3 | -0.035177 | -0.0088227 | 0.035199 | 0.0088308 | 2.1488e-05 | 8.1135e-06 | 0.053515 | 0.053515 | 0.053515 | 0.97816 | -0.15316 | 0.97878 | -0.14876 | 19.8205
4 | 0.029033 | 0.0072831 | -0.029015 | -0.0072763 | 1.8019e-05 | 6.7445e-06 | 0.044168 | 0.044168 | 0.044168 | 0.97816 | -0.15316 | 0.97753 | -0.15764 | 16.3586
5 | 0.00037773 | 9.456e-05 | -0.00037773 | -9.4667e-05 | 1.7608e-09 | -1.0654e-07 | 0.00057466 | 0.0005747 | 0.0005747 | 0.97802 | -0.15414 | 0.97802 | -0.15417 | 0.21285
6 | -0.042436 | -0.010644 | 0.042497 | 0.010667 | 6.0598e-05 | 2.3013e-05 | 0.064518 | 0.064518 | 0.064518 | 0.97878 | -0.14876 | 0.98022 | -0.13847 | 23.8955
7 | 0.0072374 | 0.001813 | -0.0072364 | -0.0018128 | 9.5317e-07 | 2.0804e-07 | 0.011003 | 0.011003 | 0.011003 | 0.97878 | -0.14876 | 0.97864 | -0.14971 | 4.075
8 | 0.025426 | 0.006377 | -0.025413 | -0.0063719 | 1.363e-05 | 5.0595e-06 | 0.038706 | 0.038706 | 0.038706 | 0.97753 | -0.15764 | 0.97699 | -0.16151 | 14.3356
9 | -0.046118 | -0.011574 | 0.046119 | 0.011575 | 1.4876e-06 | 5.6602e-07 | 0.070015 | 0.070015 | 0.070015 | 0.98022 | -0.13847 | 0.98025 | -0.13824 | 25.9313
10 | 0.0056128 | 0.0014059 | -0.0056112 | -0.0014057 | 1.6351e-06 | 1.7694e-07 | 0.008534 | 0.0085341 | 0.0085341 | 0.97864 | -0.14971 | 0.97835 | -0.15182 | 3.1608
11 | 0.022444 | 0.0056285 | -0.022415 | -0.0056177 | 2.9259e-05 | 1.0752e-05 | 0.034185 | 0.034186 | 0.034186 | 0.97699 | -0.16151 | 0.97568 | -0.17092 | 12.6614
12 | 0.0029682 | 0.00074345 | -0.0029677 | -0.00074377 | 5.3615e-07 | -3.2017e-07 | 0.0045206 | 0.0045208 | 0.0045208 | 0.97699 | -0.16151 | 0.97681 | -0.16281 | 1.6744
13 | -0.0014003 | -0.00035081 | 0.0014004 | 0.00035057 | 6.1148e-08 | -2.4763e-07 | 0.0021301 | 0.00213 | 0.0021301 | 0.9782 | -0.15286 | 0.97825 | -0.15255 | 0.78893
14 | 0.00076409 | 0.00019136 | -0.00076408 | -0.0001915 | 9.6219e-09 | -1.3959e-07 | 0.0011623 | 0.0011623 | 0.0011623 | 0.9782 | -0.15286 | 0.97819 | -0.15295 | 0.43049
15 | -0.0033329 | -0.0008349 | 0.0033332 | 0.00083476 | 3.3717e-07 | -1.3431e-07 | 0.0050696 | 0.0050695 | 0.0050696 | 0.97825 | -0.15255 | 0.97835 | -0.15182 | 1.8776
16 | 0.046013 | 0.011556 | -0.045917 | -0.01152 | 9.5955e-05 | 3.6485e-05 | 0.068807 | 0.068807 | 0.068807 | 0.99519 | -0.033385 | 0.99305 | -0.048418 | 25.4841
17 | -0.051168 | -0.012848 | 0.051231 | 0.012872 | 6.2905e-05 | 2.397e-05 | 0.076516 | 0.076516 | 0.076516 | 0.99519 | -0.033385 | 0.99645 | -0.024549 | 28.3392
18 | 0.038902 | 0.0097616 | -0.038859 | -0.0097454 | 4.2929e-05 | 1.625e-05 | 0.058296 | 0.058297 | 0.058297 | 0.99305 | -0.048418 | 0.99192 | -0.056379 | 21.5913
19 | -0.10684 | -0.026934 | 0.10721 | 0.027075 | 0.0003687 | 0.00014059 | 0.1596 | 0.1596 | 0.1596 | 0.99645 | -0.024549 | 1 | 0 | 29.556
20 | 0.055609 | 0.014062 | -0.054941 | -0.013807 | 0.00066799 | 0.00025492 | 0.083086 | 0.083087 | 0.083087 | 0.99645 | -0.024549 | 0.98411 | -0.11083 | 30.773
21 | 0.035801 | 0.0089789 | -0.035793 | -0.0089758 | 8.2987e-06 | 3.1323e-06 | 0.053709 | 0.053709 | 0.053709 | 0.99192 | -0.056379 | 0.99168 | -0.058051 | 19.8921
22 | 0.0069813 | 0.0017495 | -0.0069786 | -0.001749 | 2.6852e-06 | 5.0985e-07 | 0.010388 | 0.010388 | 0.010388 | 1 | 0 | 0.9996 | -0.0027791 | 3.8476
23 | 0.054941 | 0.013807 | -0.05485 | -0.013772 | 9.1874e-05 | 3.5066e-05 | 0.083087 | 0.083087 | 0.083087 | 0.98411 | -0.11083 | 0.98241 | -0.12286 | 30.7731
24 | 0.020391 | 0.0051144 | -0.02038 | -0.0051105 | 1.0714e-05 | 3.8843e-06 | 0.030598 | 0.030598 | 0.030598 | 0.99168 | -0.058051 | 0.99115 | -0.061843 | 11.3325
25 | 0.015402 | 0.0038614 | -0.015395 | -0.0038592 | 6.3681e-06 | 2.2028e-06 | 0.023111 | 0.023111 | 0.023111 | 0.99168 | -0.058051 | 0.99126 | -0.061037 | 8.5596
26 | 0.053095 | 0.013332 | -0.053055 | -0.013317 | 3.9093e-05 | 1.4913e-05 | 0.080429 | 0.080429 | 0.080429 | 0.98241 | -0.12286 | 0.98167 | -0.12816 | 29.7886
27 | 0.0021626 | 0.00054192 | -0.0021625 | -0.00054198 | 4.1238e-08 | -6.0011e-08 | 0.0032982 | 0.0032982 | 0.0032982 | 0.97568 | -0.17092 | 0.97566 | -0.17106 | 1.2215
28 | -0.048521 | -0.012177 | 0.048589 | 0.012203 | 6.7977e-05 | 2.5892e-05 | 0.073661 | 0.073661 | 0.073661 | 0.98025 | -0.13824 | 0.98167 | -0.12816 | 27.2818
29 | 0.0044663 | 0.0011147 | -0.004464 | -0.0011149 | 2.3349e-06 | -1.3398e-07 | 0.0067684 | 0.0067688 | 0.0067688 | 0.98167 | -0.12816 | 0.98114 | -0.13197 | 2.507
30 | 0.0024568 | 0.0006118 | -0.002454 | -0.00061477 | 2.7711e-06 | -2.9706e-06 | 0.0037246 | 0.0037261 | 0.0037261 | 0.98114 | -0.13197 | 0.98 | -0.14018 | 1.38
31 | 0.001349 | 0.00033781 | -0.0013489 | -0.00033807 | 5.6966e-08 | -2.5227e-07 | 0.0020481 | 0.0020482 | 0.0020482 | 0.98 | -0.14018 | 0.97995 | -0.14048 | 0.75861
32 | 0.018597 | 0.0046637 | -0.018589 | -0.0046609 | 7.8557e-06 | 2.8134e-06 | 0.027921 | 0.027921 | 0.027921 | 0.99115 | -0.061843 | 0.99071 | -0.064892 | 10.3413
33 | 0.014026 | 0.0035159 | -0.01402 | -0.003514 | 5.7611e-06 | 1.9474e-06 | 0.021055 | 0.021055 | 0.021055 | 0.99126 | -0.061037 | 0.99084 | -0.064004 | 7.7981
34 | 0.015209 | 0.0038137 | -0.015198 | -0.0038099 | 1.105e-05 | 3.8132e-06 | 0.022844 | 0.022844 | 0.022844 | 0.99071 | -0.064892 | 0.98997 | -0.070138 | 8.4609
35 | 0.012082 | 0.0030281 | -0.012076 | -0.0030263 | 5.654e-06 | 1.8203e-06 | 0.018144 | 0.018144 | 0.018144 | 0.99084 | -0.064004 | 0.99036 | -0.067385 | 6.72
36 | 0.011616 | 0.002912 | -0.011612 | -0.0029109 | 3.4898e-06 | 1.1064e-06 | 0.01746 | 0.01746 | 0.01746 | 0.98997 | -0.070138 | 0.98966 | -0.072307 | 6.4666
37 | 0.011612 | 0.0029109 | -0.011603 | -0.0029079 | 9.3386e-06 | 2.9615e-06 | 0.01746 | 0.01746 | 0.01746 | 0.98966 | -0.072307 | 0.98884 | -0.078117 | 6.4666
38 | 0.0052871 | 0.0013249 | -0.0052866 | -0.0013249 | 5.2378e-07 | 3.0313e-08 | 0.0079438 | 0.0079439 | 0.0079439 | 0.99036 | -0.067385 | 0.99026 | -0.068101 | 2.9422
39 | 0.003536 | 0.00088613 | -0.0035359 | -0.00088617 | 1.2876e-07 | -4.4503e-08 | 0.0053133 | 0.0053134 | 0.0053134 | 0.99026 | -0.068101 | 0.99022 | -0.068364 | 1.9679

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11955 | 0.029968

## res_load
| p_mw | q_mvar
0 | 0.0016236 | 0.00040691
1 | 0.0024849 | 0.00062279
2 | 0.0016576 | 0.00041544
3 | 0.0035884 | 0.00089933
4 | 0.00037773 | 9.4667e-05
5 | 0.0036209 | 0.00090749
6 | 0.0016236 | 0.00040691
7 | 0.00063624 | 0.00015946
8 | 0.0019325 | 0.00048433
9 | 0.00076408 | 0.0001915
10 | 0.002278 | 0.00057091
11 | 0.0051557 | 0.0012921
12 | 0.0070145 | 0.001758
13 | 0.0030584 | 0.00076651
14 | 0.0045639 | 0.0011438
15 | 0.0069786 | 0.001749
16 | 0.001755 | 0.00043984
17 | 0.0029677 | 0.00074377
18 | 0.020253 | 0.0050758
19 | 0.0021625 | 0.00054198
20 | 0.002402 | 0.00060201
21 | 0.0020072 | 0.00050305
22 | 0.0011051 | 0.00027696
23 | 0.0017828 | 0.00044681
24 | 0.0013697 | 0.00034327
25 | 0.0033804 | 0.0008472
26 | 0.0019384 | 0.00048581
27 | 0.0035825 | 0.00089785
28 | 0.011603 | 0.0029079
29 | 0.0067888 | 0.0017014
30 | 0.0017506 | 0.00043874
31 | 0.0035359 | 0.00088617
32 | 0.0013489 | 0.00033807

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1