## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1008-7_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1008-7_0_4_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_1008-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1008-7_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1008-7_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1008-7_0_4_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_1008-7_0_4_node_136 | 0.4 | n |  | TRUE
8 | bus_LV_1008-7_0_4_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1008-7_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1008-7_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1008-7_0_4_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_1008-7_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1008-7_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1008-7_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1008-7_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1008-7_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1008-7_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1008-7_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1008-7_0_4_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1008-7_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1008-7_0_4_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_1008-7_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1008-7_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1008-7_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1008-7_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_1008-7_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1008-7_0_4_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1008-7_0_4_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_1008-7_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1008-7_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1008-7_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1008-7_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1008-7_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1008-7_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_1008-7_0_4_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1008-7_0_4_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1008-7_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_1008-7_0_4_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1008-7_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1008-7_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1008-7_0_4_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_1008-7_0_4_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_1008-7_0_4_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_1008-7_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_1008-7_0_4_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_1008-7_0_4_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_1008-7_0_4_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_1008-7_0_4_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_1008-7_0_4_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_1008-7_0_4_node_280 | 0.4 | n |  | TRUE
51 | bus_LV_1008-7_0_4_node_279 | 0.4 | n |  | TRUE
52 | bus_LV_1008-7_0_4_node_135 | 0.4 | n |  | TRUE
53 | bus_LV_1008-7_0_4_node_284 | 0.4 | n |  | TRUE
54 | bus_LV_1008-7_0_4_node_288 | 0.4 | n |  | TRUE
55 | bus_LV_1008-7_0_4_node_100 | 0.4 | n |  | TRUE
56 | bus_LV_1008-7_0_4_node_112 | 0.4 | n |  | TRUE
57 | bus_LV_1008-7_0_4_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_1008-7_0_4_node_109 | 0.4 | n |  | TRUE
59 | bus_LV_1008-7_0_4_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_1008-7_0_4_node_111 | 0.4 | n |  | TRUE
61 | bus_LV_1008-7_0_4_node_179 | 0.4 | n |  | TRUE
62 | bus_LV_1008-7_0_4_node_177 | 0.4 | n |  | TRUE
63 | bus_LV_1008-7_0_4_node_132 | 0.4 | n |  | TRUE
64 | bus_LV_1008-7_0_4_node_291 | 0.4 | n |  | TRUE
65 | bus_LV_1008-7_0_4_node_133 | 0.4 | n |  | TRUE
66 | bus_LV_1008-7_0_4_node_134 | 0.4 | n |  | TRUE
67 | bus_LV_1008-7_0_4_node_165 | 0.4 | n |  | TRUE
68 | bus_LV_1008-7_0_4_node_178 | 0.4 | n |  | TRUE
69 | bus_LV_1008-7_0_4_node_180 | 0.4 | n |  | TRUE
70 | bus_LV_1008-7_0_4_node_181 | 0.4 | n |  | TRUE
71 | bus_LV_1008-7_0_4_node_272 | 0.4 | n |  | TRUE
72 | bus_LV_1008-7_0_4_node_278 | 0.4 | n |  | TRUE
73 | bus_LV_1008-7_0_4_node_293 | 0.4 | n |  | TRUE
74 | bus_LV_1008-7_0_4_node_277 | 0.4 | n |  | TRUE
75 | bus_LV_1008-7_0_4_node_182 | 0.4 | n |  | TRUE
76 | bus_LV_1008-7_0_4_node_183 | 0.4 | n |  | TRUE
77 | bus_LV_1008-7_0_4_node_184 | 0.4 | n |  | TRUE
78 | bus_LV_1008-7_0_4_node_231 | 0.4 | n |  | TRUE
79 | bus_LV_1008-7_0_4_node_186 | 0.4 | n |  | TRUE
80 | bus_LV_1008-7_0_4_node_224 | 0.4 | n |  | TRUE
81 | bus_LV_1008-7_0_4_node_227 | 0.4 | n |  | TRUE
82 | bus_LV_1008-7_0_4_node_213 | 0.4 | n |  | TRUE
83 | bus_LV_1008-7_0_4_node_214 | 0.4 | n |  | TRUE
84 | bus_LV_1008-7_0_4_node_215 | 0.4 | n |  | TRUE
85 | bus_LV_1008-7_0_4_node_216 | 0.4 | n |  | TRUE
86 | bus_LV_1008-7_0_4_node_217 | 0.4 | n |  | TRUE
87 | bus_LV_1008-7_0_4_node_218 | 0.4 | n |  | TRUE
88 | bus_LV_1008-7_0_4_node_219 | 0.4 | n |  | TRUE
89 | bus_LV_1008-7_0_4_node_220 | 0.4 | n |  | TRUE
90 | bus_LV_1008-7_0_4_node_221 | 0.4 | n |  | TRUE
91 | bus_LV_1008-7_0_4_node_222 | 0.4 | n |  | TRUE
92 | bus_LV_1008-7_0_4_node_223 | 0.4 | n |  | TRUE
93 | bus_LV_1008-7_0_4_node_225 | 0.4 | n |  | TRUE
94 | bus_LV_1008-7_0_4_node_290 | 0.4 | n |  | TRUE
95 | bus_LV_1008-7_0_4_node_226 | 0.4 | n |  | TRUE
96 | bus_LV_1008-7_0_4_node_228 | 0.4 | n |  | TRUE
97 | bus_LV_1008-7_0_4_node_229 | 0.4 | n |  | TRUE
98 | bus_LV_1008-7_0_4_node_230 | 0.4 | n |  | TRUE
99 | bus_LV_1008-7_0_4_node_232 | 0.4 | n |  | TRUE
100 | bus_LV_1008-7_0_4_node_273 | 0.4 | n |  | TRUE
101 | bus_LV_1008-7_0_4_node_274 | 0.4 | n |  | TRUE
102 | bus_LV_1008-7_0_4_node_285 | 0.4 | n |  | TRUE
103 | bus_LV_1008-7_0_4_node_275 | 0.4 | n |  | TRUE
104 | bus_LV_1008-7_0_4_node_276 | 0.4 | n |  | TRUE
105 | bus_LV_1008-7_0_4_node_292 | 0.4 | n |  | TRUE
106 | bus_LV_1008-7_0_4_node_281 | 0.4 | n |  | TRUE
107 | bus_LV_1008-7_0_4_node_282 | 0.4 | n |  | TRUE
108 | bus_LV_1008-7_0_4_node_283 | 0.4 | n |  | TRUE
109 | bus_LV_1008-7_0_4_node_286 | 0.4 | n |  | TRUE
110 | bus_LV_1008-7_0_4_node_287 | 0.4 | n |  | TRUE
111 | bus_MV_125_0_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-7_0_4_load_0 | 0 | 0.00061313 | 0.00015367 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-7_0_4_load_43 | 6 | 0.0007348 | 0.00018416 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-7_0_4_load_136 | 7 | 0.00097597 | 0.0002446 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-7_0_4_load_26 | 8 | 0.010581 | 0.002652 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-7_0_4_load_23 | 11 | 0.012892 | 0.003231 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-7_0_4_load_8 | 12 | 0.010768 | 0.0026987 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-7_0_4_load_11 | 15 | 0.0024634 | 0.00061738 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-7_0_4_load_12 | 16 | 0.011361 | 0.0028474 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-7_0_4_load_13 | 17 | 0.010259 | 0.0025711 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-7_0_4_load_18 | 22 | 0.012326 | 0.0030891 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-7_0_4_load_16 | 23 | 0.0013258 | 0.00033228 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-7_0_4_load_19 | 24 | 0.0107 | 0.0026818 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-7_0_4_load_32 | 28 | 0.0018591 | 0.00046593 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-7_0_4_load_35 | 29 | 0.0038455 | 0.00096376 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-7_0_4_load_27 | 31 | 0.011908 | 0.0029844 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-7_0_4_load_38 | 32 | 0.019969 | 0.0050048 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-7_0_4_load_30 | 33 | 0.007291 | 0.0018273 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-7_0_4_load_31 | 34 | 0.0029649 | 0.00074309 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-7_0_4_load_33 | 35 | 0.00083824 | 0.00021008 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-7_0_4_load_34 | 36 | 0.0022856 | 0.00057283 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1008-7_0_4_load_51 | 37 | 0.0022578 | 0.00056585 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1008-7_0_4_load_36 | 38 | 0.00030286 | 7.5903e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1008-7_0_4_load_41 | 40 | 0.0003414 | 8.5562e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1008-7_0_4_load_44 | 42 | 0.00025621 | 6.4213e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1008-7_0_4_load_52 | 43 | 0.00013896 | 3.4826e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1008-7_0_4_load_56 | 47 | 0.011121 | 0.0027871 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1008-7_0_4_load_57 | 48 | 0.00022187 | 5.5606e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1008-7_0_4_load_58 | 49 | 0.00016542 | 4.1459e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1008-7_0_4_load_280 | 50 | 0.00021761 | 5.4538e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1008-7_0_4_load_279 | 51 | 0.00032674 | 8.189e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1008-7_0_4_load_135 | 52 | 0.003482 | 0.00087267 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1008-7_0_4_load_284 | 53 | 0.0017541 | 0.00043963 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1008-7_0_4_load_288 | 54 | 0.00013785 | 3.4549e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1008-7_0_4_load_112 | 56 | 0.001246 | 0.00031228 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1008-7_0_4_load_108 | 57 | 0.00011939 | 2.9922e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1008-7_0_4_load_111 | 60 | 0.00012006 | 3.0091e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1008-7_0_4_load_179 | 61 | 0.0001121 | 2.8096e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1008-7_0_4_load_177 | 62 | 0.00022217 | 5.5681e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1008-7_0_4_load_132 | 63 | 0.00044363 | 0.00011119 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1008-7_0_4_load_291 | 64 | 0.00020574 | 5.1564e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1008-7_0_4_load_133 | 65 | 0.00043 | 0.00010777 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1008-7_0_4_load_134 | 66 | 0.00018284 | 4.5823e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1008-7_0_4_load_165 | 67 | 0.00071862 | 0.0001801 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1008-7_0_4_load_180 | 69 | 7.7357e-05 | 1.9388e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1008-7_0_4_load_272 | 71 | 0.00048554 | 0.00012169 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1008-7_0_4_load_278 | 72 | 0.00027494 | 6.8907e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1008-7_0_4_load_293 | 73 | 0.00017028 | 4.2676e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1008-7_0_4_load_182 | 75 | 0.00020167 | 5.0543e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1008-7_0_4_load_231 | 78 | 0.0002698 | 6.7618e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1008-7_0_4_load_227 | 81 | 5.7369e-05 | 1.4378e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1008-7_0_4_load_213 | 82 | 0.00072616 | 0.00018199 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1008-7_0_4_load_214 | 83 | 0.0001703 | 4.2682e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1008-7_0_4_load_215 | 84 | 0.00052956 | 0.00013272 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1008-7_0_4_load_216 | 85 | 0.00016334 | 4.0936e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1008-7_0_4_load_217 | 86 | 0.00014789 | 3.7064e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1008-7_0_4_load_218 | 87 | 7.8139e-05 | 1.9583e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1008-7_0_4_load_219 | 88 | 0.00022669 | 5.6813e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1008-7_0_4_load_220 | 89 | 0.00060967 | 0.0001528 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1008-7_0_4_load_221 | 90 | 0.00017305 | 4.3369e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1008-7_0_4_load_222 | 91 | 0.00019282 | 4.8326e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1008-7_0_4_load_223 | 92 | 0.00015003 | 3.7602e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1008-7_0_4_load_225 | 93 | 0.00019218 | 4.8165e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1008-7_0_4_load_290 | 94 | 0.00025038 | 6.2752e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1008-7_0_4_load_226 | 95 | 6.0599e-05 | 1.5187e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1008-7_0_4_load_228 | 96 | 0.00061379 | 0.00015383 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1008-7_0_4_load_229 | 97 | 0.00011763 | 2.948e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1008-7_0_4_load_230 | 98 | 0.00017183 | 4.3066e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1008-7_0_4_load_232 | 99 | 0.00017679 | 4.4308e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1008-7_0_4_load_273 | 100 | 0.00064152 | 0.00016078 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1008-7_0_4_load_274 | 101 | 0.00015589 | 3.907e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1008-7_0_4_load_285 | 102 | 0.00052112 | 0.0001306 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1008-7_0_4_load_275 | 103 | 0.0002139 | 5.3608e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1008-7_0_4_load_292 | 105 | 0.00039023 | 9.78e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1008-7_0_4_load_281 | 106 | 0.00083652 | 0.00020965 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1008-7_0_4_load_282 | 107 | 9.8788e-05 | 2.4759e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1008-7_0_4_load_283 | 108 | 0.00036994 | 9.2717e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1008-7_0_4_load_286 | 109 | 0.00019309 | 4.8394e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1008-7_0_4_load_287 | 110 | 0.00011955 | 2.9961e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-7_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.24964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-7_0_4_line_1 | NAYY 4x150 SE | 1 | 5 | 0.026194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-7_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.042928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1008-7_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.26006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1008-7_0_4_line_4 | NAYY 4x150 SE | 3 | 6 | 0.017457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1008-7_0_4_line_5 | NAYY 4x150 SE | 4 | 7 | 0.016105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1008-7_0_4_line_6 | NAYY 4x150 SE | 5 | 8 | 0.065818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-7_0_4_line_7 | NAYY 4x150 SE | 6 | 40 | 0.026433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1008-7_0_4_line_8 | NAYY 4x150 SE | 7 | 52 | 0.011815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1008-7_0_4_line_9 | NAYY 4x150 SE | 8 | 30 | 0.01095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-7_0_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.022833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-7_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.010906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-7_0_4_line_12 | NAYY 4x150 SE | 10 | 21 | 0.026618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-7_0_4_line_13 | NAYY 4x150 SE | 10 | 32 | 0.032764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-7_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0088324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1008-7_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.017491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1008-7_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.018351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1008-7_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.017794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-7_0_4_line_18 | NAYY 4x150 SE | 14 | 17 | 0.015465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1008-7_0_4_line_19 | NAYY 4x150 SE | 15 | 18 | 0.019635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1008-7_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.013137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-7_0_4_line_21 | NAYY 4x150 SE | 18 | 26 | 0.21624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1008-7_0_4_line_22 | NAYY 4x150 SE | 18 | 23 | 0.0078904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-7_0_4_line_23 | NAYY 4x150 SE | 19 | 22 | 0.019951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-7_0_4_line_24 | NAYY 4x150 SE | 19 | 24 | 0.013134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-7_0_4_line_25 | NAYY 4x150 SE | 20 | 21 | 0.0255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-7_0_4_line_26 | NAYY 4x150 SE | 20 | 22 | 0.025255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-7_0_4_line_27 | NAYY 4x150 SE | 21 | 33 | 0.018607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-7_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.019456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-7_0_4_line_29 | NAYY 4x150 SE | 25 | 31 | 0.014854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1008-7_0_4_line_30 | NAYY 4x150 SE | 26 | 29 | 0.039772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1008-7_0_4_line_31 | NAYY 4x150 SE | 26 | 27 | 0.061515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1008-7_0_4_line_32 | NAYY 4x150 SE | 27 | 28 | 0.1564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1008-7_0_4_line_33 | NAYY 4x150 SE | 28 | 34 | 0.015859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1008-7_0_4_line_34 | NAYY 4x150 SE | 29 | 38 | 0.058782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1008-7_0_4_line_35 | NAYY 4x150 SE | 30 | 31 | 0.017167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1008-7_0_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.018627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1008-7_0_4_line_37 | NAYY 4x150 SE | 35 | 36 | 0.013265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1008-7_0_4_line_38 | NAYY 4x150 SE | 36 | 37 | 0.0012172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1008-7_0_4_line_39 | NAYY 4x150 SE | 38 | 39 | 0.021942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1008-7_0_4_line_40 | NAYY 4x150 SE | 39 | 40 | 0.023911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1008-7_0_4_line_41 | NAYY 4x150 SE | 39 | 41 | 0.008102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1008-7_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.019513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1008-7_0_4_line_43 | NAYY 4x150 SE | 43 | 44 | 0.033084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1008-7_0_4_line_44 | NAYY 4x150 SE | 43 | 45 | 0.04143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1008-7_0_4_line_45 | NAYY 4x150 SE | 44 | 46 | 0.18699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1008-7_0_4_line_46 | NAYY 4x150 SE | 44 | 47 | 0.06097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1008-7_0_4_line_47 | NAYY 4x150 SE | 45 | 48 | 0.015889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1008-7_0_4_line_48 | NAYY 4x150 SE | 45 | 49 | 0.029176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1008-7_0_4_line_49 | NAYY 4x150 SE | 46 | 50 | 0.01747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1008-7_0_4_line_50 | NAYY 4x150 SE | 46 | 51 | 0.0082155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1008-7_0_4_line_51 | NAYY 4x150 SE | 47 | 52 | 0.10779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1008-7_0_4_line_52 | NAYY 4x150 SE | 48 | 53 | 0.045189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1008-7_0_4_line_53 | NAYY 4x150 SE | 49 | 54 | 0.031678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1008-7_0_4_line_54 | NAYY 4x150 SE | 50 | 106 | 0.0097959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1008-7_0_4_line_55 | NAYY 4x150 SE | 54 | 110 | 0.022545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_1008-7_0_4_line_56 | NAYY 4x150 SE | 55 | 56 | 0.38634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1008-7_0_4_line_57 | NAYY 4x150 SE | 55 | 57 | 0.021948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1008-7_0_4_line_58 | NAYY 4x150 SE | 56 | 64 | 0.0098976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1008-7_0_4_line_59 | NAYY 4x150 SE | 57 | 58 | 0.040629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1008-7_0_4_line_60 | NAYY 4x150 SE | 58 | 59 | 0.31409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1008-7_0_4_line_61 | NAYY 4x150 SE | 58 | 60 | 0.015157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1008-7_0_4_line_62 | NAYY 4x150 SE | 59 | 61 | 0.19949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1008-7_0_4_line_63 | NAYY 4x150 SE | 59 | 62 | 0.005404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1008-7_0_4_line_64 | NAYY 4x150 SE | 60 | 63 | 0.028447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1008-7_0_4_line_65 | NAYY 4x150 SE | 61 | 71 | 0.030727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1008-7_0_4_line_66 | NAYY 4x150 SE | 62 | 68 | 0.2128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1008-7_0_4_line_67 | NAYY 4x150 SE | 63 | 65 | 0.041914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1008-7_0_4_line_68 | NAYY 4x150 SE | 64 | 94 | 0.021287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1008-7_0_4_line_69 | NAYY 4x150 SE | 65 | 66 | 0.029301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1008-7_0_4_line_70 | NAYY 4x150 SE | 66 | 67 | 0.0050655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1008-7_0_4_line_71 | NAYY 4x150 SE | 68 | 69 | 0.2018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1008-7_0_4_line_72 | NAYY 4x150 SE | 68 | 70 | 0.10614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1008-7_0_4_line_73 | NAYY 4x150 SE | 69 | 72 | 0.010773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1008-7_0_4_line_74 | NAYY 4x150 SE | 70 | 73 | 0.042711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1008-7_0_4_line_75 | NAYY 4x150 SE | 70 | 74 | 0.010873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1008-7_0_4_line_76 | NAYY 4x150 SE | 71 | 100 | 0.21857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1008-7_0_4_line_77 | NAYY 4x150 SE | 74 | 105 | 0.053449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1008-7_0_4_line_78 | NAYY 4x150 SE | 74 | 104 | 0.11021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1008-7_0_4_line_79 | NAYY 4x150 SE | 75 | 76 | 0.025045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1008-7_0_4_line_80 | NAYY 4x150 SE | 76 | 77 | 0.36534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1008-7_0_4_line_81 | NAYY 4x150 SE | 77 | 78 | 0.043223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1008-7_0_4_line_82 | NAYY 4x150 SE | 78 | 99 | 0.031231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1008-7_0_4_line_83 | NAYY 4x150 SE | 79 | 80 | 0.041394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1008-7_0_4_line_84 | NAYY 4x150 SE | 79 | 81 | 0.25274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1008-7_0_4_line_85 | NAYY 4x150 SE | 80 | 93 | 0.14533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_1008-7_0_4_line_86 | NAYY 4x150 SE | 80 | 92 | 0.32792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1008-7_0_4_line_87 | NAYY 4x150 SE | 81 | 95 | 0.034322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1008-7_0_4_line_88 | NAYY 4x150 SE | 82 | 83 | 0.048514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1008-7_0_4_line_89 | NAYY 4x150 SE | 83 | 84 | 0.092273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1008-7_0_4_line_90 | NAYY 4x150 SE | 84 | 85 | 0.026766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1008-7_0_4_line_91 | NAYY 4x150 SE | 85 | 86 | 0.021135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1008-7_0_4_line_92 | NAYY 4x150 SE | 86 | 87 | 0.0144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1008-7_0_4_line_93 | NAYY 4x150 SE | 87 | 88 | 0.05814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1008-7_0_4_line_94 | NAYY 4x150 SE | 88 | 89 | 0.037284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1008-7_0_4_line_95 | NAYY 4x150 SE | 89 | 90 | 0.029222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1008-7_0_4_line_96 | NAYY 4x150 SE | 90 | 91 | 0.30653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1008-7_0_4_line_97 | NAYY 4x150 SE | 91 | 92 | 0.023742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1008-7_0_4_line_98 | NAYY 4x150 SE | 93 | 94 | 0.0023797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1008-7_0_4_line_99 | NAYY 4x150 SE | 95 | 96 | 0.00082261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1008-7_0_4_line_100 | NAYY 4x150 SE | 96 | 97 | 0.22823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1008-7_0_4_line_101 | NAYY 4x150 SE | 97 | 98 | 0.38958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1008-7_0_4_line_102 | NAYY 4x150 SE | 98 | 99 | 0.0001279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1008-7_0_4_line_103 | NAYY 4x150 SE | 100 | 101 | 0.016116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1008-7_0_4_line_104 | NAYY 4x150 SE | 101 | 102 | 0.018738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_1008-7_0_4_line_105 | NAYY 4x150 SE | 102 | 109 | 0.011784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1008-7_0_4_line_106 | NAYY 4x150 SE | 103 | 104 | 0.18016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1008-7_0_4_line_107 | NAYY 4x150 SE | 106 | 107 | 0.00048395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1008-7_0_4_line_108 | NAYY 4x150 SE | 107 | 108 | 0.0023004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1008-7_0_4_line_109 | NAYY 4x150 SE | 109 | 110 | 0.033698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-7_0_4_trafo_13 | 0.25 MVA 20/0.4 kV | 111 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2643411.8633 | 1199872.1747 | 2643358.5486 | 1199796.5567 | 2643332.2787 | 1199748.8173 | 2643314.1589 | 1199704.6946 | 2643296.8727 | 1199652.5534
1 | 2643411.8633 | 1199872.1747 | 2643417.157 | 1199866.5878 | 2643418.5053 | 1199863.3402 | 2643416.4876 | 1199860.2127 | 2643416.6232 | 1199855.1775 | 2643418.9111 | 1199849.3909
2 | 2643298.5044 | 1199352.6836 | 2643285.2016 | 1199311.8644
3 | 2643167.7718 | 1199343.6449 | 2643168.891 | 1199329.9452 | 2643171.9716 | 1199292.3908 | 2643171.2144 | 1199280.2119 | 2643170.0267 | 1199272.8214 | 2643169.3009 | 1199266.835 | 2643169.0921 | 1199262.0086 | 2643169.5074 | 1199256.1638 | 2643173.1629 | 1199232.8549 | 2643210.6487 | 1199244.143 | 2643218.5705 | 1199246.8462 | 2643226.2872 | 1199249.4812 | 2643234.8926 | 1199252.4228 | 2643247.0955 | 1199257.9919 | 2643258.0677 | 1199265.2864 | 2643270.6658 | 1199275.172 | 2643279.1915 | 1199284.8947 | 2643283.2797 | 1199292.3173 | 2643282.6339 | 1199297.3932 | 2643282.8784 | 1199301.4862 | 2643283.8166 | 1199306.5069 | 2643285.2016 | 1199311.8644
4 | 2643298.5044 | 1199352.6836 | 2643300.2628 | 1199370.052
5 | 2643167.7718 | 1199343.6449 | 2643166.4568 | 1199359.6956
6 | 2643418.9111 | 1199849.3909 | 2643415.9638 | 1199847.435 | 2643412.699 | 1199843.0644 | 2643411.4502 | 1199832.6162 | 2643412.529 | 1199826.6317 | 2643418.0328 | 1199816.2325 | 2643419.5148 | 1199812.3856 | 2643418.8667 | 1199808.323 | 2643416.1228 | 1199803.5226 | 2643411.6688 | 1199798.3096 | 2643409.5636 | 1199790.7639
7 | 2643303.0172 | 1199396.3402 | 2643302.5617 | 1199392.7576 | 2643300.2628 | 1199370.052
8 | 2643165.492 | 1199371.4712 | 2643166.4568 | 1199359.6956
9 | 2643409.4725 | 1199779.9389 | 2643408.8343 | 1199788.15 | 2643409.5636 | 1199790.7639
10 | 2643452.2489 | 1199739.4489 | 2643438.8368 | 1199757.9508
11 | 2643438.8368 | 1199757.9508 | 2643435.2482 | 1199755.1898 | 2643432.3387 | 1199755.3577 | 2643429.6976 | 1199757.599
12 | 2643452.2489 | 1199739.4489 | 2643432.0016 | 1199722.1032
13 | 2643452.2489 | 1199739.4489 | 2643472.4093 | 1199713.6224
14 | 2643355.3164 | 1199681.6464 | 2643356.9138 | 1199689.1956 | 2643357.1754 | 1199690.2806
15 | 2643367.2723 | 1199704.3459 | 2643364.3922 | 1199700.4561 | 2643357.6603 | 1199692.2916 | 2643357.1754 | 1199690.2806
16 | 2643355.3164 | 1199681.6464 | 2643370.6496 | 1199671.564
17 | 2643367.2723 | 1199704.3459 | 2643381.9815 | 1199694.3324
18 | 2643367.2723 | 1199704.3459 | 2643370.4279 | 1199719.4859
19 | 2643387.0559 | 1199660.7759 | 2643370.6496 | 1199671.564
20 | 2643379.7968 | 1199728.4057 | 2643370.6419 | 1199720.5127 | 2643370.4279 | 1199719.4859
21 | 2643268.1016 | 1199500.0908 | 2643290.3967 | 1199495.5495 | 2643289.5977 | 1199498.6566 | 2643289.5842 | 1199501.5693 | 2643291.1378 | 1199506.7612 | 2643312.781 | 1199552.2768 | 2643320.2781 | 1199565.205 | 2643358.7114 | 1199620.8369 | 2643370.0405 | 1199637.5951 | 2643387.0559 | 1199660.7759
22 | 2643387.0559 | 1199660.7759 | 2643391.4965 | 1199667.2982
23 | 2643379.7968 | 1199728.4057 | 2643388.26 | 1199724.5983 | 2643392.7529 | 1199719.2168 | 2643395.7072 | 1199717.0554
24 | 2643379.7968 | 1199728.4057 | 2643383.8161 | 1199740.91
25 | 2643416.09 | 1199702.1432 | 2643432.0016 | 1199722.1032
26 | 2643416.09 | 1199702.1432 | 2643395.7072 | 1199717.0554
27 | 2643432.0016 | 1199722.1032 | 2643417.0724 | 1199733.2092
28 | 2643399.5972 | 1199751.7403 | 2643384.2491 | 1199742.2569 | 2643383.8161 | 1199740.91
29 | 2643399.5972 | 1199751.7403 | 2643400.6027 | 1199760.0633 | 2643399.0041 | 1199766.333
30 | 2643268.1016 | 1199500.0908 | 2643263.5166 | 1199460.5839
31 | 2643325.2285 | 1199481.983 | 2643298.0625 | 1199488.3565 | 2643295.4579 | 1199489.505 | 2643293.4216 | 1199491.0356 | 2643291.7552 | 1199493.0024 | 2643290.3967 | 1199495.5495 | 2643268.1016 | 1199500.0908
32 | 2643325.2285 | 1199481.983 | 2643334.2454 | 1199508.9745 | 2643342.8601 | 1199526.3134 | 2643347.4819 | 1199534.6738 | 2643354.4282 | 1199545.8526 | 2643372.9773 | 1199571.746 | 2643388.6236 | 1199590.5701 | 2643407.5055 | 1199613.2784
33 | 2643418.4542 | 1199624.7332 | 2643410.172 | 1199616.4854 | 2643407.5055 | 1199613.2784
34 | 2643263.5166 | 1199460.5839 | 2643259.9314 | 1199429.6922 | 2643287.0194 | 1199423.9842
35 | 2643409.4725 | 1199779.9389 | 2643399.0041 | 1199766.333
36 | 2643418.4542 | 1199624.7332 | 2643431.6527 | 1199637.8769
37 | 2643431.6527 | 1199637.8769 | 2643437.7465 | 1199643.9455 | 2643441.2499 | 1199647.0252
38 | 2643441.2499 | 1199647.0252 | 2643442.1641 | 1199647.8288
39 | 2643308.4897 | 1199419.46 | 2643287.0194 | 1199423.9842
40 | 2643308.4897 | 1199419.46 | 2643304.6218 | 1199408.9594 | 2643303.0172 | 1199396.3402
41 | 2643308.4897 | 1199419.46 | 2643316.6018 | 1199418.9851
42 | 2643316.6018 | 1199418.9851 | 2643316.1313 | 1199399.4779
43 | 2643106.4248 | 1199528.7842 | 2643103.2922 | 1199535.5988 | 2643096.8218 | 1199548.1148 | 2643090.8291 | 1199557.9232
44 | 2643062.9476 | 1199588.4824 | 2643064.727 | 1199586.6719 | 2643070.2886 | 1199580.8643 | 2643087.0432 | 1199563.2973 | 2643090.6813 | 1199558.1651 | 2643090.8291 | 1199557.9232
45 | 2643106.4248 | 1199528.7842 | 2643138.967 | 1199539.1023 | 2643141.8574 | 1199541.6024 | 2643144.4264 | 1199546.4236 | 2643177.6434 | 1199638.2926 | 2643180.3119 | 1199640.9245 | 2643184.7398 | 1199642.4128 | 2643189.641 | 1199642.6706 | 2643195.801 | 1199642.5706 | 2643201.0337 | 1199643.3088 | 2643205.0415 | 1199644.9942 | 2643208.1038 | 1199647.918 | 2643213.3876 | 1199659.496
46 | 2643106.4248 | 1199528.7842 | 2643131.9027 | 1199473.3922
47 | 2643062.9476 | 1199588.4824 | 2643066.7566 | 1199589.2324 | 2643068.9871 | 1199591.383 | 2643073.1073 | 1199599.2813
48 | 2643062.9476 | 1199588.4824 | 2643058.0454 | 1199593.6389 | 2643051.4541 | 1199599.706 | 2643047.5134 | 1199602.4458 | 2643041.6634 | 1199604.9607 | 2643039.7709 | 1199605.3662
49 | 2643213.3876 | 1199659.496 | 2643229.972 | 1199654.0059
50 | 2643213.3876 | 1199659.496 | 2643215.7746 | 1199667.357
51 | 2643165.492 | 1199371.4712 | 2643164.624 | 1199382.0659 | 2643161.9913 | 1199394.4984 | 2643161.1059 | 1199396.9044 | 2643152.7028 | 1199419.7789 | 2643134.665 | 1199467.3866 | 2643131.9027 | 1199473.3922
52 | 2643091.7262 | 1199640.4183 | 2643091.1985 | 1199639.5923 | 2643085.9699 | 1199628.7596 | 2643081.6564 | 1199617.7335 | 2643074.4242 | 1199601.8058 | 2643073.1073 | 1199599.2813
53 | 2643008.3968 | 1199609.4301 | 2643011.1963 | 1199608.8993 | 2643032.8791 | 1199606.843 | 2643039.7709 | 1199605.3662
54 | 2643229.972 | 1199654.0059 | 2643239.2716 | 1199650.9274
55 | 2643008.3968 | 1199609.4301 | 2642997.9765 | 1199611.4057 | 2642991.6268 | 1199613.5279 | 2642987.0059 | 1199616.007
56 | 2642519.3274 | 1200128.0523 | 2642507.1668 | 1200156.3151 | 2642490.294 | 1200174.9279 | 2642473.6816 | 1200213.6873 | 2642441.7897 | 1200247.2464 | 2642377.3667 | 1200319.8638 | 2642370.6926 | 1200339.9723 | 2642374.3029 | 1200349.3587 | 2642435.1996 | 1200428.1569 | 2642441.2714 | 1200440.8598
57 | 2642519.3274 | 1200128.0523 | 2642523.2332 | 1200129.0696 | 2642540.838 | 1200132.3698
58 | 2642443.8188 | 1200450.3972 | 2642443.8188 | 1200450.3972 | 2642441.838 | 1200442.0451 | 2642441.2714 | 1200440.8598
59 | 2642581.0407 | 1200128.5916 | 2642561.546 | 1200132.6329 | 2642541.4796 | 1200132.4901 | 2642540.838 | 1200132.3698
60 | 2642581.0407 | 1200128.5916 | 2642680.0617 | 1200103.9168 | 2642692.0724 | 1200098.9219 | 2642713.4313 | 1200086.5341 | 2642793.7166 | 1200042.9278 | 2642835.2141 | 1200019.634 | 2642856.8405 | 1200011.4287 | 2642869.698 | 1200009.4197
61 | 2642581.0407 | 1200128.5916 | 2642584.1187 | 1200138.9416 | 2642586.7202 | 1200142.4398
62 | 2642869.698 | 1200009.4197 | 2642905.4065 | 1199991.9437 | 2642922.4217 | 1199982.3715 | 2642935.8561 | 1199964.7024 | 2642952.7614 | 1199910.0597 | 2642956.9199 | 1199900.2841 | 2642961.412 | 1199892.8121 | 2642972.6043 | 1199878.9069 | 2642986.5509 | 1199866.2889 | 2642990.5308 | 1199863.5719
63 | 2642869.698 | 1200009.4197 | 2642874.8135 | 1200011.1618
64 | 2642612.2183 | 1200155.0454 | 2642593.5568 | 1200145.6014 | 2642586.7202 | 1200142.4398
65 | 2643017.7932 | 1199850.0566 | 2643011.5826 | 1199851.5272 | 2643001.4086 | 1199856.1456 | 2642990.5308 | 1199863.5719
66 | 2643085.9239 | 1200035.5323 | 2643048.1006 | 1200028.4338 | 2643011.9242 | 1200023.1039 | 2642957.7363 | 1200018.7009 | 2642878.5683 | 1200012.4405 | 2642874.8135 | 1200011.1618
67 | 2642612.2183 | 1200155.0454 | 2642644.1591 | 1200171.2096 | 2642650.2204 | 1200172.0248
68 | 2642443.8188 | 1200450.3972 | 2642435.1523 | 1200463.7766 | 2642431.5289 | 1200467.7075
69 | 2642678.0978 | 1200179.0857 | 2642666.6011 | 1200174.4826 | 2642659.8827 | 1200171.8221 | 2642652.0156 | 1200172.2662 | 2642650.2204 | 1200172.0248
70 | 2642682.8004 | 1200180.9685 | 2642678.0978 | 1200179.0857
71 | 2643085.9239 | 1200035.5323 | 2643019.6602 | 1200131.8985 | 2643015.8457 | 1200151.004 | 2643017.3327 | 1200170.7591 | 2643022.8416 | 1200199.7039 | 2643027.8397 | 1200215.004
72 | 2643190.009 | 1200057.5397 | 2643152.1658 | 1200047.9723 | 2643085.9239 | 1200035.5323
73 | 2643037.6045 | 1200219.5546 | 2643027.8397 | 1200215.004
74 | 2643190.009 | 1200057.5397 | 2643182.1234 | 1200052.0908 | 2643177.1143 | 1200047.8412 | 2643172.1051 | 1200042.5465 | 2643169.2047 | 1200038.3121 | 2643162.3743 | 1200025.878
75 | 2643190.009 | 1200057.5397 | 2643200.3219 | 1200061.0717
76 | 2643017.7932 | 1199850.0566 | 2643036.6422 | 1199845.593 | 2643049.8128 | 1199841.3966 | 2643057.959 | 1199837.1528 | 2643063.3288 | 1199832.5778 | 2643066.3873 | 1199827.5748 | 2643068.3749 | 1199821.1632 | 2643069.5793 | 1199813.5565 | 2643069.8561 | 1199804.7202 | 2643069.3104 | 1199795.9225 | 2643067.5217 | 1199787.4159 | 2643064.4984 | 1199779.0672 | 2643059.152 | 1199768.7563 | 2643049.9074 | 1199757.4167 | 2643018.3927 | 1199718.7238 | 2643009.1042 | 1199703.9376 | 2643000.5641 | 1199685.8278
77 | 2643205.3032 | 1200009.1118 | 2643207.7546 | 1200027.0174 | 2643207.8063 | 1200035.6671 | 2643207.6599 | 1200040.113 | 2643206.9224 | 1200044.1988 | 2643205.01 | 1200049.677 | 2643200.3219 | 1200061.0717
78 | 2643299.9841 | 1200108.1633 | 2643249.7775 | 1200080.7735 | 2643220.8488 | 1200068.1018 | 2643200.3219 | 1200061.0717
79 | 2642164.1631 | 1201215.3941 | 2642156.3213 | 1201204.8884 | 2642153.0277 | 1201193.4166
80 | 2642164.1631 | 1201215.3941 | 2642191.8453 | 1201212.2319 | 2642209.9226 | 1201211.1367 | 2642219.4064 | 1201212.2153 | 2642226.948 | 1201214.5588 | 2642235.3907 | 1201218.6429 | 2642244.3279 | 1201224.9095 | 2642248.9558 | 1201230.2675 | 2642253.5682 | 1201238.8938 | 2642263.3685 | 1201259.797 | 2642273.1239 | 1201280.5777 | 2642283.2993 | 1201300.0828 | 2642289.9646 | 1201310.0911 | 2642297.393 | 1201317.6479 | 2642307.6745 | 1201326.4367 | 2642375.4787 | 1201379.7245 | 2642435.1178 | 1201425.0952
81 | 2642435.1178 | 1201425.0952 | 2642442.6778 | 1201416.2216 | 2642445.7799 | 1201410.2403 | 2642449.4246 | 1201400.7497 | 2642451.2028 | 1201394.7144 | 2642451.7536 | 1201388.9707 | 2642451.5642 | 1201386.3785
82 | 2642451.5642 | 1201386.3785 | 2642451.2888 | 1201382.6082 | 2642445.8017 | 1201355.7112
83 | 2642365.5408 | 1200606.1076 | 2642369.1759 | 1200603.3762 | 2642375.1302 | 1200601.006 | 2642380.7844 | 1200600.1789 | 2642387.6002 | 1200600.8498 | 2642405.3782 | 1200603.5773
84 | 2642365.5408 | 1200606.1076 | 2642363.4352 | 1200608.9054 | 2642361.9929 | 1200613.709 | 2642361.4683 | 1200618.986 | 2642361.7771 | 1200625.9032 | 2642369.9242 | 1200662.1257 | 2642391.8328 | 1200766.1283 | 2642395.0925 | 1200776.6129 | 2642400.7821 | 1200785.7917 | 2642405.6 | 1200792.2962 | 2642420.5351 | 1200807.2438 | 2642425.8275 | 1200813.3848 | 2642429.4117 | 1200818.9022 | 2642436.5869 | 1200836.4519 | 2642438.6339 | 1200839.8164
85 | 2642405.3782 | 1200603.5773 | 2642411.5557 | 1200595.4944 | 2642409.8479 | 1200576.5605 | 2642403.2249 | 1200531.5327 | 2642402.1351 | 1200512.392 | 2642419.3107 | 1200480.9628 | 2642429.916 | 1200469.4573
86 | 2642405.3782 | 1200603.5773 | 2642494.0521 | 1200622.9509 | 2642519.2948 | 1200632.4912 | 2642634.5869 | 1200727.7543 | 2642683.5769 | 1200763.4428
87 | 2642462.16 | 1200864.666 | 2642443.352 | 1200846.3721 | 2642439.6643 | 1200841.5099 | 2642438.6339 | 1200839.8164
88 | 2643071.3198 | 1200567.5101 | 2643037.6804 | 1200549.4964 | 2643027.3278 | 1200549.7342
89 | 2643027.3278 | 1200549.7342 | 2642943.341 | 1200551.664 | 2642936.1682 | 1200555.7676
90 | 2642936.1682 | 1200555.7676 | 2642933.4959 | 1200557.2965 | 2642930.9542 | 1200569.8964 | 2642927.7319 | 1200580.2399
91 | 2642927.7319 | 1200580.2399 | 2642921.4458 | 1200600.4184
92 | 2642921.4458 | 1200600.4184 | 2642917.1627 | 1200614.1668
93 | 2642917.1627 | 1200614.1668 | 2642917.1627 | 1200614.1668 | 2642886.8016 | 1200663.7502
94 | 2642886.8016 | 1200663.7502 | 2642867.332 | 1200695.5466
95 | 2642867.332 | 1200695.5466 | 2642852.0723 | 1200720.4675
96 | 2642852.0723 | 1200720.4675 | 2642841.9646 | 1200736.9746 | 2642835.2629 | 1200759.7172 | 2642850.2286 | 1200837.168 | 2642846.8758 | 1200849.3509 | 2642838.6502 | 1200857.441 | 2642821.9021 | 1200857.7212 | 2642703.1604 | 1200776.8635
97 | 2642683.5769 | 1200763.4428 | 2642685.3692 | 1200764.7485 | 2642703.1604 | 1200776.8635
98 | 2642429.916 | 1200469.4573 | 2642431.5289 | 1200467.7075
99 | 2642462.7497 | 1200865.2396 | 2642462.16 | 1200864.666
100 | 2642462.7497 | 1200865.2396 | 2642475.2915 | 1200877.4386 | 2642523.2407 | 1200925.3062 | 2642589.6035 | 1200980.4205 | 2642598.3844 | 1200988.3209 | 2642603.6979 | 1200994.6623 | 2642607.3274 | 1201001.2474 | 2642610.3316 | 1201009.0621 | 2642611.81 | 1201016.2989 | 2642611.6117 | 1201022.7567 | 2642610.2924 | 1201029.5178
101 | 2642445.7762 | 1201355.5859 | 2642443.6982 | 1201345.4001 | 2642443.1576 | 1201337.9253 | 2642443.555 | 1201329.1232 | 2642445.7181 | 1201319.2663 | 2642461.8317 | 1201272.0541 | 2642472.599 | 1201243.5256 | 2642477.6798 | 1201231.1769 | 2642482.3289 | 1201223.8836 | 2642488.6054 | 1201216.802 | 2642495.1269 | 1201211.6566 | 2642501.4223 | 1201208.3439 | 2642510.3276 | 1201205.1498 | 2642517.8922 | 1201203.1691 | 2642534.4423 | 1201200.6409 | 2642541.4528 | 1201198.4562 | 2642546.8113 | 1201195.237 | 2642549.6049 | 1201191.9995 | 2642551.7871 | 1201188.0461 | 2642562.9962 | 1201152.0723 | 2642585.0071 | 1201091.3836 | 2642607.1618 | 1201039.4344 | 2642610.2924 | 1201029.5178 | 2642610.2924 | 1201029.5178
102 | 2642445.8017 | 1201355.7112 | 2642445.7762 | 1201355.5859
103 | 2642993.4269 | 1199671.3991 | 2642994.6011 | 1199673.1828 | 2643000.5641 | 1199685.8278
104 | 2642983.1238 | 1199655.7475 | 2642993.4269 | 1199671.3991
105 | 2642983.1238 | 1199655.7475 | 2642981.2257 | 1199652.8642 | 2642977.6664 | 1199645.3309
106 | 2643299.9841 | 1200108.1633 | 2643289.886 | 1200120.2081 | 2643215.9395 | 1200153.2586 | 2643145.8152 | 1200198.48
107 | 2643239.731 | 1199650.7753 | 2643239.2716 | 1199650.9274
108 | 2643241.9149 | 1199650.0524 | 2643239.731 | 1199650.7753
109 | 2642977.6664 | 1199645.3309 | 2642977.2886 | 1199644.5312 | 2642975.7993 | 1199638.8284 | 2642975.8077 | 1199632.3582 | 2642977.1472 | 1199627.1315 | 2642979.7144 | 1199622.6808 | 2642986.208 | 1199616.4351 | 2642987.0059 | 1199616.007

## bus_geodata
| x | y | coords
0 | 2643296.8727 | 1199652.5534
1 | 2643411.8633 | 1199872.1747
2 | 2643285.2016 | 1199311.8644
3 | 2643298.5044 | 1199352.6836
4 | 2643167.7718 | 1199343.6449
5 | 2643418.9111 | 1199849.3909
6 | 2643300.2628 | 1199370.052
7 | 2643166.4568 | 1199359.6956
8 | 2643409.5636 | 1199790.7639
9 | 2643438.8368 | 1199757.9508
10 | 2643452.2489 | 1199739.4489
11 | 2643429.6976 | 1199757.599
12 | 2643357.1754 | 1199690.2806
13 | 2643355.3164 | 1199681.6464
14 | 2643367.2723 | 1199704.3459
15 | 2643370.6496 | 1199671.564
16 | 2643381.9815 | 1199694.3324
17 | 2643370.4279 | 1199719.4859
18 | 2643387.0559 | 1199660.7759
19 | 2643379.7968 | 1199728.4057
20 | 2643416.09 | 1199702.1432
21 | 2643432.0016 | 1199722.1032
22 | 2643395.7072 | 1199717.0554
23 | 2643391.4965 | 1199667.2982
24 | 2643383.8161 | 1199740.91
25 | 2643399.5972 | 1199751.7403
26 | 2643268.1016 | 1199500.0908
27 | 2643325.2285 | 1199481.983
28 | 2643407.5055 | 1199613.2784
29 | 2643263.5166 | 1199460.5839
30 | 2643409.4725 | 1199779.9389
31 | 2643399.0041 | 1199766.333
32 | 2643472.4093 | 1199713.6224
33 | 2643417.0724 | 1199733.2092
34 | 2643418.4542 | 1199624.7332
35 | 2643431.6527 | 1199637.8769
36 | 2643441.2499 | 1199647.0252
37 | 2643442.1641 | 1199647.8288
38 | 2643287.0194 | 1199423.9842
39 | 2643308.4897 | 1199419.46
40 | 2643303.0172 | 1199396.3403
41 | 2643316.6018 | 1199418.9851
42 | 2643316.1313 | 1199399.4779
43 | 2643090.8291 | 1199557.9232
44 | 2643106.4248 | 1199528.7842
45 | 2643062.9476 | 1199588.4824
46 | 2643213.3876 | 1199659.496
47 | 2643131.9027 | 1199473.3922
48 | 2643073.1073 | 1199599.2813
49 | 2643039.7709 | 1199605.3662
50 | 2643229.972 | 1199654.0059
51 | 2643215.7746 | 1199667.357
52 | 2643165.492 | 1199371.4712
53 | 2643091.7262 | 1199640.4183
54 | 2643008.3968 | 1199609.4301
55 | 2642519.3274 | 1200128.0523
56 | 2642441.2714 | 1200440.8598
57 | 2642540.838 | 1200132.3698
58 | 2642581.0407 | 1200128.5916
59 | 2642869.698 | 1200009.4197
60 | 2642586.7202 | 1200142.4398
61 | 2642990.5308 | 1199863.5719
62 | 2642874.8135 | 1200011.1618
63 | 2642612.2183 | 1200155.0454
64 | 2642443.8188 | 1200450.3972
65 | 2642650.2204 | 1200172.0248
66 | 2642678.0978 | 1200179.0857
67 | 2642682.8004 | 1200180.9685
68 | 2643085.9239 | 1200035.5323
69 | 2643027.8397 | 1200215.004
70 | 2643190.009 | 1200057.5397
71 | 2643017.7932 | 1199850.0566
72 | 2643037.6045 | 1200219.5546
73 | 2643162.3743 | 1200025.878
74 | 2643200.3219 | 1200061.0717
75 | 2642153.0276 | 1201193.4166
76 | 2642164.1631 | 1201215.3941
77 | 2642435.1178 | 1201425.0952
78 | 2642451.5642 | 1201386.3785
79 | 2642365.5408 | 1200606.1076
80 | 2642405.3782 | 1200603.5773
81 | 2642438.6339 | 1200839.8164
82 | 2643071.3198 | 1200567.5101
83 | 2643027.3278 | 1200549.7342
84 | 2642936.1682 | 1200555.7676
85 | 2642927.7319 | 1200580.2399
86 | 2642921.4458 | 1200600.4184
87 | 2642917.1627 | 1200614.1668
88 | 2642886.8016 | 1200663.7502
89 | 2642867.332 | 1200695.5466
90 | 2642852.0723 | 1200720.4675
91 | 2642703.1604 | 1200776.8635
92 | 2642683.5769 | 1200763.4428
93 | 2642429.916 | 1200469.4573
94 | 2642431.5289 | 1200467.7075
95 | 2642462.16 | 1200864.666
96 | 2642462.7497 | 1200865.2396
97 | 2642610.2924 | 1201029.5178
98 | 2642445.7762 | 1201355.5859
99 | 2642445.8017 | 1201355.7112
100 | 2643000.5641 | 1199685.8278
101 | 2642993.4269 | 1199671.3991
102 | 2642983.1238 | 1199655.7475
103 | 2643145.8152 | 1200198.48
104 | 2643299.9841 | 1200108.1633
105 | 2643205.3032 | 1200009.1118
106 | 2643239.2716 | 1199650.9274
107 | 2643239.731 | 1199650.7753
108 | 2643241.9149 | 1199650.0524
109 | 2642977.6664 | 1199645.3309
110 | 2642987.0059 | 1199616.007
111 | 2643379.7968 | 1199728.4057

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99586 | -0.029099 | 0.00061313 | 0.00015367
1 | 0.99608 | -0.027528 | 0 | 0
2 | 0.989 | -0.078422 | 0 | 0
3 | 0.98967 | -0.073592 | 0 | 0
4 | 0.98495 | -0.10778 | 0 | 0
5 | 0.9961 | -0.02736 | 0 | 0
6 | 0.98994 | -0.07163 | 0.0007348 | 0.00018416
7 | 0.9847 | -0.1096 | 0.00097597 | 0.0002446
8 | 0.99616 | -0.026934 | 0.010581 | 0.002652
9 | 0.99227 | -0.054207 | 0 | 0
10 | 0.99269 | -0.051224 | 0 | 0
11 | 0.99206 | -0.055633 | 0.012892 | 0.003231
12 | 0.99893 | -0.0075563 | 0.010768 | 0.0026987
13 | 0.99871 | -0.0091096 | 0 | 0
14 | 0.99945 | -0.0038547 | 0 | 0
15 | 0.99825 | -0.012339 | 0.0024634 | 0.00061738
16 | 0.99916 | -0.0058753 | 0.011361 | 0.0028474
17 | 1 | 0 | -0.1621 | -0.040438
18 | 0.99778 | -0.015636 | 0 | 0
19 | 0.99838 | -0.011338 | 0 | 0
20 | 0.99542 | -0.032043 | 0 | 0
21 | 0.99395 | -0.042375 | 0 | 0
22 | 0.99687 | -0.021841 | 0.012326 | 0.0030891
23 | 0.99777 | -0.015741 | 0.0013258 | 0.00033228
24 | 0.99774 | -0.015792 | 0.0107 | 0.0026818
25 | 0.9971 | -0.020308 | 0 | 0
26 | 0.99279 | -0.051152 | 0 | 0
27 | 0.99189 | -0.057529 | 0 | 0
28 | 0.98959 | -0.073777 | 0.0018591 | 0.00046593
29 | 0.99207 | -0.056342 | 0.0038455 | 0.00096376
30 | 0.99633 | -0.025698 | 0 | 0
31 | 0.99661 | -0.02376 | 0.011908 | 0.0029844
32 | 0.99175 | -0.057857 | 0.019969 | 0.0050048
33 | 0.99375 | -0.043746 | 0.007291 | 0.0018273
34 | 0.9894 | -0.075127 | 0.0029649 | 0.00074309
35 | 0.98925 | -0.07615 | 0.00083824 | 0.00021008
36 | 0.98916 | -0.076764 | 0.0022856 | 0.00057283
37 | 0.98916 | -0.076792 | 0.0022578 | 0.00056585
38 | 0.99111 | -0.063259 | 0.00030286 | 7.5903e-05
39 | 0.99075 | -0.065821 | 0 | 0
40 | 0.99036 | -0.068594 | 0.0003414 | 8.5562e-05
41 | 0.99075 | -0.065842 | 0 | 0
42 | 0.99074 | -0.065893 | 0.00025621 | 6.4213e-05
43 | 0.98235 | -0.1269 | 0.00013896 | 3.4826e-05
44 | 0.98259 | -0.12513 | 0 | 0
45 | 0.98206 | -0.12909 | 0 | 0
46 | 0.98209 | -0.12873 | 0 | 0
47 | 0.98308 | -0.12148 | 0.011121 | 0.0027871
48 | 0.98201 | -0.12942 | 0.00022187 | 5.5606e-05
49 | 0.98188 | -0.13044 | 0.00016542 | 4.1459e-05
50 | 0.98205 | -0.12901 | 0.00021761 | 5.4538e-05
51 | 0.98208 | -0.12876 | 0.00032674 | 8.189e-05
52 | 0.98453 | -0.1109 | 0.003482 | 0.00087267
53 | 0.9819 | -0.13024 | 0.0017541 | 0.00043963
54 | 0.98169 | -0.13188 | 0.00013785 | 3.4549e-05
55 | 0.97728 | -0.16512 | 0 | 0
56 | 0.97602 | -0.17461 | 0.001246 | 0.00031228
57 | 0.97735 | -0.16458 | 0.00011939 | 2.9922e-05
58 | 0.97749 | -0.16356 | 0 | 0
59 | 0.97883 | -0.15352 | 0 | 0
60 | 0.97745 | -0.16386 | 0.00012006 | 3.0091e-05
61 | 0.9798 | -0.14612 | 0.0001121 | 2.8096e-05
62 | 0.97881 | -0.1536 | 0.00022217 | 5.5681e-05
63 | 0.97737 | -0.16439 | 0.00044363 | 0.00011119
64 | 0.97599 | -0.17481 | 0.00020574 | 5.1564e-05
65 | 0.97729 | -0.16497 | 0.00043 | 0.00010777
66 | 0.97725 | -0.16525 | 0.00018284 | 4.5823e-05
67 | 0.97725 | -0.16529 | 0.00071862 | 0.0001801
68 | 0.97847 | -0.15627 | 0 | 0
69 | 0.97836 | -0.15704 | 7.7357e-05 | 1.9388e-05
70 | 0.97835 | -0.15718 | 0 | 0
71 | 0.97996 | -0.14497 | 0.00048554 | 0.00012169
72 | 0.97836 | -0.15707 | 0.00027494 | 6.8907e-05
73 | 0.97834 | -0.15725 | 0.00017028 | 4.2676e-05
74 | 0.97834 | -0.15725 | 0 | 0
75 | 0.97369 | -0.19254 | 0.00020167 | 5.0543e-05
76 | 0.9737 | -0.19249 | 0 | 0
77 | 0.9738 | -0.19164 | 0 | 0
78 | 0.97382 | -0.19153 | 0.0002698 | 6.7618e-05
79 | 0.97531 | -0.17991 | 0 | 0
80 | 0.97542 | -0.17913 | 0 | 0
81 | 0.9747 | -0.18465 | 5.7369e-05 | 1.4378e-05
82 | 0.97183 | -0.2054 | 0.00072616 | 0.00018199
83 | 0.97188 | -0.20503 | 0.0001703 | 4.2682e-05
84 | 0.972 | -0.20415 | 0.00052956 | 0.00013272
85 | 0.97205 | -0.20374 | 0.00016334 | 4.0936e-05
86 | 0.9721 | -0.20338 | 0.00014789 | 3.7064e-05
87 | 0.97214 | -0.20311 | 7.8139e-05 | 1.9583e-05
88 | 0.9723 | -0.20199 | 0.00022669 | 5.6813e-05
89 | 0.97241 | -0.20117 | 0.00060967 | 0.0001528
90 | 0.97252 | -0.20035 | 0.00017305 | 4.3369e-05
91 | 0.97379 | -0.19108 | 0.00019282 | 4.8326e-05
92 | 0.97389 | -0.19031 | 0.00015003 | 3.7602e-05
93 | 0.97593 | -0.17527 | 0.00019218 | 4.8165e-05
94 | 0.97593 | -0.17522 | 0.00025038 | 6.2752e-05
95 | 0.97462 | -0.18527 | 6.0599e-05 | 1.5187e-05
96 | 0.97462 | -0.18528 | 0.00061379 | 0.00015383
97 | 0.9743 | -0.18775 | 0.00011763 | 2.948e-05
98 | 0.97384 | -0.19136 | 0.00017183 | 4.3066e-05
99 | 0.97384 | -0.19136 | 0.00017679 | 4.4308e-05
100 | 0.98109 | -0.13638 | 0.00064152 | 0.00016078
101 | 0.98118 | -0.13571 | 0.00015589 | 3.907e-05
102 | 0.98128 | -0.13492 | 0.00052112 | 0.0001306
103 | 0.97825 | -0.15794 | 0.0002139 | 5.3608e-05
104 | 0.9783 | -0.15752 | 0 | 0
105 | 0.97831 | -0.15747 | 0.00039023 | 9.78e-05
106 | 0.98203 | -0.12914 | 0.00083652 | 0.00020965
107 | 0.98203 | -0.12914 | 9.8788e-05 | 2.4759e-05
108 | 0.98203 | -0.12915 | 0.00036994 | 9.2717e-05
109 | 0.98135 | -0.1344 | 0.00019309 | 4.8394e-05
110 | 0.98155 | -0.1329 | 0.00011955 | 2.9961e-05
111 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00061313 | -0.00015367 | 0.00061326 | 0.00015047 | 1.3059e-07 | -3.1986e-06 | 0.00091615 | 0.00091501 | 0.00091615 | 0.99586 | -0.029099 | 0.99608 | -0.027528 | 0.33931
1 | -0.00061326 | -0.00015047 | 0.00061328 | 0.00015013 | 1.3683e-08 | -3.357e-07 | 0.00091501 | 0.00091489 | 0.00091501 | 0.99608 | -0.027528 | 0.9961 | -0.02736 | 0.33889
2 | -0.032441 | -0.0080432 | 0.032463 | 0.0080497 | 2.1246e-05 | 6.5176e-06 | 0.048779 | 0.048779 | 0.048779 | 0.989 | -0.078422 | 0.98967 | -0.073592 | 6.0221
3 | 0.032441 | 0.0080432 | -0.032313 | -0.0080036 | 0.00012872 | 3.9536e-05 | 0.048779 | 0.048783 | 0.048783 | 0.989 | -0.078422 | 0.98495 | -0.10778 | 6.0226
4 | -0.032463 | -0.0080497 | 0.032471 | 0.0080524 | 8.6397e-06 | 2.6498e-06 | 0.048779 | 0.048778 | 0.048779 | 0.98967 | -0.073592 | 0.98994 | -0.07163 | 6.022
5 | 0.032313 | 0.0080036 | -0.032305 | -0.0080012 | 7.9716e-06 | 2.4512e-06 | 0.048783 | 0.048783 | 0.048783 | 0.98495 | -0.10778 | 0.9847 | -0.1096 | 6.0226
6 | -0.00061328 | -0.00015013 | 0.00061331 | 0.00014929 | 3.4366e-08 | -8.436e-07 | 0.00091489 | 0.0009146 | 0.00091489 | 0.9961 | -0.02736 | 0.99616 | -0.026934 | 0.33885
7 | -0.033206 | -0.0082365 | 0.03322 | 0.0082408 | 1.3681e-05 | 4.2419e-06 | 0.049883 | 0.049883 | 0.049883 | 0.98994 | -0.07163 | 0.99036 | -0.068594 | 6.1584
8 | 0.031329 | 0.0077566 | -0.031323 | -0.0077549 | 5.5001e-06 | 1.6646e-06 | 0.047308 | 0.047308 | 0.047308 | 0.9847 | -0.1096 | 0.98453 | -0.1109 | 5.8405
9 | -0.011195 | -0.0028012 | 0.011197 | 0.0028018 | 1.9102e-06 | 5.9213e-07 | 0.016721 | 0.016721 | 0.016721 | 0.99616 | -0.026934 | 0.99633 | -0.025698 | 6.1928
10 | -0.012894 | -0.0032318 | 0.0129 | 0.0032335 | 5.3272e-06 | 1.7538e-06 | 0.019336 | 0.019336 | 0.019336 | 0.99227 | -0.054207 | 0.99269 | -0.051224 | 7.1616
11 | 0.012894 | 0.0032318 | -0.012892 | -0.003231 | 2.5445e-06 | 8.3781e-07 | 0.019336 | 0.019336 | 0.019336 | 0.99227 | -0.054207 | 0.99206 | -0.055633 | 7.1616
12 | -0.032887 | -0.0082449 | 0.032927 | 0.0082601 | 4.0366e-05 | 1.5181e-05 | 0.049298 | 0.049298 | 0.049298 | 0.99269 | -0.051224 | 0.99395 | -0.042375 | 18.2585
13 | 0.019988 | 0.0050114 | -0.019969 | -0.0050048 | 1.8353e-05 | 6.6357e-06 | 0.029962 | 0.029962 | 0.029962 | 0.99269 | -0.051224 | 0.99175 | -0.057857 | 11.097
14 | 0.052371 | 0.013076 | -0.05236 | -0.013072 | 1.1176e-05 | 3.9516e-06 | 0.077995 | 0.077995 | 0.077995 | 0.99893 | -0.0075563 | 0.99871 | -0.0091096 | 9.6291
15 | -0.063139 | -0.015774 | 0.063171 | 0.015786 | 3.217e-05 | 1.1686e-05 | 0.094035 | 0.094035 | 0.094035 | 0.99893 | -0.0075563 | 0.99945 | -0.0038547 | 11.6093
16 | 0.05236 | 0.013072 | -0.052337 | -0.013064 | 2.322e-05 | 8.2107e-06 | 0.077995 | 0.077996 | 0.077996 | 0.99871 | -0.0091096 | 0.99825 | -0.012339 | 9.6291
17 | 0.011365 | 0.0028484 | -0.011361 | -0.0028474 | 3.1788e-06 | 9.895e-07 | 0.01692 | 0.01692 | 0.01692 | 0.99945 | -0.0038547 | 0.99916 | -0.0058753 | 6.2667
18 | -0.074536 | -0.018635 | 0.074575 | 0.018649 | 3.9602e-05 | 1.4623e-05 | 0.11096 | 0.11095 | 0.11096 | 0.99945 | -0.0038547 | 1 | 0 | 13.6982
19 | 0.049873 | 0.012446 | -0.049851 | -0.012438 | 2.2561e-05 | 7.9076e-06 | 0.074324 | 0.074324 | 0.074324 | 0.99825 | -0.012339 | 0.99778 | -0.015636 | 9.1758
20 | 0.086728 | 0.021788 | -0.086592 | -0.021736 | 0.00013656 | 5.2351e-05 | 0.12907 | 0.12907 | 0.12907 | 1 | 0 | 0.99838 | -0.011338 | 47.8043
21 | 0.048525 | 0.012106 | -0.048289 | -0.012024 | 0.00023542 | 8.2117e-05 | 0.072347 | 0.07235 | 0.07235 | 0.99778 | -0.015636 | 0.99279 | -0.051152 | 8.9321
22 | 0.0013258 | 0.00033219 | -0.0013258 | -0.00033228 | 1.9249e-08 | -9.5654e-08 | 0.0019772 | 0.0019773 | 0.0019773 | 0.99778 | -0.015636 | 0.99777 | -0.015741 | 0.73231
23 | 0.052737 | 0.01325 | -0.05266 | -0.01322 | 7.6939e-05 | 2.9331e-05 | 0.078613 | 0.078613 | 0.078613 | 0.99838 | -0.011338 | 0.99687 | -0.021841 | 29.116
24 | 0.033854 | 0.0084862 | -0.033834 | -0.0084783 | 2.0867e-05 | 7.8541e-06 | 0.050458 | 0.050459 | 0.050459 | 0.99838 | -0.011338 | 0.99774 | -0.015792 | 18.6883
25 | 0.040278 | 0.01011 | -0.04022 | -0.010088 | 5.7695e-05 | 2.1859e-05 | 0.060215 | 0.060215 | 0.060215 | 0.99542 | -0.032043 | 0.99395 | -0.042375 | 22.3019
26 | -0.040278 | -0.01011 | 0.040335 | 0.010131 | 5.7141e-05 | 2.1648e-05 | 0.060215 | 0.060215 | 0.060215 | 0.99542 | -0.032043 | 0.99687 | -0.021841 | 22.3018
27 | 0.0072924 | 0.0018276 | -0.007291 | -0.0018273 | 1.3839e-06 | 2.9114e-07 | 0.010917 | 0.010917 | 0.010917 | 0.99395 | -0.042375 | 0.99375 | -0.043746 | 4.0435
28 | 0.023133 | 0.0057965 | -0.023119 | -0.0057912 | 1.4451e-05 | 5.304e-06 | 0.0345 | 0.0345 | 0.0345 | 0.99774 | -0.015792 | 0.9971 | -0.020308 | 12.7778
29 | 0.023119 | 0.0057912 | -0.023108 | -0.0057872 | 1.1032e-05 | 4.0495e-06 | 0.0345 | 0.0345 | 0.0345 | 0.9971 | -0.020308 | 0.99661 | -0.02376 | 12.7778
30 | 0.038049 | 0.0094563 | -0.038022 | -0.0094475 | 2.6879e-05 | 8.7962e-06 | 0.057001 | 0.057001 | 0.057001 | 0.99279 | -0.051152 | 0.99207 | -0.056342 | 7.0372
31 | 0.01024 | 0.0025677 | -0.010231 | -0.002565 | 9.0434e-06 | 2.6835e-06 | 0.015349 | 0.015349 | 0.015349 | 0.99279 | -0.051152 | 0.99189 | -0.057529 | 5.6849
32 | 0.010231 | 0.002565 | -0.010208 | -0.0025582 | 2.2993e-05 | 6.8296e-06 | 0.015349 | 0.01535 | 0.01535 | 0.99189 | -0.057529 | 0.98959 | -0.073777 | 5.6852
33 | 0.0083493 | 0.0020923 | -0.0083477 | -0.0020919 | 1.5598e-06 | 3.9621e-07 | 0.012554 | 0.012555 | 0.012555 | 0.98959 | -0.073777 | 0.9894 | -0.075127 | 4.6498
34 | 0.034177 | 0.0084838 | -0.034145 | -0.0084737 | 3.2094e-05 | 1.0069e-05 | 0.051233 | 0.051234 | 0.051234 | 0.99207 | -0.056342 | 0.99111 | -0.063259 | 6.3252
35 | -0.011197 | -0.0028018 | 0.0112 | 0.0028028 | 2.9949e-06 | 9.2825e-07 | 0.016721 | 0.01672 | 0.016721 | 0.99633 | -0.025698 | 0.99661 | -0.02376 | 6.1928
36 | 0.0053828 | 0.0013488 | -0.005382 | -0.0013487 | 7.6174e-07 | 5.3794e-08 | 0.0080954 | 0.0080955 | 0.0080955 | 0.9894 | -0.075127 | 0.98925 | -0.07615 | 2.9983
37 | 0.0045438 | 0.0011386 | -0.0045434 | -0.0011387 | 3.8665e-07 | -2.1577e-08 | 0.0068346 | 0.0068347 | 0.0068347 | 0.98925 | -0.07615 | 0.98916 | -0.076764 | 2.5314
38 | 0.0022578 | 0.00056584 | -0.0022578 | -0.00056585 | 8.7614e-09 | -1.2254e-08 | 0.0033964 | 0.0033964 | 0.0033964 | 0.98916 | -0.076764 | 0.98916 | -0.076792 | 1.2579
39 | 0.033842 | 0.0083978 | -0.03383 | -0.0083941 | 1.1768e-05 | 3.6783e-06 | 0.05078 | 0.05078 | 0.05078 | 0.99111 | -0.063259 | 0.99075 | -0.065821 | 6.2691
40 | 0.033574 | 0.0083303 | -0.033561 | -0.0083263 | 1.2631e-05 | 3.9347e-06 | 0.050395 | 0.050395 | 0.050395 | 0.99075 | -0.065821 | 0.99036 | -0.068594 | 6.2217
41 | 0.00025621 | 6.3858e-05 | -0.00025621 | -6.3962e-05 | 7.4822e-10 | -1.0405e-07 | 0.00038468 | 0.00038472 | 0.00038472 | 0.99075 | -0.065821 | 0.99075 | -0.065842 | 0.14249
42 | 0.00025621 | 6.3962e-05 | -0.00025621 | -6.4213e-05 | 1.8026e-09 | -2.5058e-07 | 0.00038472 | 0.00038481 | 0.00038481 | 0.99075 | -0.065842 | 0.99074 | -0.065893 | 0.14252
43 | -0.014819 | -0.0036221 | 0.014822 | 0.0036221 | 3.4572e-06 | 7.2826e-08 | 0.022414 | 0.022414 | 0.022414 | 0.98235 | -0.1269 | 0.98259 | -0.12513 | 2.7672
44 | 0.01468 | 0.0035872 | -0.014676 | -0.0035872 | 4.2486e-06 | 6.0992e-08 | 0.022204 | 0.022204 | 0.022204 | 0.98235 | -0.1269 | 0.98206 | -0.12909 | 2.7413
45 | 0.0018506 | 0.00046109 | -0.0018497 | -0.0004631 | 9.1609e-07 | -2.015e-06 | 0.0028016 | 0.0028024 | 0.0028024 | 0.98259 | -0.12513 | 0.98209 | -0.12873 | 1.0379
46 | -0.016673 | -0.0040832 | 0.016681 | 0.004084 | 8.0631e-06 | 7.832e-07 | 0.025215 | 0.025215 | 0.025215 | 0.98259 | -0.12513 | 0.98308 | -0.12148 | 3.113
47 | 0.0019763 | 0.00049457 | -0.0019762 | -0.00049474 | 8.889e-08 | -1.6684e-07 | 0.0029942 | 0.0029943 | 0.0029943 | 0.98206 | -0.12909 | 0.98201 | -0.12942 | 1.109
48 | 0.012699 | 0.0030926 | -0.012697 | -0.0030929 | 2.2396e-06 | -2.459e-07 | 0.01921 | 0.019211 | 0.019211 | 0.98206 | -0.12909 | 0.98188 | -0.13044 | 2.3717
49 | 0.0015229 | 0.00038132 | -0.0015229 | -0.00038151 | 5.8038e-08 | -1.9872e-07 | 0.0023074 | 0.0023074 | 0.0023074 | 0.98209 | -0.12873 | 0.98205 | -0.12901 | 0.85461
50 | 0.00032674 | 8.1786e-05 | -0.00032674 | -8.189e-05 | 1.2564e-09 | -1.0347e-07 | 0.00049503 | 0.00049507 | 0.00049507 | 0.98209 | -0.12873 | 0.98208 | -0.12876 | 0.18336
51 | -0.027802 | -0.0068711 | 0.027841 | 0.0068823 | 3.9637e-05 | 1.1139e-05 | 0.042047 | 0.042046 | 0.042047 | 0.98308 | -0.12148 | 0.98453 | -0.1109 | 5.191
52 | 0.0017543 | 0.00043913 | -0.0017541 | -0.00043963 | 1.9924e-07 | -4.9501e-07 | 0.0026581 | 0.0026583 | 0.0026583 | 0.98201 | -0.12942 | 0.9819 | -0.13024 | 0.98455
53 | 0.012532 | 0.0030514 | -0.012529 | -0.0030517 | 2.3686e-06 | -2.9074e-07 | 0.01896 | 0.01896 | 0.01896 | 0.98188 | -0.13044 | 0.98169 | -0.13188 | 2.3408
54 | 0.0013053 | 0.00032698 | -0.0013052 | -0.00032709 | 2.3909e-08 | -1.1474e-07 | 0.0019777 | 0.0019778 | 0.0019778 | 0.98205 | -0.12901 | 0.98203 | -0.12914 | 0.7325
55 | 0.012391 | 0.0030171 | -0.01239 | -0.0030174 | 1.6489e-06 | -2.2082e-07 | 0.018751 | 0.018752 | 0.018752 | 0.98169 | -0.13188 | 0.98155 | -0.1329 | 2.315
56 | 0.0067548 | 0.0016468 | -0.0067463 | -0.001658 | 8.4774e-06 | -1.1243e-05 | 0.010269 | 0.010274 | 0.010274 | 0.97728 | -0.16512 | 0.97602 | -0.17461 | 1.2683
57 | -0.0067548 | -0.0016468 | 0.0067552 | 0.0016462 | 4.8134e-07 | -6.3994e-07 | 0.010269 | 0.010268 | 0.010269 | 0.97728 | -0.16512 | 0.97735 | -0.16458 | 1.2677
58 | 0.0055003 | 0.0013458 | -0.0055001 | -0.0013461 | 1.4436e-07 | -3.1555e-07 | 0.008374 | 0.0083741 | 0.0083741 | 0.97602 | -0.17461 | 0.97599 | -0.17481 | 1.0338
59 | -0.0068746 | -0.0016761 | 0.0068756 | 0.0016749 | 9.228e-07 | -1.1727e-06 | 0.01045 | 0.010449 | 0.01045 | 0.97735 | -0.16458 | 0.97749 | -0.16356 | 1.2901
60 | -0.0087711 | -0.0021485 | 0.0087827 | 0.0021411 | 1.1612e-05 | -7.3613e-06 | 0.013334 | 0.01333 | 0.013334 | 0.97749 | -0.16356 | 0.97883 | -0.15352 | 1.6462
61 | 0.0018955 | 0.0004736 | -0.0018954 | -0.00047376 | 7.8724e-08 | -1.5972e-07 | 0.002885 | 0.002885 | 0.002885 | 0.97749 | -0.16356 | 0.97745 | -0.16386 | 1.0685
62 | -0.010132 | -0.0024677 | 0.010142 | 0.0024639 | 9.8104e-06 | -3.7568e-06 | 0.015378 | 0.015375 | 0.015378 | 0.97883 | -0.15352 | 0.9798 | -0.14612 | 1.8985
63 | 0.0013494 | 0.00032654 | -0.0013494 | -0.00032661 | 1.4134e-08 | -6.2489e-08 | 0.0020473 | 0.0020473 | 0.0020473 | 0.97883 | -0.15352 | 0.97881 | -0.1536 | 0.75828
64 | 0.0017754 | 0.00044367 | -0.0017752 | -0.00044398 | 1.2963e-07 | -3.0668e-07 | 0.0027023 | 0.0027024 | 0.0027024 | 0.97745 | -0.16386 | 0.97737 | -0.16439 | 1.0009
65 | -0.010254 | -0.002492 | 0.010256 | 0.0024915 | 1.5444e-06 | -5.6716e-07 | 0.015545 | 0.015545 | 0.015545 | 0.9798 | -0.14612 | 0.97996 | -0.14497 | 1.9192
66 | 0.0011273 | 0.00027093 | -0.0011269 | -0.00027345 | 3.8831e-07 | -2.5244e-06 | 0.0017096 | 0.0017105 | 0.0017105 | 0.97881 | -0.1536 | 0.97847 | -0.15627 | 0.63353
67 | 0.0013316 | 0.00033279 | -0.0013315 | -0.00033328 | 1.0747e-07 | -4.839e-07 | 0.002027 | 0.0020272 | 0.0020272 | 0.97737 | -0.16439 | 0.97729 | -0.16497 | 0.7508
68 | 0.0052944 | 0.0012945 | -0.0052941 | -0.0012952 | 2.8768e-07 | -6.8738e-07 | 0.0080604 | 0.0080607 | 0.0080607 | 0.97599 | -0.17481 | 0.97593 | -0.17522 | 0.99515
69 | 0.00090149 | 0.00022551 | -0.00090145 | -0.00022586 | 3.4443e-08 | -3.5389e-07 | 0.0013724 | 0.0013726 | 0.0013726 | 0.97729 | -0.16497 | 0.97725 | -0.16525 | 0.50836
70 | 0.00071862 | 0.00018004 | -0.00071862 | -0.0001801 | 3.7844e-09 | -6.2011e-08 | 0.0010942 | 0.0010942 | 0.0010942 | 0.97725 | -0.16525 | 0.97725 | -0.16529 | 0.40526
71 | 0.00035233 | 8.5639e-05 | -0.0003523 | -8.8159e-05 | 3.6086e-08 | -2.5206e-06 | 0.00053488 | 0.00053577 | 0.00053577 | 0.97847 | -0.15627 | 0.97836 | -0.15704 | 0.19843
72 | 0.00077454 | 0.00018781 | -0.00077444 | -0.00018911 | 9.1577e-08 | -1.2977e-06 | 0.0011757 | 0.0011761 | 0.0011761 | 0.97847 | -0.15627 | 0.97835 | -0.15718 | 0.4356
73 | 0.00027494 | 6.8772e-05 | -0.00027494 | -6.8907e-05 | 1.1754e-09 | -1.3483e-07 | 0.00041812 | 0.00041817 | 0.00041817 | 0.97836 | -0.15704 | 0.97836 | -0.15707 | 0.15488
74 | 0.00017028 | 4.214e-05 | -0.00017028 | -4.2676e-05 | 1.7863e-09 | -5.3564e-07 | 0.0002588 | 0.00025899 | 0.00025899 | 0.97835 | -0.15718 | 0.97834 | -0.15725 | 0.095921
75 | 0.00060416 | 0.00014697 | -0.00060416 | -0.0001471 | 5.7096e-09 | -1.3434e-07 | 0.00091733 | 0.00091738 | 0.00091738 | 0.97835 | -0.15718 | 0.97834 | -0.15725 | 0.33977
76 | -0.010741 | -0.0026132 | 0.010753 | 0.0026095 | 1.205e-05 | -3.6359e-06 | 0.016282 | 0.016279 | 0.016282 | 0.97996 | -0.14497 | 0.98109 | -0.13638 | 2.0101
77 | 0.00039024 | 9.7134e-05 | -0.00039023 | -9.78e-05 | 1.1745e-08 | -6.6662e-07 | 0.0005933 | 0.00059354 | 0.00059354 | 0.97834 | -0.15725 | 0.97831 | -0.15747 | 0.21983
78 | 0.00021392 | 4.997e-05 | -0.00021391 | -5.1351e-05 | 7.2342e-09 | -1.3811e-06 | 0.0003241 | 0.00032457 | 0.00032457 | 0.97834 | -0.15725 | 0.9783 | -0.15752 | 0.12021
79 | -0.00020167 | -5.0543e-05 | 0.00020167 | 5.0232e-05 | 1.4839e-09 | -3.1094e-07 | 0.00030819 | 0.00030808 | 0.00030819 | 0.97369 | -0.19254 | 0.9737 | -0.19249 | 0.11415
80 | -0.00020167 | -5.0232e-05 | 0.00020169 | 4.5695e-05 | 2.1526e-08 | -4.5364e-06 | 0.00030808 | 0.00030652 | 0.00030808 | 0.9737 | -0.19249 | 0.9738 | -0.19164 | 0.1141
81 | -0.00020169 | -4.5695e-05 | 0.00020169 | 4.5159e-05 | 2.5326e-09 | -5.3676e-07 | 0.00030652 | 0.00030635 | 0.00030652 | 0.9738 | -0.19164 | 0.97382 | -0.19153 | 0.11353
82 | -0.00047149 | -0.00011278 | 0.0004715 | 0.00011239 | 1.006e-08 | -3.847e-07 | 0.00071855 | 0.00071842 | 0.00071855 | 0.97382 | -0.19153 | 0.97384 | -0.19136 | 0.26613
83 | -0.0016713 | -0.00040206 | 0.0016715 | 0.00040161 | 1.6716e-07 | -4.5234e-07 | 0.002544 | 0.0025438 | 0.002544 | 0.97531 | -0.17991 | 0.97542 | -0.17913 | 0.94222
84 | 0.0016713 | 0.00040206 | -0.0016703 | -0.00040482 | 1.0211e-06 | -2.7594e-06 | 0.002544 | 0.0025451 | 0.0025451 | 0.97531 | -0.17991 | 0.9747 | -0.18465 | 0.94262
85 | -0.004849 | -0.001187 | 0.0048515 | 0.0011844 | 2.474e-06 | -2.6785e-06 | 0.0073872 | 0.0073859 | 0.0073872 | 0.97542 | -0.17913 | 0.97593 | -0.17527 | 1.368
86 | 0.0031775 | 0.00078543 | -0.0031727 | -0.00078767 | 4.8017e-06 | -2.24e-06 | 0.0048434 | 0.0048449 | 0.0048449 | 0.97542 | -0.17913 | 0.97389 | -0.19031 | 1.7944
87 | 0.0016129 | 0.00039044 | -0.0016128 | -0.00039082 | 1.2935e-07 | -3.78e-07 | 0.0024575 | 0.0024577 | 0.0024577 | 0.9747 | -0.18465 | 0.97462 | -0.18527 | 0.91024
88 | -0.00072616 | -0.00018199 | 0.0007262 | 0.00018141 | 3.7418e-08 | -5.8676e-07 | 0.0011119 | 0.0011116 | 0.0011119 | 0.97183 | -0.2054 | 0.97188 | -0.20503 | 0.4118
89 | -0.0008965 | -0.00022409 | 0.00089661 | 0.00022299 | 1.0841e-07 | -1.1019e-06 | 0.0013724 | 0.001372 | 0.0013724 | 0.97188 | -0.20503 | 0.972 | -0.20415 | 0.50829
90 | -0.0014262 | -0.00035571 | 0.0014262 | 0.0003554 | 7.9566e-08 | -3.0118e-07 | 0.0021827 | 0.0021826 | 0.0021827 | 0.972 | -0.20415 | 0.97205 | -0.20374 | 0.8084
91 | -0.0015896 | -0.00039634 | 0.0015897 | 0.00039611 | 7.8038e-08 | -2.3199e-07 | 0.0024326 | 0.0024325 | 0.0024326 | 0.97205 | -0.20374 | 0.9721 | -0.20338 | 0.90096
92 | -0.0017375 | -0.00043317 | 0.0017376 | 0.00043302 | 6.3524e-08 | -1.541e-07 | 0.0026589 | 0.0026588 | 0.0026589 | 0.9721 | -0.20338 | 0.97214 | -0.20311 | 0.98477
93 | -0.0018158 | -0.0004526 | 0.001816 | 0.00045199 | 2.8004e-07 | -6.1326e-07 | 0.0027784 | 0.0027781 | 0.0027784 | 0.97214 | -0.20311 | 0.9723 | -0.20199 | 1.029
94 | -0.0020427 | -0.0005088 | 0.0020429 | 0.00050843 | 2.272e-07 | -3.7508e-07 | 0.0031251 | 0.0031249 | 0.0031251 | 0.9723 | -0.20199 | 0.97241 | -0.20117 | 1.1574
95 | -0.0026526 | -0.00066122 | 0.0026529 | 0.00066098 | 3.0024e-07 | -2.4707e-07 | 0.0040578 | 0.0040577 | 0.0040578 | 0.97241 | -0.20117 | 0.97252 | -0.20035 | 1.5029
96 | -0.002826 | -0.00070435 | 0.0028295 | 0.00070191 | 3.5726e-06 | -2.4344e-06 | 0.0043225 | 0.0043211 | 0.0043225 | 0.97252 | -0.20035 | 0.97379 | -0.19108 | 1.6009
97 | -0.0030224 | -0.00075024 | 0.0030227 | 0.00075006 | 3.1563e-07 | -1.74e-07 | 0.0046158 | 0.0046157 | 0.0046158 | 0.97379 | -0.19108 | 0.97389 | -0.19031 | 1.7095
98 | -0.0050437 | -0.0012325 | 0.0050437 | 0.0012324 | 2.9187e-08 | -7.7981e-08 | 0.007679 | 0.0076789 | 0.007679 | 0.97593 | -0.17527 | 0.97593 | -0.17522 | 0.94802
99 | 0.0015522 | 0.00037563 | -0.0015522 | -0.00037564 | 2.8712e-09 | -9.1468e-09 | 0.0023651 | 0.0023651 | 0.0023651 | 0.97462 | -0.18527 | 0.97462 | -0.18528 | 0.87598
100 | 0.00093843 | 0.00022181 | -0.00093814 | -0.00022454 | 2.9063e-07 | -2.7314e-06 | 0.0014281 | 0.0014291 | 0.0014291 | 0.97462 | -0.18528 | 0.9743 | -0.18775 | 0.52928
101 | 0.00082051 | 0.00019506 | -0.00082013 | -0.00019976 | 3.7999e-07 | -4.7032e-06 | 0.0012494 | 0.0012511 | 0.0012511 | 0.9743 | -0.18775 | 0.97384 | -0.19136 | 0.46337
102 | 0.00064829 | 0.0001567 | -0.00064829 | -0.0001567 | 7.7991e-11 | -1.5616e-09 | 0.00098854 | 0.00098854 | 0.00098854 | 0.97384 | -0.19136 | 0.97384 | -0.19136 | 0.36613
103 | -0.011395 | -0.0027703 | 0.011396 | 0.0027701 | 9.977e-07 | -2.2685e-07 | 0.017252 | 0.017252 | 0.017252 | 0.98109 | -0.13638 | 0.98118 | -0.13571 | 2.1299
104 | -0.011552 | -0.0028091 | 0.011553 | 0.0028089 | 1.192e-06 | -2.5161e-07 | 0.017488 | 0.017488 | 0.017488 | 0.98118 | -0.13571 | 0.98128 | -0.13492 | 2.1591
105 | -0.012074 | -0.0029395 | 0.012075 | 0.0029394 | 8.1887e-07 | -1.3167e-07 | 0.018278 | 0.018278 | 0.018278 | 0.98128 | -0.13492 | 0.98135 | -0.1344 | 2.2566
106 | -0.0002139 | -5.3608e-05 | 0.00021391 | 5.1351e-05 | 1.1871e-08 | -2.2574e-06 | 0.00032536 | 0.00032457 | 0.00032536 | 0.97825 | -0.15794 | 0.9783 | -0.15752 | 0.1205
107 | 0.00046873 | 0.00011744 | -0.00046873 | -0.00011745 | 1.5237e-10 | -6.0644e-09 | 0.00071023 | 0.00071023 | 0.00071023 | 0.98203 | -0.12914 | 0.98203 | -0.12914 | 0.26305
108 | 0.00036994 | 9.2688e-05 | -0.00036994 | -9.2717e-05 | 4.5108e-10 | -2.8931e-08 | 0.00056055 | 0.00056056 | 0.00056056 | 0.98203 | -0.12914 | 0.98203 | -0.12915 | 0.20761
109 | -0.012268 | -0.0029878 | 0.01227 | 0.0029874 | 2.4172e-06 | -3.4782e-07 | 0.018571 | 0.01857 | 0.018571 | 0.98135 | -0.1344 | 0.98155 | -0.1329 | 2.2927

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17236 | 0.043009

## res_load
| p_mw | q_mvar
0 | 0.00061313 | 0.00015367
1 | 0.0007348 | 0.00018416
2 | 0.00097597 | 0.0002446
3 | 0.010581 | 0.002652
4 | 0.012892 | 0.003231
5 | 0.010768 | 0.0026987
6 | 0.0024634 | 0.00061738
7 | 0.011361 | 0.0028474
8 | 0.010259 | 0.0025711
9 | 0.012326 | 0.0030891
10 | 0.0013258 | 0.00033228
11 | 0.0107 | 0.0026818
12 | 0.0018591 | 0.00046593
13 | 0.0038455 | 0.00096376
14 | 0.011908 | 0.0029844
15 | 0.019969 | 0.0050048
16 | 0.007291 | 0.0018273
17 | 0.0029649 | 0.00074309
18 | 0.00083824 | 0.00021008
19 | 0.0022856 | 0.00057283
20 | 0.0022578 | 0.00056585
21 | 0.00030286 | 7.5903e-05
22 | 0.0003414 | 8.5562e-05
23 | 0.00025621 | 6.4213e-05
24 | 0.00013896 | 3.4826e-05
25 | 0.011121 | 0.0027871
26 | 0.00022187 | 5.5606e-05
27 | 0.00016542 | 4.1459e-05
28 | 0.00021761 | 5.4538e-05
29 | 0.00032674 | 8.189e-05
30 | 0.003482 | 0.00087267
31 | 0.0017541 | 0.00043963
32 | 0.00013785 | 3.4549e-05
33 | 0.001246 | 0.00031228
34 | 0.00011939 | 2.9922e-05
35 | 0.00012006 | 3.0091e-05
36 | 0.0001121 | 2.8096e-05
37 | 0.00022217 | 5.5681e-05
38 | 0.00044363 | 0.00011119
39 | 0.00020574 | 5.1564e-05
40 | 0.00043 | 0.00010777
41 | 0.00018284 | 4.5823e-05
42 | 0.00071862 | 0.0001801
43 | 7.7357e-05 | 1.9388e-05
44 | 0.00048554 | 0.00012169
45 | 0.00027494 | 6.8907e-05
46 | 0.00017028 | 4.2676e-05
47 | 0.00020167 | 5.0543e-05
48 | 0.0002698 | 6.7618e-05
49 | 5.7369e-05 | 1.4378e-05
50 | 0.00072616 | 0.00018199
51 | 0.0001703 | 4.2682e-05
52 | 0.00052956 | 0.00013272
53 | 0.00016334 | 4.0936e-05
54 | 0.00014789 | 3.7064e-05
55 | 7.8139e-05 | 1.9583e-05
56 | 0.00022669 | 5.6813e-05
57 | 0.00060967 | 0.0001528
58 | 0.00017305 | 4.3369e-05
59 | 0.00019282 | 4.8326e-05
60 | 0.00015003 | 3.7602e-05
61 | 0.00019218 | 4.8165e-05
62 | 0.00025038 | 6.2752e-05
63 | 6.0599e-05 | 1.5187e-05
64 | 0.00061379 | 0.00015383
65 | 0.00011763 | 2.948e-05
66 | 0.00017183 | 4.3066e-05
67 | 0.00017679 | 4.4308e-05
68 | 0.00064152 | 0.00016078
69 | 0.00015589 | 3.907e-05
70 | 0.00052112 | 0.0001306
71 | 0.0002139 | 5.3608e-05
72 | 0.00039023 | 9.78e-05
73 | 0.00083652 | 0.00020965
74 | 9.8788e-05 | 2.4759e-05
75 | 0.00036994 | 9.2717e-05
76 | 0.00019309 | 4.8394e-05
77 | 0.00011955 | 2.9961e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1