## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1008-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1008-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1008-8_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1008-8_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1008-8_0_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1008-8_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1008-8_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1008-8_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1008-8_0_3_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1008-8_0_3_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1008-8_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1008-8_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1008-8_0_3_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1008-8_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1008-8_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1008-8_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1008-8_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1008-8_0_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1008-8_0_3_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1008-8_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_1008-8_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1008-8_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1008-8_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1008-8_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1008-8_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1008-8_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1008-8_0_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1008-8_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_MV_125_0_node_93 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-8_0_3_load_0 | 0 | 0.025035 | 0.0062743 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-8_0_3_load_1 | 1 | 0.0034235 | 0.00085801 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-8_0_3_load_2 | 2 | 0.0020767 | 0.00052048 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-8_0_3_load_17 | 9 | 0.013009 | 0.0032604 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-8_0_3_load_26 | 10 | 0.038923 | 0.0097549 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-8_0_3_load_25 | 11 | 0.010654 | 0.0026701 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-8_0_3_load_27 | 13 | 0.0010219 | 0.0002561 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-8_0_3_load_21 | 14 | 0.00069711 | 0.00017471 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-8_0_3_load_18 | 16 | 0.024259 | 0.00608 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-8_0_3_load_24 | 17 | 0.013026 | 0.0032646 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-8_0_3_load_23 | 18 | 0.013942 | 0.0034943 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-8_0_3_load_28 | 19 | 0.0087985 | 0.0022051 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-8_0_3_load_29 | 20 | 0.012104 | 0.0030336 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-8_0_3_load_19 | 22 | 0.0035736 | 0.00089563 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-8_0_3_load_22 | 23 | 0.034833 | 0.0087299 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-8_0_3_load_13 | 24 | 0.010621 | 0.0026618 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-8_0_3_load_16 | 25 | 0.0072808 | 0.0018247 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-8_0_3_load_31 | 26 | 0.0092075 | 0.0023076 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-8_0_3_load_30 | 27 | 0.0069992 | 0.0017542 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-8_0_3_load_20 | 28 | 0.0012589 | 0.00031551 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-8_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1008-8_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0085242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-8_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1008-8_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.12635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-8_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.069116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1008-8_0_3_line_6 | NAYY 4x150 SE | 5 | 17 | 0.03837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-8_0_3_line_7 | NAYY 4x150 SE | 5 | 18 | 0.013665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-8_0_3_line_8 | NAYY 4x150 SE | 6 | 10 | 0.005423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-8_0_3_line_9 | NAYY 4x150 SE | 6 | 11 | 0.033626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-8_0_3_line_10 | NAYY 4x150 SE | 7 | 8 | 0.028194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-8_0_3_line_11 | NAYY 4x150 SE | 7 | 9 | 0.033699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-8_0_3_line_12 | NAYY 4x150 SE | 8 | 11 | 0.016769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-8_0_3_line_13 | NAYY 4x150 SE | 8 | 21 | 0.006102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-8_0_3_line_14 | NAYY 4x150 SE | 9 | 15 | 0.0032931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-8_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.013551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-8_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.060649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-8_0_3_line_17 | NAYY 4x150 SE | 14 | 22 | 0.056683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-8_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.012907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-8_0_3_line_19 | NAYY 4x150 SE | 17 | 23 | 0.0058972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1008-8_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.019383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-8_0_3_line_21 | NAYY 4x150 SE | 20 | 27 | 0.0063093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-8_0_3_line_22 | NAYY 4x150 SE | 21 | 25 | 0.015947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-8_0_3_line_23 | NAYY 4x150 SE | 21 | 24 | 0.011759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-8_0_3_line_24 | NAYY 4x150 SE | 22 | 28 | 0.0080032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1008-8_0_3_line_25 | NAYY 4x150 SE | 23 | 28 | 0.043082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1008-8_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0011299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-8_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.014617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-8_0_3_trafo_0 | 0.25 MVA 20/0.4 kV | 29 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2644218.3492 | 1200366.4064 | 2644216.4068 | 1200367.4023 | 2644213.1555 | 1200363.376 | 2644204.641 | 1200353.5853
1 | 2644218.3492 | 1200366.4064 | 2644229.1324 | 1200360.8777
2 | 2644196.151 | 1200352.8221 | 2644204.641 | 1200353.5853
3 | 2644249.6851 | 1200353.5072 | 2644243.9163 | 1200353.2977 | 2644229.1324 | 1200360.8777
4 | 2644147.309 | 1200279.609 | 2644143.0834 | 1200282.7796 | 2644139.0039 | 1200286.7851 | 2644132.9218 | 1200292.9104 | 2644125.735 | 1200303.2965 | 2644127.4321 | 1200307.4781 | 2644127.4172 | 1200312.592 | 2644131.2282 | 1200317.1115 | 2644137.9339 | 1200322.4084 | 2644155.2625 | 1200332.3975 | 2644169.6358 | 1200330.2469 | 2644176.0836 | 1200332.3068 | 2644196.151 | 1200352.8221
5 | 2644249.6851 | 1200353.5072 | 2644258.1379 | 1200368.5449 | 2644265.6741 | 1200381.9416 | 2644268.1159 | 1200386.2954 | 2644268.8819 | 1200391.8264 | 2644255.8129 | 1200414.209
6 | 2644147.309 | 1200279.609 | 2644154.9116 | 1200274.7847 | 2644178.6043 | 1200261.1075 | 2644180.5148 | 1200260.4868
7 | 2644147.309 | 1200279.609 | 2644142.1812 | 1200266.943
8 | 2644255.8129 | 1200414.209 | 2644260.9565 | 1200412.4905
9 | 2644255.8129 | 1200414.209 | 2644243.5528 | 1200435.3302 | 2644240.965 | 1200444.1638
10 | 2644236.2507 | 1200460.2569 | 2644247.1873 | 1200464.6959 | 2644255.4704 | 1200466.6472 | 2644263.4058 | 1200467.2396
11 | 2644263.4058 | 1200467.2396 | 2644274.7319 | 1200468.4241 | 2644297.0189 | 1200469.4611
12 | 2644236.2507 | 1200460.2569 | 2644240.965 | 1200444.1638
13 | 2644236.2507 | 1200460.2569 | 2644230.7669 | 1200457.5482
14 | 2644300.3084 | 1200469.6141 | 2644297.0189 | 1200469.4611
15 | 2644342.7773 | 1200198.7871 | 2644353.0612 | 1200189.9634
16 | 2644342.7773 | 1200198.7871 | 2644327.7922 | 1200208.4593 | 2644300.4174 | 1200220.6967 | 2644288.4574 | 1200225.3362
17 | 2644288.4574 | 1200225.3362 | 2644260.7935 | 1200236.0676 | 2644235.3187 | 1200245.0466
18 | 2644300.3084 | 1200469.6141 | 2644313.2142 | 1200469.7966
19 | 2644186.1235 | 1200258.6648 | 2644180.5148 | 1200260.4868
20 | 2644183.404 | 1200425.1761 | 2644186.8399 | 1200427.0952 | 2644199.5348 | 1200435.8961
21 | 2644204.72 | 1200439.4908 | 2644199.5348 | 1200435.8961
22 | 2644230.7669 | 1200457.5482 | 2644217.6611 | 1200448.4624
23 | 2644230.7669 | 1200457.5482 | 2644224.2131 | 1200467.312
24 | 2644235.3187 | 1200245.0466 | 2644234.1327 | 1200245.4646 | 2644227.688 | 1200247.457
25 | 2644186.1235 | 1200258.6648 | 2644192.424 | 1200256.6181 | 2644214.5004 | 1200251.534 | 2644227.688 | 1200247.457
26 | 2644216.7326 | 1200447.8187 | 2644217.6611 | 1200448.4624
27 | 2644204.72 | 1200439.4908 | 2644216.7326 | 1200447.8187

## bus_geodata
| x | y | coords
0 | 2644218.3492 | 1200366.4064
1 | 2644204.641 | 1200353.5853
2 | 2644229.1324 | 1200360.8777
3 | 2644196.151 | 1200352.8221
4 | 2644249.6851 | 1200353.5072
5 | 2644147.309 | 1200279.609
6 | 2644255.8129 | 1200414.209
7 | 2644263.4058 | 1200467.2396
8 | 2644236.2507 | 1200460.2569
9 | 2644297.0189 | 1200469.4611
10 | 2644260.9565 | 1200412.4905
11 | 2644240.965 | 1200444.1638
12 | 2644342.7773 | 1200198.7871
13 | 2644353.0612 | 1200189.9634
14 | 2644288.4574 | 1200225.3362
15 | 2644300.3084 | 1200469.6141
16 | 2644313.2142 | 1200469.7966
17 | 2644180.5148 | 1200260.4868
18 | 2644142.1812 | 1200266.943
19 | 2644183.404 | 1200425.1761
20 | 2644199.5348 | 1200435.8961
21 | 2644230.7669 | 1200457.5482
22 | 2644235.3187 | 1200245.0466
23 | 2644186.1235 | 1200258.6648
24 | 2644224.2131 | 1200467.312
25 | 2644217.6611 | 1200448.4624
26 | 2644216.7326 | 1200447.8187
27 | 2644204.72 | 1200439.4908
28 | 2644227.688 | 1200247.457
29 | 2644196.151 | 1200352.8221

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.22021 | -0.055475
1 | 0.99788 | -0.014604 | 0.0034235 | 0.00085801
2 | 0.99873 | -0.008717 | 0.0020767 | 0.00052048
3 | 0.99704 | -0.020452 | 0 | 0
4 | 0.99643 | -0.024645 | 0 | 0
5 | 0.9845 | -0.1083 | 0 | 0
6 | 0.98932 | -0.074285 | 0 | 0
7 | 0.9805 | -0.13664 | 0 | 0
8 | 0.98203 | -0.12575 | 0 | 0
9 | 0.97867 | -0.1497 | 0.013009 | 0.0032604
10 | 0.98901 | -0.076438 | 0.038923 | 0.0097549
11 | 0.98428 | -0.10977 | 0.010654 | 0.0026701
12 | 0.98041 | -0.13744 | 0 | 0
13 | 0.98039 | -0.13758 | 0.0010219 | 0.0002561
14 | 0.9805 | -0.13679 | 0.00069711 | 0.00017471
15 | 0.97855 | -0.15054 | 0 | 0
16 | 0.9781 | -0.1538 | 0.024259 | 0.00608
17 | 0.98146 | -0.12987 | 0.013026 | 0.0032646
18 | 0.98422 | -0.11026 | 0.013942 | 0.0034943
19 | 0.97942 | -0.14438 | 0.0087985 | 0.0022051
20 | 0.97967 | -0.14261 | 0.012104 | 0.0030336
21 | 0.98154 | -0.12922 | 0 | 0
22 | 0.98064 | -0.13578 | 0.0035736 | 0.00089563
23 | 0.98111 | -0.1324 | 0.034833 | 0.0087299
24 | 0.98136 | -0.13052 | 0.010621 | 0.0026618
25 | 0.98051 | -0.13656 | 0.0072808 | 0.0018247
26 | 0.98045 | -0.137 | 0.0092075 | 0.0023076
27 | 0.97986 | -0.14124 | 0.0069992 | 0.0017542
28 | 0.9807 | -0.13533 | 0.0012589 | 0.00031551
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.073014 | 0.01846 | -0.072864 | -0.018402 | 0.00014992 | 5.7397e-05 | 0.1087 | 0.1087 | 0.1087 | 1 | 0 | 0.99788 | -0.014604 | 40.2603
1 | 0.1464 | 0.037015 | -0.14622 | -0.036946 | 0.0001796 | 6.8761e-05 | 0.21795 | 0.21795 | 0.21795 | 1 | 0 | 0.99873 | -0.008717 | 40.3619
2 | 0.069441 | 0.017544 | -0.069384 | -0.017523 | 5.7087e-05 | 2.1845e-05 | 0.1036 | 0.1036 | 0.1036 | 0.99788 | -0.014604 | 0.99704 | -0.020452 | 38.3696
3 | 0.14414 | 0.036426 | -0.14382 | -0.036302 | 0.00032244 | 0.00012343 | 0.21486 | 0.21486 | 0.21486 | 0.99873 | -0.008717 | 0.99643 | -0.024645 | 39.789
4 | 0.069384 | 0.017523 | -0.068537 | -0.017199 | 0.00084617 | 0.00032382 | 0.1036 | 0.1036 | 0.1036 | 0.99704 | -0.020452 | 0.9845 | -0.1083 | 38.3698
5 | 0.14382 | 0.036302 | -0.14282 | -0.035921 | 0.00099551 | 0.0003811 | 0.21486 | 0.21486 | 0.21486 | 0.99643 | -0.024645 | 0.98932 | -0.074285 | 39.7891
6 | 0.054591 | 0.013703 | -0.054428 | -0.013641 | 0.00016304 | 6.222e-05 | 0.082519 | 0.082519 | 0.082519 | 0.9845 | -0.1083 | 0.98146 | -0.12987 | 30.5628
7 | 0.013946 | 0.0034956 | -0.013942 | -0.0034943 | 3.7887e-06 | 1.2835e-06 | 0.021079 | 0.021079 | 0.021079 | 0.9845 | -0.1083 | 0.98422 | -0.11026 | 7.8071
8 | 0.038934 | 0.0097593 | -0.038923 | -0.0097549 | 1.1605e-05 | 4.3938e-06 | 0.058561 | 0.058561 | 0.058561 | 0.98932 | -0.074285 | 0.98901 | -0.076438 | 21.6892
9 | 0.10389 | 0.026162 | -0.10338 | -0.025965 | 0.00051261 | 0.00019673 | 0.1563 | 0.1563 | 0.1563 | 0.98932 | -0.074285 | 0.98428 | -0.10977 | 57.8891
10 | -0.03735 | -0.009371 | 0.037406 | 0.0093924 | 5.6532e-05 | 2.1387e-05 | 0.056686 | 0.056686 | 0.056686 | 0.9805 | -0.13664 | 0.98203 | -0.12575 | 20.9949
11 | 0.03735 | 0.009371 | -0.037282 | -0.0093455 | 6.7571e-05 | 2.5565e-05 | 0.056686 | 0.056686 | 0.056686 | 0.9805 | -0.13664 | 0.97867 | -0.1497 | 20.995
12 | -0.092515 | -0.023216 | 0.092721 | 0.023295 | 0.00020567 | 7.889e-05 | 0.14019 | 0.14019 | 0.14019 | 0.98203 | -0.12575 | 0.98428 | -0.10977 | 51.9238
13 | 0.055109 | 0.013824 | -0.055082 | -0.013814 | 2.6553e-05 | 1.0136e-05 | 0.083508 | 0.083508 | 0.083508 | 0.98203 | -0.12575 | 0.98154 | -0.12922 | 30.9289
14 | 0.024273 | 0.0060851 | -0.02427 | -0.0060841 | 2.799e-06 | 1.0352e-06 | 0.036907 | 0.036907 | 0.036907 | 0.97867 | -0.1497 | 0.97855 | -0.15054 | 13.6692
15 | 0.0010219 | 0.00025594 | -0.0010219 | -0.0002561 | 2.0339e-08 | -1.6305e-07 | 0.0015509 | 0.001551 | 0.001551 | 0.98041 | -0.13744 | 0.98039 | -0.13758 | 0.57443
16 | -0.0010219 | -0.00025594 | 0.001022 | 0.00025521 | 9.1013e-08 | -7.2987e-07 | 0.0015509 | 0.0015506 | 0.0015509 | 0.98041 | -0.13744 | 0.9805 | -0.13679 | 0.57441
17 | -0.0017191 | -0.00042992 | 0.0017193 | 0.0004293 | 2.4066e-07 | -6.2246e-07 | 0.0026086 | 0.0026083 | 0.0026086 | 0.9805 | -0.13679 | 0.98064 | -0.13578 | 0.96614
18 | 0.02427 | 0.0060841 | -0.024259 | -0.00608 | 1.097e-05 | 4.0573e-06 | 0.036907 | 0.036907 | 0.036907 | 0.97855 | -0.15054 | 0.9781 | -0.1538 | 13.6692
19 | 0.041402 | 0.010376 | -0.041388 | -0.010371 | 1.4499e-05 | 5.5021e-06 | 0.06277 | 0.06277 | 0.06277 | 0.98146 | -0.12987 | 0.98111 | -0.1324 | 23.2483
20 | -0.0087985 | -0.0022051 | 0.0088007 | 0.0022057 | 2.1612e-06 | 5.8724e-07 | 0.013367 | 0.013367 | 0.013367 | 0.97942 | -0.14438 | 0.97967 | -0.14261 | 4.9509
21 | -0.020905 | -0.0052393 | 0.020909 | 0.0052407 | 3.9693e-06 | 1.4472e-06 | 0.031752 | 0.031752 | 0.031752 | 0.97967 | -0.14261 | 0.97986 | -0.14124 | 11.7601
22 | 0.04446 | 0.011151 | -0.044415 | -0.011134 | 4.5211e-05 | 1.7188e-05 | 0.067404 | 0.067404 | 0.067404 | 0.98154 | -0.12922 | 0.98051 | -0.13656 | 24.9646
23 | 0.010622 | 0.0026623 | -0.010621 | -0.0026618 | 1.9029e-06 | 5.8329e-07 | 0.016104 | 0.016104 | 0.016104 | 0.98154 | -0.12922 | 0.98136 | -0.13052 | 5.9643
24 | -0.0052929 | -0.0013249 | 0.0052933 | 0.001325 | 3.2209e-07 | 2.2905e-08 | 0.0080309 | 0.0080309 | 0.0080309 | 0.98064 | -0.13578 | 0.9807 | -0.13533 | 2.9744
25 | 0.0065548 | 0.0016409 | -0.0065522 | -0.0016405 | 2.6566e-06 | 4.7796e-07 | 0.0099408 | 0.009941 | 0.009941 | 0.98111 | -0.1324 | 0.9807 | -0.13533 | 3.6819
26 | 0.037134 | 0.0093095 | -0.037132 | -0.0093086 | 2.2391e-06 | 8.4696e-07 | 0.056355 | 0.056355 | 0.056355 | 0.98051 | -0.13656 | 0.98045 | -0.137 | 20.8723
27 | 0.027924 | 0.007001 | -0.027908 | -0.0069949 | 1.6383e-05 | 6.1168e-06 | 0.042381 | 0.042381 | 0.042381 | 0.98045 | -0.137 | 0.97986 | -0.14124 | 15.6968

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24525 | 0.061749

## res_load
| p_mw | q_mvar
0 | 0.025035 | 0.0062743
1 | 0.0034235 | 0.00085801
2 | 0.0020767 | 0.00052048
3 | 0.013009 | 0.0032604
4 | 0.038923 | 0.0097549
5 | 0.010654 | 0.0026701
6 | 0.0010219 | 0.0002561
7 | 0.00069711 | 0.00017471
8 | 0.024259 | 0.00608
9 | 0.013026 | 0.0032646
10 | 0.013942 | 0.0034943
11 | 0.0087985 | 0.0022051
12 | 0.012104 | 0.0030336
13 | 0.0035736 | 0.00089563
14 | 0.034833 | 0.0087299
15 | 0.010621 | 0.0026618
16 | 0.0072808 | 0.0018247
17 | 0.0092075 | 0.0023076
18 | 0.0069992 | 0.0017542
19 | 0.0012589 | 0.00031551

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1