## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1008-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1008-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1008-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1008-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1008-9_0_4_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_1008-9_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1008-9_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1008-9_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1008-9_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1008-9_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1008-9_0_4_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_1008-9_0_4_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_1008-9_0_4_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_1008-9_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1008-9_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1008-9_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1008-9_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1008-9_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1008-9_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1008-9_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1008-9_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_1008-9_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_1008-9_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_1008-9_0_4_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_1008-9_0_4_node_71 | 0.4 | n |  | TRUE
25 | bus_LV_1008-9_0_4_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_1008-9_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1008-9_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1008-9_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1008-9_0_4_node_81 | 0.4 | n |  | TRUE
30 | bus_LV_1008-9_0_4_node_82 | 0.4 | n |  | TRUE
31 | bus_LV_1008-9_0_4_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_1008-9_0_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_1008-9_0_4_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1008-9_0_4_node_78 | 0.4 | n |  | TRUE
35 | bus_LV_1008-9_0_4_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_1008-9_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1008-9_0_4_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_1008-9_0_4_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_1008-9_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1008-9_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1008-9_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1008-9_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1008-9_0_4_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_1008-9_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1008-9_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_1008-9_0_4_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_1008-9_0_4_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_1008-9_0_4_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_1008-9_0_4_node_59 | 0.4 | n |  | TRUE
50 | bus_LV_1008-9_0_4_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_1008-9_0_4_node_62 | 0.4 | n |  | TRUE
52 | bus_LV_1008-9_0_4_node_63 | 0.4 | n |  | TRUE
53 | bus_LV_1008-9_0_4_node_64 | 0.4 | n |  | TRUE
54 | bus_LV_1008-9_0_4_node_83 | 0.4 | n |  | TRUE
55 | bus_LV_1008-9_0_4_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_1008-9_0_4_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_1008-9_0_4_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_1008-9_0_4_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_1008-9_0_4_node_28 | 0.4 | n |  | TRUE
60 | bus_LV_1008-9_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1008-9_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_1008-9_0_4_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_1008-9_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_1008-9_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1008-9_0_4_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_1008-9_0_4_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_1008-9_0_4_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_1008-9_0_4_node_32 | 0.4 | n |  | TRUE
69 | bus_LV_1008-9_0_4_node_33 | 0.4 | n |  | TRUE
70 | bus_LV_1008-9_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_1008-9_0_4_node_34 | 0.4 | n |  | TRUE
72 | bus_LV_1008-9_0_4_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_1008-9_0_4_node_36 | 0.4 | n |  | TRUE
74 | bus_LV_1008-9_0_4_node_38 | 0.4 | n |  | TRUE
75 | bus_LV_1008-9_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_1008-9_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_1008-9_0_4_node_43 | 0.4 | n |  | TRUE
78 | bus_LV_1008-9_0_4_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_1008-9_0_4_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_1008-9_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_1008-9_0_4_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_1008-9_0_4_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_1008-9_0_4_node_50 | 0.4 | n |  | TRUE
84 | bus_MV_125_0_node_95 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1008-9_0_4_load_0 | 0 | 0.00021971 | 5.5064e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1008-9_0_4_load_8 | 5 | 0.00023621 | 5.92e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1008-9_0_4_load_6 | 6 | 0.00020277 | 5.082e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1008-9_0_4_load_7 | 7 | 0.00044447 | 0.00011139 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1008-9_0_4_load_5 | 8 | 0.0003548 | 8.8921e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1008-9_0_4_load_17 | 9 | 0.00036165 | 9.0637e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1008-9_0_4_load_40 | 10 | 0.00021935 | 5.4975e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1008-9_0_4_load_42 | 11 | 0.00048087 | 0.00012052 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1008-9_0_4_load_4 | 12 | 0.00034886 | 8.7433e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1008-9_0_4_load_15 | 13 | 0.00012755 | 3.1967e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1008-9_0_4_load_23 | 17 | 0.00035649 | 8.9344e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1008-9_0_4_load_19 | 18 | 5.9907e-05 | 1.5014e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1008-9_0_4_load_21 | 19 | 0.00017017 | 4.2649e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1008-9_0_4_load_9 | 20 | 0.00082677 | 0.00020721 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1008-9_0_4_load_10 | 21 | 0.0037979 | 0.00095185 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1008-9_0_4_load_11 | 22 | 0.012248 | 0.0030696 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1008-9_0_4_load_74 | 23 | 0.022092 | 0.0055368 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1008-9_0_4_load_71 | 24 | 0.030435 | 0.0076277 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1008-9_0_4_load_13 | 27 | 0.0036177 | 0.00090668 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1008-9_0_4_load_81 | 29 | 0.010148 | 0.0025433 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1008-9_0_4_load_82 | 30 | 0.017529 | 0.0043932 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1008-9_0_4_load_39 | 31 | 0.00018643 | 4.6723e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1008-9_0_4_load_44 | 32 | 0.000291 | 7.2932e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1008-9_0_4_load_78 | 34 | 0.007236 | 0.0018135 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1008-9_0_4_load_75 | 35 | 0.086038 | 0.021563 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1008-9_0_4_load_22 | 36 | 0.00048208 | 0.00012082 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1008-9_0_4_load_46 | 37 | 0.00022169 | 5.556e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1008-9_0_4_load_24 | 39 | 0.00010736 | 2.6906e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1008-9_0_4_load_25 | 40 | 0.00059441 | 0.00014897 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1008-9_0_4_load_26 | 41 | 0.00086445 | 0.00021665 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1008-9_0_4_load_31 | 43 | 0.00022586 | 5.6605e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1008-9_0_4_load_29 | 44 | 0.0005168 | 0.00012952 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1008-9_0_4_load_30 | 45 | 0.00016705 | 4.1866e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1008-9_0_4_load_80 | 46 | 0.00054527 | 0.00013666 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1008-9_0_4_load_60 | 47 | 0.00036183 | 9.0684e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1008-9_0_4_load_68 | 48 | 0.00029932 | 7.5016e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1008-9_0_4_load_59 | 49 | 0.00043091 | 0.000108 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1008-9_0_4_load_61 | 50 | 0.0019358 | 0.00048515 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1008-9_0_4_load_62 | 51 | 0.00037698 | 9.4479e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1008-9_0_4_load_63 | 52 | 0.0005754 | 0.00014421 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1008-9_0_4_load_64 | 53 | 0.0015025 | 0.00037656 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1008-9_0_4_load_83 | 54 | 0.0003072 | 7.6992e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1008-9_0_4_load_65 | 55 | 0.0017029 | 0.00042679 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1008-9_0_4_load_67 | 57 | 0.00020306 | 5.0892e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1008-9_0_4_load_69 | 58 | 0.0094081 | 0.0023579 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1008-9_0_4_load_28 | 59 | 0.00015581 | 3.9051e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1008-9_0_4_load_53 | 61 | 0.0017719 | 0.00044408 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1008-9_0_4_load_54 | 62 | 0.00059498 | 0.00014912 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1008-9_0_4_load_51 | 63 | 0.0010175 | 0.00025502 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1008-9_0_4_load_55 | 64 | 0.00013804 | 3.4595e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1008-9_0_4_load_56 | 65 | 0.00043402 | 0.00010878 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1008-9_0_4_load_57 | 66 | 0.000455 | 0.00011403 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1008-9_0_4_load_58 | 67 | 0.0010298 | 0.00025809 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1008-9_0_4_load_32 | 68 | 0.00060292 | 0.00015111 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1008-9_0_4_load_33 | 69 | 0.00010239 | 2.5662e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1008-9_0_4_load_47 | 70 | 0.00020897 | 5.2374e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1008-9_0_4_load_34 | 71 | 0.0001639 | 4.1077e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1008-9_0_4_load_36 | 73 | 0.00086051 | 0.00021566 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1008-9_0_4_load_38 | 74 | 0.0002416 | 6.0551e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1008-9_0_4_load_43 | 77 | 0.00051726 | 0.00012964 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1008-9_0_4_load_76 | 78 | 0.0065092 | 0.0016313 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1008-9_0_4_load_77 | 79 | 0.00088776 | 0.00022249 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1008-9_0_4_load_79 | 80 | 0.0011941 | 0.00029926 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1008-9_0_4_load_48 | 81 | 0.00095594 | 0.00023958 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1008-9_0_4_load_49 | 82 | 0.00016859 | 4.2253e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1008-9_0_4_load_50 | 83 | 0.000335 | 8.396e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1008-9_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1008-9_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0054096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1008-9_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1008-9_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.16542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1008-9_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.02878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1008-9_0_4_line_5 | NAYY 4x150 SE | 4 | 10 | 0.044023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1008-9_0_4_line_6 | NAYY 4x150 SE | 5 | 12 | 0.10894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1008-9_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.0033201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1008-9_0_4_line_8 | NAYY 4x150 SE | 6 | 8 | 0.03571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1008-9_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.30134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1008-9_0_4_line_10 | NAYY 4x150 SE | 8 | 12 | 0.037476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1008-9_0_4_line_11 | NAYY 4x150 SE | 9 | 13 | 0.022672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1008-9_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.096681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1008-9_0_4_line_13 | NAYY 4x150 SE | 11 | 77 | 0.021912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1008-9_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0092143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1008-9_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.024958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1008-9_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.024218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1008-9_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.083116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1008-9_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0094635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1008-9_0_4_line_19 | NAYY 4x150 SE | 18 | 19 | 0.29851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1008-9_0_4_line_20 | NAYY 4x150 SE | 19 | 36 | 0.040814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1008-9_0_4_line_21 | NAYY 4x150 SE | 20 | 21 | 0.086844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1008-9_0_4_line_22 | NAYY 4x150 SE | 21 | 22 | 0.05196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1008-9_0_4_line_23 | NAYY 4x150 SE | 22 | 26 | 0.04163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1008-9_0_4_line_24 | NAYY 4x150 SE | 23 | 24 | 0.1219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1008-9_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.030927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1008-9_0_4_line_26 | NAYY 4x150 SE | 24 | 27 | 0.027542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1008-9_0_4_line_27 | NAYY 4x150 SE | 25 | 35 | 0.045702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1008-9_0_4_line_28 | NAYY 4x150 SE | 25 | 76 | 0.044924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1008-9_0_4_line_29 | NAYY 4x150 SE | 26 | 27 | 0.038051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1008-9_0_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.07064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1008-9_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.02329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1008-9_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.019497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1008-9_0_4_line_33 | NAYY 4x150 SE | 30 | 34 | 0.14194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1008-9_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.14098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1008-9_0_4_line_35 | NAYY 4x150 SE | 31 | 33 | 0.0015659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1008-9_0_4_line_36 | NAYY 4x150 SE | 32 | 77 | 0.030631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1008-9_0_4_line_37 | NAYY 4x150 SE | 33 | 75 | 0.56486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1008-9_0_4_line_38 | NAYY 4x150 SE | 33 | 72 | 0.060393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1008-9_0_4_line_39 | NAYY 4x150 SE | 34 | 78 | 0.016616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1008-9_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.058197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1008-9_0_4_line_41 | NAYY 4x150 SE | 38 | 70 | 0.33677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1008-9_0_4_line_42 | NAYY 4x150 SE | 38 | 43 | 0.16794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1008-9_0_4_line_43 | NAYY 4x150 SE | 39 | 40 | 0.034381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1008-9_0_4_line_44 | NAYY 4x150 SE | 39 | 41 | 0.078936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1008-9_0_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.021737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1008-9_0_4_line_46 | NAYY 4x150 SE | 42 | 44 | 0.028781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1008-9_0_4_line_47 | NAYY 4x150 SE | 43 | 44 | 0.18709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1008-9_0_4_line_48 | NAYY 4x150 SE | 43 | 45 | 0.03163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1008-9_0_4_line_49 | NAYY 4x150 SE | 44 | 59 | 0.015726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1008-9_0_4_line_50 | NAYY 4x150 SE | 45 | 68 | 0.012879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1008-9_0_4_line_51 | NAYY 4x150 SE | 46 | 47 | 0.12576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1008-9_0_4_line_52 | NAYY 4x150 SE | 46 | 48 | 0.047785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1008-9_0_4_line_53 | NAYY 4x150 SE | 47 | 50 | 0.018012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1008-9_0_4_line_54 | NAYY 4x150 SE | 47 | 49 | 0.022178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1008-9_0_4_line_55 | NAYY 4x150 SE | 48 | 56 | 0.018214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1008-9_0_4_line_56 | NAYY 4x150 SE | 50 | 51 | 0.0051739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1008-9_0_4_line_57 | NAYY 4x150 SE | 51 | 52 | 0.070283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1008-9_0_4_line_58 | NAYY 4x150 SE | 52 | 53 | 0.068209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1008-9_0_4_line_59 | NAYY 4x150 SE | 52 | 54 | 0.33565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1008-9_0_4_line_60 | NAYY 4x150 SE | 55 | 56 | 0.032229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1008-9_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.012122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1008-9_0_4_line_62 | NAYY 4x150 SE | 57 | 58 | 0.13633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1008-9_0_4_line_63 | NAYY 4x150 SE | 58 | 76 | 0.013621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1008-9_0_4_line_64 | NAYY 4x150 SE | 60 | 61 | 0.048917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1008-9_0_4_line_65 | NAYY 4x150 SE | 60 | 62 | 0.0054563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1008-9_0_4_line_66 | NAYY 4x150 SE | 60 | 63 | 0.065217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1008-9_0_4_line_67 | NAYY 4x150 SE | 61 | 82 | 0.030573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1008-9_0_4_line_68 | NAYY 4x150 SE | 62 | 64 | 0.0093613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1008-9_0_4_line_69 | NAYY 4x150 SE | 63 | 83 | 0.031332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1008-9_0_4_line_70 | NAYY 4x150 SE | 64 | 65 | 0.012038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1008-9_0_4_line_71 | NAYY 4x150 SE | 65 | 66 | 0.04464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1008-9_0_4_line_72 | NAYY 4x150 SE | 66 | 67 | 0.010397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1008-9_0_4_line_73 | NAYY 4x150 SE | 68 | 69 | 0.013627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1008-9_0_4_line_74 | NAYY 4x150 SE | 69 | 71 | 0.0066359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1008-9_0_4_line_75 | NAYY 4x150 SE | 70 | 81 | 0.012863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1008-9_0_4_line_76 | NAYY 4x150 SE | 71 | 72 | 0.0053212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1008-9_0_4_line_77 | NAYY 4x150 SE | 72 | 73 | 0.014239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1008-9_0_4_line_78 | NAYY 4x150 SE | 73 | 74 | 0.029381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1008-9_0_4_line_79 | NAYY 4x150 SE | 75 | 76 | 0.053655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1008-9_0_4_line_80 | NAYY 4x150 SE | 78 | 79 | 0.011229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1008-9_0_4_line_81 | NAYY 4x150 SE | 79 | 80 | 0.050692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1008-9_0_4_line_82 | NAYY 4x150 SE | 81 | 82 | 0.01422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1008-9_0_4_trafo_74 | 0.25 MVA 20/0.4 kV | 84 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2644213.0886 | 1201731.7933 | 2644219.3133 | 1201737.0534 | 2644224.7107 | 1201744.8351
1 | 2644227.5479 | 1201749.4324 | 2644226.2037 | 1201746.9878 | 2644224.7107 | 1201744.8351
2 | 2644192.1334 | 1201724.9456 | 2644195.5573 | 1201725.071 | 2644213.0886 | 1201731.7933
3 | 2644227.5479 | 1201749.4324 | 2644370.1375 | 1201833.2918
4 | 2644192.1334 | 1201724.9456 | 2644168.3421 | 1201708.7516
5 | 2644370.1375 | 1201833.2918 | 2644392.3837 | 1201845.5527 | 2644407.5393 | 1201856.3736
6 | 2644168.3421 | 1201708.7516 | 2644096.5815 | 1201790.7108
7 | 2644154.3009 | 1201840.2092 | 2644151.4736 | 1201838.4687
8 | 2644151.4736 | 1201838.4687 | 2644134.9436 | 1201828.2929 | 2644122.6333 | 1201817.6104
9 | 2644154.3009 | 1201840.2092 | 2644003.6593 | 1202101.1911
10 | 2644096.5815 | 1201790.7108 | 2644096.5815 | 1201790.7108 | 2644117.8227 | 1201813.4359 | 2644122.6333 | 1201817.6104
11 | 2644003.6593 | 1202101.1911 | 2643989.488 | 1202100.2641 | 2643981.0174 | 1202100.3129
12 | 2644434.9008 | 1201949.1025 | 2644407.5393 | 1201856.3736
13 | 2644434.9008 | 1201949.1025 | 2644438.7868 | 1201966.2102 | 2644440.3474 | 1201970.2901
14 | 2643971.8408 | 1202101.1459 | 2643981.0174 | 1202100.3129
15 | 2643971.8408 | 1202101.1459 | 2643981.0043 | 1202105.1933 | 2643988.0872 | 1202109.6368 | 2643993.3467 | 1202113.6778
16 | 2644012.5832 | 1202128.4611 | 2643993.3467 | 1202113.6778
17 | 2643993.3467 | 1202113.6778 | 2643980.515 | 1202130.3151 | 2643970.4849 | 1202141.6589 | 2643959.3882 | 1202152.1277 | 2643955.4615 | 1202156.2344 | 2643953.2391 | 1202159.3754 | 2643951.6113 | 1202162.3652 | 2643951.0863 | 1202164.418 | 2643950.9728 | 1202166.4072 | 2643951.2839 | 1202168.5996 | 2643953.2747 | 1202172.1163 | 2643958.0543 | 1202179.0325
18 | 2644012.5832 | 1202128.4611 | 2644019.9984 | 1202134.3409
19 | 2644019.9984 | 1202134.3409 | 2644221.974 | 1202354.1519
20 | 2644240.9058 | 1202387.7405 | 2644225.1643 | 1202372.8459 | 2644225.0221 | 1202364.2956 | 2644221.974 | 1202354.1519
21 | 2644708.4458 | 1201296.2353 | 2644713.4288 | 1201303.7599 | 2644743.9738 | 1201344.3447 | 2644758.766 | 1201359.1304 | 2644763.3807 | 1201363.1343
22 | 2644763.3807 | 1201363.1343 | 2644773.5651 | 1201371.9707 | 2644800.4924 | 1201399.4539
23 | 2644829.6268 | 1201429.1898 | 2644800.4924 | 1201399.4539
24 | 2644994.1531 | 1201506.3756 | 2644876.2754 | 1201475.3026
25 | 2645019.0728 | 1201512.638 | 2645009.462 | 1201514.4 | 2645004.5393 | 1201517.209 | 2644996.8238 | 1201511.859 | 2644994.1531 | 1201506.3756
26 | 2644876.2754 | 1201475.3026 | 2644856.6878 | 1201455.94
27 | 2645019.0728 | 1201512.638 | 2645023.2895 | 1201507.578 | 2645028.8478 | 1201502.2279 | 2645030.8 | 1201499.7079 | 2645029.7235 | 1201494.0966 | 2645028.1254 | 1201489.0039 | 2645018.0237 | 1201475.0866
28 | 2645034.1995 | 1201554.6091 | 2645034.0904 | 1201550.9061 | 2645032.1143 | 1201542.4531 | 2645026.4033 | 1201528.669 | 2645019.0728 | 1201512.638
29 | 2644829.6268 | 1201429.1898 | 2644856.6878 | 1201455.94
30 | 2644880.3731 | 1201380.2204 | 2644873.7015 | 1201384.8285 | 2644852.7546 | 1201408.2402 | 2644841.2098 | 1201419.2154 | 2644829.6268 | 1201429.1898
31 | 2644880.3731 | 1201380.2204 | 2644883.8648 | 1201379.4573 | 2644886.9921 | 1201379.5809 | 2644890.5716 | 1201381.3087 | 2644892.9795 | 1201382.9722 | 2644898.0415 | 1201383.9218 | 2644902.5903 | 1201383.2667
32 | 2644880.3731 | 1201380.2204 | 2644882.4725 | 1201377.3457 | 2644886.0701 | 1201371.6139 | 2644890.8404 | 1201363.7675
33 | 2644890.8404 | 1201363.7675 | 2644989.9733 | 1201262.1882
34 | 2644596.2772 | 1201991.7403 | 2644455.3904 | 1201996.8754
35 | 2644597.5426 | 1201992.6627 | 2644596.2772 | 1201991.7403
36 | 2644440.3474 | 1201970.2901 | 2644442.527 | 1201975.988 | 2644455.3904 | 1201996.8754
37 | 2644597.5426 | 1201992.6627 | 2644997.6217 | 1201593.9115
38 | 2644597.5426 | 1201992.6627 | 2644619.4358 | 1202013.3378 | 2644639.8466 | 1202035.814
39 | 2644989.9733 | 1201262.1882 | 2644980.7242 | 1201248.3847
40 | 2644583.5932 | 1202217.0082 | 2644582.6937 | 1202223.3273 | 2644580.6957 | 1202228.9823 | 2644577.1903 | 1202234.7149 | 2644574.4131 | 1202237.707 | 2644571.6485 | 1202239.0094 | 2644567.9108 | 1202239.1594 | 2644566.0517 | 1202238.434 | 2644564.0295 | 1202236.1176 | 2644559.8099 | 1202229.4491 | 2644557.3571 | 1202224.6503 | 2644554.3754 | 1202220.3701 | 2644550.7876 | 1202217.4113
41 | 2644583.5932 | 1202217.0082 | 2644659.4483 | 1202545.1284
42 | 2644688.6894 | 1202086.0194 | 2644583.5932 | 1202217.0082
43 | 2644940.3885 | 1202228.556 | 2644970.6975 | 1202244.7863
44 | 2644940.3885 | 1202228.556 | 2644920.0199 | 1202217.6487 | 2644869.726 | 1202193.4091
45 | 2644850.1447 | 1202183.9717 | 2644869.726 | 1202193.4091
46 | 2644850.1447 | 1202183.9717 | 2644840.3074 | 1202200.852 | 2644837.5336 | 1202203.3659 | 2644832.5318 | 1202205.6519
47 | 2644688.6894 | 1202086.0194 | 2644832.5318 | 1202205.6519
48 | 2644667.4182 | 1202062.6323 | 2644670.197 | 1202065.3351 | 2644687.3313 | 1202084.2294 | 2644688.6894 | 1202086.0194
49 | 2644831.3632 | 1202219.3954 | 2644829.5803 | 1202216.6361 | 2644828.4422 | 1202213.1366 | 2644829.2018 | 1202210.2852 | 2644830.5009 | 1202207.5378 | 2644832.5318 | 1202205.6519
50 | 2644667.4182 | 1202062.6323 | 2644658.186 | 1202053.6523
51 | 2645297.2162 | 1201677.4972 | 2645241.5544 | 1201564.7244
52 | 2645241.5544 | 1201564.7244 | 2645230.5009 | 1201547.9312 | 2645226.9083 | 1201541.9229 | 2645223.8676 | 1201539.4207 | 2645220.5372 | 1201538.9953 | 2645217.6684 | 1201539.9185 | 2645209.2721 | 1201546.0055
53 | 2645297.2162 | 1201677.4972 | 2645304.4018 | 1201672.7615 | 2645307.3895 | 1201671.1944 | 2645313.0581 | 1201669.1301
54 | 2645277.4924 | 1201687.5902 | 2645294.5956 | 1201679.2242 | 2645297.2162 | 1201677.4972
55 | 2645192.6114 | 1201553.1811 | 2645200.326 | 1201550.5601 | 2645207.773 | 1201547.0922 | 2645209.2721 | 1201546.0055
56 | 2645317.9196 | 1201667.3597 | 2645313.0581 | 1201669.1301
57 | 2645317.9196 | 1201667.3597 | 2645325.3629 | 1201664.6491 | 2645329.9327 | 1201660.2034 | 2645332.7883 | 1201654.9888 | 2645337.6261 | 1201643.3077 | 2645339.9812 | 1201639.8569 | 2645344.1759 | 1201636.7092 | 2645348.3325 | 1201635.5734 | 2645352.3389 | 1201636.1819 | 2645356.1403 | 1201638.7122 | 2645361.2251 | 1201643.6424 | 2645366.7214 | 1201649.4069
58 | 2645366.7214 | 1201649.4069 | 2645397.0158 | 1201681.1798 | 2645401.7707 | 1201687.4416 | 2645408.5641 | 1201698.8664 | 2645410.6581 | 1201701.2244
59 | 2645366.7214 | 1201649.4069 | 2645560.8031 | 1201375.5631
60 | 2645192.6114 | 1201553.1811 | 2645196.9235 | 1201554.6367 | 2645207.2383 | 1201571.502 | 2645209.3103 | 1201579.1344
61 | 2645192.6114 | 1201553.1811 | 2645181.3589 | 1201556.6536 | 2645181.0307 | 1201556.7614
62 | 2645045.0918 | 1201546.4911 | 2645181.0307 | 1201556.7614
63 | 2645034.1995 | 1201554.6091 | 2645036.4537 | 1201552.4137 | 2645044.7243 | 1201546.7061 | 2645045.0918 | 1201546.4911
64 | 2644739.8874 | 1202614.9683 | 2644718.739 | 1202594.7653 | 2644703.6569 | 1202582.1388
65 | 2644739.8874 | 1202614.9683 | 2644743.8337 | 1202618.7363
66 | 2644739.8874 | 1202614.9683 | 2644735.1195 | 1202620.6136 | 2644727.8348 | 1202620.9037 | 2644715.6838 | 1202617.6332 | 2644705.6738 | 1202614.0118 | 2644683.9001 | 1202603.1318 | 2644681.127 | 1202602.0724
67 | 2644680.2143 | 1202562.5132 | 2644703.6569 | 1202582.1388
68 | 2644750.6043 | 1202625.2011 | 2644743.8337 | 1202618.7363
69 | 2644658.9446 | 1202613.7514 | 2644659.7873 | 1202607.9099 | 2644661.9509 | 1202603.5013 | 2644665.5257 | 1202600.6931 | 2644671.8404 | 1202599.8509 | 2644677.5186 | 1202600.6938 | 2644681.127 | 1202602.0724
70 | 2644750.6043 | 1202625.2011 | 2644759.3106 | 1202633.5141
71 | 2644759.3106 | 1202633.5141 | 2644765.9166 | 1202639.8217 | 2644766.4259 | 1202641.9267 | 2644765.8774 | 1202644.0349 | 2644761.3148 | 1202653.7618 | 2644761.0884 | 1202656.5617 | 2644761.6687 | 1202660.3571 | 2644763.7464 | 1202665.4089 | 2644769.0249 | 1202671.824
72 | 2644769.0249 | 1202671.824 | 2644769.3795 | 1202672.255 | 2644776.3245 | 1202679.2242
73 | 2644648.4178 | 1202044.151 | 2644658.186 | 1202053.6523
74 | 2644648.4178 | 1202044.151 | 2644643.661 | 1202039.5242
75 | 2644659.4483 | 1202545.1284 | 2644669.311 | 1202553.3852
76 | 2644639.8466 | 1202035.814 | 2644643.661 | 1202039.5242
77 | 2644639.8466 | 1202035.814 | 2644636.0783 | 1202039.021 | 2644632.7621 | 1202040.7972 | 2644627.9588 | 1202040.9504 | 2644627.2758 | 1202040.7135
78 | 2644600.2873 | 1202029.7375 | 2644607.1118 | 1202034.0798 | 2644615.7044 | 1202036.0673 | 2644624.8466 | 1202039.871 | 2644627.2758 | 1202040.7135
79 | 2644997.6217 | 1201593.9115 | 2645000.0315 | 1201591.2726 | 2645003.0568 | 1201587.7378 | 2645011.2882 | 1201578.1277 | 2645017.688 | 1201571.1941 | 2645027.0766 | 1201561.5371 | 2645034.1995 | 1201554.6091
80 | 2644980.7242 | 1201248.3847 | 2644980.0829 | 1201247.4277 | 2644973.6825 | 1201239.6446
81 | 2644946.735 | 1201197.7661 | 2644948.0062 | 1201201.1492 | 2644951.3634 | 1201210.1907 | 2644956.2073 | 1201219.9104 | 2644960.9314 | 1201227.3501 | 2644970.4513 | 1201235.7153 | 2644973.6825 | 1201239.6446
82 | 2644669.311 | 1202553.3852 | 2644680.2143 | 1202562.5132

## bus_geodata
| x | y | coords
0 | 2644224.7107 | 1201744.8351
1 | 2644213.0886 | 1201731.7933
2 | 2644227.5479 | 1201749.4324
3 | 2644192.1334 | 1201724.9456
4 | 2644370.1375 | 1201833.2918
5 | 2644168.3421 | 1201708.7516
6 | 2644151.4736 | 1201838.4687
7 | 2644154.3009 | 1201840.2092
8 | 2644122.6333 | 1201817.6104
9 | 2644003.6593 | 1202101.1911
10 | 2644407.5393 | 1201856.3736
11 | 2644434.9008 | 1201949.1025
12 | 2644096.5815 | 1201790.7108
13 | 2643981.0174 | 1202100.3129
14 | 2643971.8408 | 1202101.1459
15 | 2643993.3467 | 1202113.6778
16 | 2644012.5832 | 1202128.4611
17 | 2643958.0543 | 1202179.0325
18 | 2644019.9984 | 1202134.3409
19 | 2644221.974 | 1202354.1519
20 | 2644708.4458 | 1201296.2353
21 | 2644763.3807 | 1201363.1343
22 | 2644800.4924 | 1201399.4539
23 | 2644994.1531 | 1201506.3756
24 | 2644876.2754 | 1201475.3026
25 | 2645019.0728 | 1201512.638
26 | 2644829.6268 | 1201429.1898
27 | 2644856.6878 | 1201455.94
28 | 2644880.3731 | 1201380.2204
29 | 2644902.5903 | 1201383.2667
30 | 2644890.8404 | 1201363.7675
31 | 2644596.2772 | 1201991.7403
32 | 2644455.3904 | 1201996.8753
33 | 2644597.5426 | 1201992.6627
34 | 2644989.9733 | 1201262.1882
35 | 2645018.0237 | 1201475.0866
36 | 2644240.9058 | 1202387.7405
37 | 2644550.7876 | 1202217.4113
38 | 2644583.5932 | 1202217.0082
39 | 2644940.3885 | 1202228.556
40 | 2644970.6975 | 1202244.7863
41 | 2644869.726 | 1202193.4091
42 | 2644850.1447 | 1202183.9717
43 | 2644688.6894 | 1202086.0194
44 | 2644832.5318 | 1202205.6519
45 | 2644667.4182 | 1202062.6323
46 | 2645241.5544 | 1201564.7244
47 | 2645297.2162 | 1201677.4972
48 | 2645209.2721 | 1201546.0055
49 | 2645277.4924 | 1201687.5902
50 | 2645313.0581 | 1201669.1301
51 | 2645317.9196 | 1201667.3597
52 | 2645366.7214 | 1201649.4069
53 | 2645410.6581 | 1201701.2244
54 | 2645560.8031 | 1201375.5631
55 | 2645209.3103 | 1201579.1344
56 | 2645192.6114 | 1201553.1811
57 | 2645181.0307 | 1201556.7614
58 | 2645045.0918 | 1201546.4911
59 | 2644831.3632 | 1202219.3954
60 | 2644739.8874 | 1202614.9683
61 | 2644703.6569 | 1202582.1388
62 | 2644743.8337 | 1202618.7363
63 | 2644681.127 | 1202602.0724
64 | 2644750.6043 | 1202625.2011
65 | 2644759.3106 | 1202633.5141
66 | 2644769.0249 | 1202671.824
67 | 2644776.3245 | 1202679.2242
68 | 2644658.186 | 1202053.6523
69 | 2644648.4178 | 1202044.151
70 | 2644659.4483 | 1202545.1284
71 | 2644643.661 | 1202039.5242
72 | 2644639.8466 | 1202035.814
73 | 2644627.2758 | 1202040.7135
74 | 2644600.2873 | 1202029.7375
75 | 2644997.6217 | 1201593.9115
76 | 2645034.1995 | 1201554.6091
77 | 2644440.3474 | 1201970.2901
78 | 2644980.7242 | 1201248.3847
79 | 2644973.6825 | 1201239.6446
80 | 2644946.735 | 1201197.7661
81 | 2644669.311 | 1202553.3852
82 | 2644680.2143 | 1202562.5132
83 | 2644658.9446 | 1202613.7514
84 | 2644992.2967 | 1201502.5641

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97679 | -0.16557 | 0.00021971 | 5.5064e-05
1 | 0.97671 | -0.16617 | 0 | 0
2 | 0.97682 | -0.16538 | 0 | 0
3 | 0.97661 | -0.16692 | 0 | 0
4 | 0.97763 | -0.15937 | 0 | 0
5 | 0.97648 | -0.1679 | 0.00023621 | 5.92e-05
6 | 0.97576 | -0.17321 | 0.00020277 | 5.082e-05
7 | 0.97575 | -0.17328 | 0.00044447 | 0.00011139
8 | 0.97587 | -0.17235 | 0.0003548 | 8.8921e-05
9 | 0.97506 | -0.1784 | 0.00036165 | 9.0637e-05
10 | 0.97785 | -0.15777 | 0.00021935 | 5.4975e-05
11 | 0.97835 | -0.15403 | 0.00048087 | 0.00012052
12 | 0.97601 | -0.17132 | 0.00034886 | 8.7433e-05
13 | 0.97503 | -0.1787 | 0.00012755 | 3.1967e-05
14 | 0.97501 | -0.1788 | 0 | 0
15 | 0.97497 | -0.1791 | 0 | 0
16 | 0.97495 | -0.17928 | 0 | 0
17 | 0.97493 | -0.17941 | 0.00035649 | 8.9344e-05
18 | 0.97494 | -0.17936 | 5.9907e-05 | 1.5014e-05
19 | 0.97465 | -0.18146 | 0.00017017 | 4.2649e-05
20 | 0.9843 | -0.1099 | 0.00082677 | 0.00020721
21 | 0.9844 | -0.10916 | 0.0037979 | 0.00095185
22 | 0.98475 | -0.10668 | 0.012248 | 0.0030696
23 | 1 | 0 | -0.21859 | -0.054873
24 | 0.99167 | -0.057967 | 0.030435 | 0.0076277
25 | 0.99731 | -0.018742 | 0 | 0
26 | 0.98577 | -0.099452 | 0 | 0
27 | 0.98911 | -0.075916 | 0.0036177 | 0.00090668
28 | 0.98129 | -0.13118 | 0 | 0
29 | 0.98095 | -0.13363 | 0.010148 | 0.0025433
30 | 0.98035 | -0.13793 | 0.017529 | 0.0043932
31 | 0.97969 | -0.14421 | 0.00018643 | 4.6723e-05
32 | 0.97869 | -0.15157 | 0.000291 | 7.2932e-05
33 | 0.9797 | -0.14413 | 0 | 0
34 | 0.97707 | -0.16136 | 0.007236 | 0.0018135
35 | 0.99166 | -0.058423 | 0.086038 | 0.021563
36 | 0.97462 | -0.18167 | 0.00048208 | 0.00012082
37 | 0.97578 | -0.17235 | 0.00022169 | 5.556e-05
38 | 0.9758 | -0.17221 | 0 | 0
39 | 0.9768 | -0.16505 | 0.00010736 | 2.6906e-05
40 | 0.97677 | -0.16527 | 0.00059441 | 0.00014897
41 | 0.97688 | -0.16447 | 0.00086445 | 0.00021665
42 | 0.97693 | -0.16411 | 0 | 0
43 | 0.9776 | -0.15921 | 0.00022586 | 5.6605e-05
44 | 0.97699 | -0.16364 | 0.0005168 | 0.00012952
45 | 0.97806 | -0.15594 | 0.00016705 | 4.1866e-05
46 | 0.99238 | -0.05361 | 0.00054527 | 0.00013666
47 | 0.99139 | -0.060686 | 0.00036183 | 9.0684e-05
48 | 0.99279 | -0.050657 | 0.00029932 | 7.5016e-05
49 | 0.99137 | -0.060783 | 0.00043091 | 0.000108
50 | 0.99127 | -0.061554 | 0.0019358 | 0.00048515
51 | 0.99124 | -0.061702 | 0.00037698 | 9.4479e-05
52 | 0.991 | -0.063435 | 0.0005754 | 0.00014421
53 | 0.99086 | -0.064479 | 0.0015025 | 0.00037656
54 | 0.99086 | -0.064538 | 0.0003072 | 7.6992e-05
55 | 0.99288 | -0.050033 | 0.0017029 | 0.00042679
56 | 0.99296 | -0.049476 | 0 | 0
57 | 0.9931 | -0.048482 | 0.00020306 | 5.0892e-05
58 | 0.99471 | -0.037022 | 0.0094081 | 0.0023579
59 | 0.97699 | -0.16366 | 0.00015581 | 3.9051e-05
60 | 0.97149 | -0.20334 | 0 | 0
61 | 0.97177 | -0.20126 | 0.0017719 | 0.00044408
62 | 0.97147 | -0.2035 | 0.00059498 | 0.00014912
63 | 0.97136 | -0.20428 | 0.0010175 | 0.00025502
64 | 0.97144 | -0.2037 | 0.00013804 | 3.4595e-05
65 | 0.9714 | -0.20394 | 0.00043402 | 0.00010878
66 | 0.97131 | -0.20465 | 0.000455 | 0.00011403
67 | 0.97129 | -0.20476 | 0.0010298 | 0.00025809
68 | 0.97825 | -0.15458 | 0.00060292 | 0.00015111
69 | 0.97846 | -0.15306 | 0.00010239 | 2.5662e-05
70 | 0.97229 | -0.19755 | 0.00020897 | 5.2374e-05
71 | 0.97856 | -0.15232 | 0.0001639 | 4.1077e-05
72 | 0.97864 | -0.15171 | 0 | 0
73 | 0.97862 | -0.15188 | 0.00086051 | 0.00021566
74 | 0.97861 | -0.15195 | 0.0002416 | 6.0551e-05
75 | 0.99373 | -0.043969 | 0 | 0
76 | 0.99506 | -0.034586 | 0 | 0
77 | 0.97848 | -0.15308 | 0.00051726 | 0.00012964
78 | 0.97686 | -0.16285 | 0.0065092 | 0.0016313
79 | 0.97683 | -0.1631 | 0.00088776 | 0.00022249
80 | 0.97674 | -0.16373 | 0.0011941 | 0.00029926
81 | 0.97216 | -0.19849 | 0.00095594 | 0.00023958
82 | 0.97203 | -0.19939 | 0.00016859 | 4.2253e-05
83 | 0.97134 | -0.20439 | 0.000335 | 8.396e-05
84 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0031493 | 0.00077654 | -0.0031491 | -0.00077666 | 2.5259e-07 | -1.2339e-07 | 0.004793 | 0.0047931 | 0.0047931 | 0.97679 | -0.16557 | 0.97671 | -0.16617 | 1.7752
1 | -0.003369 | -0.0008316 | 0.0033691 | 0.00083157 | 8.8756e-08 | -3.3579e-08 | 0.0051277 | 0.0051277 | 0.0051277 | 0.97679 | -0.16557 | 0.97682 | -0.16538 | 1.8992
2 | 0.0031491 | 0.00077666 | -0.0031487 | -0.00077682 | 3.1745e-07 | -1.5501e-07 | 0.0047931 | 0.0047932 | 0.0047932 | 0.97671 | -0.16617 | 0.97661 | -0.16692 | 1.7753
3 | -0.0033691 | -0.00083157 | 0.0033718 | 0.00083054 | 2.7137e-06 | -1.0288e-06 | 0.0051277 | 0.005127 | 0.0051277 | 0.97682 | -0.16538 | 0.97763 | -0.15937 | 1.8991
4 | 0.0031487 | 0.00077682 | -0.0031483 | -0.00077702 | 4.126e-07 | -2.0137e-07 | 0.0047932 | 0.0047933 | 0.0047933 | 0.97661 | -0.16692 | 0.97648 | -0.1679 | 1.7753
5 | -0.0033718 | -0.00083054 | 0.0033725 | 0.00083027 | 7.2206e-07 | -2.7441e-07 | 0.005127 | 0.0051268 | 0.005127 | 0.97763 | -0.15937 | 0.97785 | -0.15777 | 1.8989
6 | 0.0029121 | 0.00071782 | -0.0029108 | -0.00071867 | 1.3362e-06 | -8.4814e-07 | 0.0044334 | 0.0044339 | 0.0044339 | 0.97648 | -0.1679 | 0.97601 | -0.17132 | 1.6422
7 | 0.0020037 | 0.00049218 | -0.0020037 | -0.00049221 | 1.9299e-08 | -3.4048e-08 | 0.0030521 | 0.0030521 | 0.0030521 | 0.97576 | -0.17321 | 0.97575 | -0.17328 | 1.1304
8 | -0.0022065 | -0.000543 | 0.0022068 | 0.00054265 | 2.5175e-07 | -3.4928e-07 | 0.0033613 | 0.0033612 | 0.0033613 | 0.97576 | -0.17321 | 0.97587 | -0.17235 | 1.2449
9 | 0.0015592 | 0.00038082 | -0.0015582 | -0.00038417 | 1.0606e-06 | -3.3534e-06 | 0.0023743 | 0.0023756 | 0.0023756 | 0.97575 | -0.17328 | 0.97506 | -0.1784 | 0.87986
10 | -0.0025616 | -0.00063157 | 0.0025619 | 0.00063124 | 3.5606e-07 | -3.3134e-07 | 0.0039022 | 0.003902 | 0.0039022 | 0.97587 | -0.17235 | 0.97601 | -0.17132 | 1.4452
11 | 0.0011965 | 0.00029353 | -0.0011965 | -0.0002938 | 4.7058e-08 | -2.6469e-07 | 0.0018237 | 0.0018238 | 0.0018238 | 0.97506 | -0.1784 | 0.97503 | -0.1787 | 0.6755
12 | -0.0035919 | -0.00088524 | 0.0035937 | 0.00088472 | 1.7987e-06 | -5.2162e-07 | 0.0054606 | 0.0054601 | 0.0054606 | 0.97785 | -0.15777 | 0.97835 | -0.15403 | 2.0224
13 | -0.0040746 | -0.0010052 | 0.0040751 | 0.0010052 | 5.2414e-07 | -7.36e-08 | 0.0061915 | 0.0061914 | 0.0061915 | 0.97835 | -0.15403 | 0.97848 | -0.15308 | 2.2931
14 | 0.0010689 | 0.00026183 | -0.0010689 | -0.00026194 | 1.5262e-08 | -1.0905e-07 | 0.0016292 | 0.0016292 | 0.0016292 | 0.97503 | -0.1787 | 0.97501 | -0.1788 | 0.60342
15 | 0.0010689 | 0.00026194 | -0.0010689 | -0.00026223 | 4.1341e-08 | -2.9536e-07 | 0.0016292 | 0.0016293 | 0.0016293 | 0.97501 | -0.1788 | 0.97497 | -0.1791 | 0.60346
16 | 0.00071238 | 0.00017392 | -0.00071237 | -0.00017422 | 1.7812e-08 | -2.9516e-07 | 0.0010856 | 0.0010857 | 0.0010857 | 0.97497 | -0.1791 | 0.97495 | -0.17928 | 0.40212
17 | 0.0003565 | 8.8313e-05 | -0.00035649 | -8.9344e-05 | 1.5344e-08 | -1.0306e-06 | 0.00054373 | 0.0005441 | 0.0005441 | 0.97497 | -0.1791 | 0.97493 | -0.17941 | 0.20152
18 | 0.00071237 | 0.00017422 | -0.00071236 | -0.00017433 | 6.9612e-09 | -1.1533e-07 | 0.0010857 | 0.0010858 | 0.0010858 | 0.97495 | -0.17928 | 0.97494 | -0.17936 | 0.40213
19 | 0.00065245 | 0.00015932 | -0.00065227 | -0.00016297 | 1.8441e-07 | -3.6504e-06 | 0.00099432 | 0.00099564 | 0.00099564 | 0.97494 | -0.17936 | 0.97465 | -0.18146 | 0.36876
20 | 0.00048209 | 0.00012032 | -0.00048208 | -0.00012082 | 1.3793e-08 | -5.0334e-07 | 0.00073584 | 0.00073602 | 0.00073602 | 0.97465 | -0.18146 | 0.97462 | -0.18167 | 0.2726
21 | -0.00082677 | -0.00020721 | 0.00082685 | 0.00020614 | 8.4629e-08 | -1.0714e-06 | 0.0012499 | 0.0012495 | 0.0012499 | 0.9843 | -0.1099 | 0.9844 | -0.10916 | 0.46292
22 | -0.0046248 | -0.001158 | 0.0046264 | 0.0011579 | 1.5843e-06 | -5.1454e-08 | 0.0069904 | 0.0069902 | 0.0069904 | 0.9844 | -0.10916 | 0.98475 | -0.10668 | 2.589
23 | -0.016874 | -0.0042275 | 0.016891 | 0.0042335 | 1.6888e-05 | 5.9652e-06 | 0.025497 | 0.025497 | 0.025497 | 0.98475 | -0.10668 | 0.98577 | -0.099452 | 9.4435
24 | 0.095865 | 0.024208 | -0.09509 | -0.023913 | 0.00077464 | 0.00029477 | 0.14271 | 0.14271 | 0.14271 | 1 | 0 | 0.99167 | -0.057967 | 26.4284
25 | 0.12192 | 0.030665 | -0.12161 | -0.030544 | 0.00031774 | 0.0001214 | 0.18146 | 0.18146 | 0.18146 | 1 | 0 | 0.99731 | -0.018742 | 33.6044
26 | 0.064655 | 0.016285 | -0.064493 | -0.016223 | 0.00016186 | 6.1899e-05 | 0.097045 | 0.097045 | 0.097045 | 0.99167 | -0.057967 | 0.98911 | -0.075916 | 35.9426
27 | 0.086513 | 0.021745 | -0.086038 | -0.021563 | 0.00047532 | 0.00018222 | 0.1291 | 0.1291 | 0.1291 | 0.99731 | -0.018742 | 0.99166 | -0.058423 | 47.8156
28 | 0.035094 | 0.0087984 | -0.035017 | -0.0087695 | 7.6859e-05 | 2.8976e-05 | 0.052362 | 0.052362 | 0.052362 | 0.99731 | -0.018742 | 0.99506 | -0.034586 | 19.3933
29 | -0.060676 | -0.01524 | 0.060875 | 0.015317 | 0.00019924 | 7.6142e-05 | 0.091603 | 0.091603 | 0.091603 | 0.98577 | -0.099452 | 0.98911 | -0.075916 | 33.9269
30 | 0.043785 | 0.011007 | -0.043592 | -0.010934 | 0.00019262 | 7.319e-05 | 0.066105 | 0.066106 | 0.066106 | 0.98577 | -0.099452 | 0.98129 | -0.13118 | 24.4836
31 | 0.010152 | 0.0025444 | -0.010148 | -0.0025433 | 3.4438e-06 | 1.0304e-06 | 0.015394 | 0.015394 | 0.015394 | 0.98129 | -0.13118 | 0.98095 | -0.13363 | 5.7014
32 | 0.033441 | 0.0083894 | -0.03341 | -0.0083776 | 3.1288e-05 | 1.1788e-05 | 0.050712 | 0.050712 | 0.050712 | 0.98129 | -0.13118 | 0.98035 | -0.13793 | 18.7823
33 | 0.01588 | 0.0039844 | -0.015829 | -0.0039664 | 5.1466e-05 | 1.8011e-05 | 0.024106 | 0.024106 | 0.024106 | 0.98035 | -0.13793 | 0.97707 | -0.16136 | 8.9282
34 | 0.0048891 | 0.0012078 | -0.0048843 | -0.0012077 | 4.8434e-06 | 8.9476e-08 | 0.0074197 | 0.0074203 | 0.0074203 | 0.97969 | -0.14421 | 0.97869 | -0.15157 | 2.7483
35 | -0.0050755 | -0.0012545 | 0.0050756 | 0.0012545 | 5.7976e-08 | 2.581e-09 | 0.0077028 | 0.0077028 | 0.0077028 | 0.97969 | -0.14421 | 0.9797 | -0.14413 | 2.8529
36 | 0.0045933 | 0.0011348 | -0.0045923 | -0.0011348 | 9.3068e-07 | -2.6875e-08 | 0.0069779 | 0.006978 | 0.006978 | 0.97869 | -0.15157 | 0.97848 | -0.15308 | 2.5844
37 | -0.017078 | -0.0042543 | 0.017315 | 0.0043382 | 0.00023695 | 8.3921e-05 | 0.025929 | 0.025927 | 0.025929 | 0.9797 | -0.14413 | 0.99373 | -0.043969 | 9.6034
38 | 0.012002 | 0.0029997 | -0.01199 | -0.0029957 | 1.2519e-05 | 4.0555e-06 | 0.018226 | 0.018227 | 0.018227 | 0.9797 | -0.14413 | 0.97864 | -0.15171 | 6.7506
39 | 0.0085929 | 0.0021529 | -0.0085912 | -0.0021524 | 1.7756e-06 | 4.7485e-07 | 0.013086 | 0.013086 | 0.013086 | 0.97707 | -0.16136 | 0.97686 | -0.16285 | 4.8468
40 | -0.00022169 | -5.556e-05 | 0.00022169 | 5.4835e-05 | 4.1471e-09 | -7.2539e-07 | 0.00033806 | 0.0003378 | 0.00033806 | 0.97578 | -0.17235 | 0.9758 | -0.17221 | 0.12521
41 | 0.0071395 | 0.0017856 | -0.0071146 | -0.0017802 | 2.4906e-05 | 5.3874e-06 | 0.010886 | 0.010887 | 0.010887 | 0.9758 | -0.17221 | 0.97229 | -0.19755 | 4.0323
42 | -0.0073612 | -0.0018404 | 0.0073744 | 0.0018434 | 1.32e-05 | 2.9751e-06 | 0.011224 | 0.011223 | 0.011224 | 0.9758 | -0.17221 | 0.9776 | -0.15921 | 4.1569
43 | 0.00059443 | 0.00014855 | -0.00059441 | -0.00014897 | 1.7589e-08 | -4.2359e-07 | 0.00090538 | 0.00090553 | 0.00090553 | 0.9768 | -0.16505 | 0.97677 | -0.16527 | 0.33538
44 | -0.00070179 | -0.00017546 | 0.00070184 | 0.00017449 | 5.6261e-08 | -9.6652e-07 | 0.0010689 | 0.0010686 | 0.0010689 | 0.9768 | -0.16505 | 0.97688 | -0.16447 | 0.3959
45 | -0.0015663 | -0.00039114 | 0.0015664 | 0.0003909 | 7.7172e-08 | -2.4247e-07 | 0.0023853 | 0.0023852 | 0.0023853 | 0.97688 | -0.16447 | 0.97693 | -0.16411 | 0.88345
46 | -0.0015664 | -0.0003909 | 0.0015665 | 0.00039058 | 1.0217e-07 | -3.2109e-07 | 0.0023852 | 0.0023851 | 0.0023852 | 0.97693 | -0.16411 | 0.97699 | -0.16364 | 0.88342
47 | 0.0022404 | 0.00055713 | -0.0022391 | -0.00055895 | 1.3567e-06 | -1.8225e-06 | 0.0034086 | 0.0034095 | 0.0034095 | 0.9776 | -0.15921 | 0.97699 | -0.16364 | 1.2628
48 | -0.0098407 | -0.0024571 | 0.0098451 | 0.0024584 | 4.4261e-06 | 1.3056e-06 | 0.014975 | 0.014975 | 0.014975 | 0.9776 | -0.15921 | 0.97806 | -0.15594 | 5.5464
49 | 0.00015581 | 3.8854e-05 | -0.00015581 | -3.9051e-05 | 5.525e-10 | -1.9672e-07 | 0.00023724 | 0.00023731 | 0.00023731 | 0.97699 | -0.16364 | 0.97699 | -0.16366 | 0.087894
50 | -0.010012 | -0.0025003 | 0.010014 | 0.0025009 | 1.8639e-06 | 5.5523e-07 | 0.015229 | 0.015229 | 0.015229 | 0.97806 | -0.15594 | 0.97825 | -0.15458 | 5.6405
51 | 0.0054974 | 0.0013704 | -0.005492 | -0.0013699 | 5.3291e-06 | 4.2644e-07 | 0.0082404 | 0.008241 | 0.008241 | 0.99238 | -0.05361 | 0.99139 | -0.060686 | 3.0522
52 | -0.0060426 | -0.001507 | 0.0060451 | 0.0015073 | 2.4464e-06 | 3.2328e-07 | 0.009058 | 0.0090578 | 0.009058 | 0.99238 | -0.05361 | 0.99279 | -0.050657 | 3.3548
53 | 0.0046993 | 0.0011715 | -0.0046987 | -0.0011716 | 5.5883e-07 | -1.7291e-08 | 0.0070512 | 0.0070513 | 0.0070513 | 0.99139 | -0.060686 | 0.99127 | -0.061554 | 2.6116
54 | 0.00043092 | 0.00010771 | -0.00043091 | -0.000108 | 5.7885e-09 | -2.8374e-07 | 0.00064669 | 0.00064679 | 0.00064679 | 0.99139 | -0.060686 | 0.99137 | -0.060783 | 0.23955
55 | -0.0063444 | -0.0015824 | 0.0063454 | 0.0015825 | 1.0271e-06 | 1.5948e-07 | 0.0095064 | 0.0095063 | 0.0095064 | 0.99279 | -0.050657 | 0.99296 | -0.049476 | 3.5209
56 | 0.0027629 | 0.0006864 | -0.0027629 | -0.00068645 | 5.548e-08 | -4.5357e-08 | 0.0041454 | 0.0041454 | 0.0041454 | 0.99127 | -0.061554 | 0.99124 | -0.061702 | 1.5353
57 | 0.0023859 | 0.00059197 | -0.0023853 | -0.00059266 | 5.6198e-07 | -6.8962e-07 | 0.0035795 | 0.0035798 | 0.0035798 | 0.99124 | -0.061702 | 0.991 | -0.063435 | 1.3259
58 | 0.0015027 | 0.00037576 | -0.0015025 | -0.00037656 | 2.1666e-07 | -7.9536e-07 | 0.002256 | 0.0022564 | 0.0022564 | 0.991 | -0.063435 | 0.99086 | -0.064479 | 0.83569
59 | 0.00030724 | 7.2685e-05 | -0.0003072 | -7.6992e-05 | 4.443e-08 | -4.3068e-06 | 0.00045985 | 0.00046134 | 0.00046134 | 0.991 | -0.063435 | 0.99086 | -0.064538 | 0.17087
60 | -0.0017029 | -0.00042679 | 0.001703 | 0.00042642 | 1.3098e-07 | -3.6648e-07 | 0.0025521 | 0.002552 | 0.0025521 | 0.99288 | -0.050033 | 0.99296 | -0.049476 | 0.94522
61 | -0.0080485 | -0.0020089 | 0.0080496 | 0.0020092 | 1.0998e-06 | 2.6618e-07 | 0.012058 | 0.012058 | 0.012058 | 0.99296 | -0.049476 | 0.9931 | -0.048482 | 4.466
62 | -0.0082526 | -0.0020601 | 0.0082656 | 0.0020633 | 1.3e-05 | 3.2333e-06 | 0.012362 | 0.012362 | 0.012362 | 0.9931 | -0.048482 | 0.99471 | -0.037022 | 4.5787
63 | -0.017674 | -0.0044212 | 0.01768 | 0.0044233 | 5.9399e-06 | 2.1077e-06 | 0.026436 | 0.026436 | 0.026436 | 0.99471 | -0.037022 | 0.99506 | -0.034586 | 9.791
64 | -0.0040049 | -0.0010016 | 0.004006 | 0.0010014 | 1.1483e-06 | -1.6422e-07 | 0.0061335 | 0.0061332 | 0.0061335 | 0.97149 | -0.20334 | 0.97177 | -0.20126 | 2.2717
65 | 0.0026522 | 0.00066372 | -0.0026521 | -0.00066377 | 5.6176e-08 | -4.5951e-08 | 0.0040619 | 0.004062 | 0.004062 | 0.97149 | -0.20334 | 0.97147 | -0.2035 | 1.5044
66 | 0.0013527 | 0.00033785 | -0.0013525 | -0.00033859 | 1.7466e-07 | -7.4023e-07 | 0.0020715 | 0.0020718 | 0.0020718 | 0.97149 | -0.20334 | 0.97136 | -0.20428 | 0.76734
67 | -0.0057779 | -0.0014455 | 0.0057794 | 0.0014457 | 1.493e-06 | 1.9535e-07 | 0.0088465 | 0.0088463 | 0.0088465 | 0.97177 | -0.20126 | 0.97203 | -0.19939 | 3.2765
68 | 0.0020571 | 0.00051465 | -0.0020571 | -0.00051475 | 5.7985e-08 | -9.36e-08 | 0.0031506 | 0.0031506 | 0.0031506 | 0.97147 | -0.2035 | 0.97144 | -0.2037 | 1.1669
69 | 0.00033501 | 8.3574e-05 | -0.000335 | -8.396e-05 | 5.1479e-09 | -3.8586e-07 | 0.00051306 | 0.0005132 | 0.0005132 | 0.97136 | -0.20428 | 0.97134 | -0.20439 | 0.19007
70 | 0.001919 | 0.00048015 | -0.001919 | -0.00048028 | 6.4893e-08 | -1.2407e-07 | 0.0029392 | 0.0029393 | 0.0029393 | 0.97144 | -0.2037 | 0.9714 | -0.20394 | 1.0886
71 | 0.0014849 | 0.0003715 | -0.0014848 | -0.000372 | 1.4411e-07 | -4.9715e-07 | 0.0022744 | 0.0022746 | 0.0022746 | 0.9714 | -0.20394 | 0.97131 | -0.20465 | 0.84245
72 | 0.0010298 | 0.00025796 | -0.0010298 | -0.00025809 | 1.6147e-08 | -1.2247e-07 | 0.0015776 | 0.0015776 | 0.0015776 | 0.97131 | -0.20465 | 0.97129 | -0.20476 | 0.5843
73 | -0.010617 | -0.002652 | 0.010619 | 0.0026526 | 2.2168e-06 | 6.8149e-07 | 0.016146 | 0.016146 | 0.016146 | 0.97825 | -0.15458 | 0.97846 | -0.15306 | 5.9801
74 | -0.010722 | -0.0026783 | 0.010723 | 0.0026786 | 1.1004e-06 | 3.3988e-07 | 0.016302 | 0.016302 | 0.016302 | 0.97846 | -0.15306 | 0.97856 | -0.15232 | 6.0378
75 | 0.0069056 | 0.0017278 | -0.0069047 | -0.0017276 | 8.9631e-07 | 1.8523e-07 | 0.010567 | 0.010568 | 0.010568 | 0.97229 | -0.19755 | 0.97216 | -0.19849 | 3.9139
76 | -0.010887 | -0.0027197 | 0.010887 | 0.00272 | 9.096e-07 | 2.8299e-07 | 0.016551 | 0.016551 | 0.016551 | 0.97856 | -0.15232 | 0.97864 | -0.15171 | 6.13
77 | 0.0011021 | 0.00027568 | -0.0011021 | -0.00027585 | 2.4947e-08 | -1.6931e-07 | 0.0016756 | 0.0016757 | 0.0016757 | 0.97864 | -0.15171 | 0.97862 | -0.15188 | 0.62061
78 | 0.0002416 | 6.0183e-05 | -0.0002416 | -6.0551e-05 | 2.4734e-09 | -3.682e-07 | 0.00036723 | 0.00036736 | 0.00036736 | 0.97862 | -0.15188 | 0.97861 | -0.15195 | 0.13606
79 | -0.017315 | -0.0043382 | 0.017337 | 0.0043461 | 2.2505e-05 | 7.9598e-06 | 0.025927 | 0.025926 | 0.025927 | 0.99373 | -0.043969 | 0.99506 | -0.034586 | 9.6025
80 | 0.002082 | 0.00052105 | -0.0020819 | -0.00052116 | 7.0463e-08 | -1.1347e-07 | 0.0031712 | 0.0031712 | 0.0031712 | 0.97686 | -0.16285 | 0.97683 | -0.1631 | 1.1745
81 | 0.0011942 | 0.00029867 | -0.0011941 | -0.00029926 | 1.0466e-07 | -5.9426e-07 | 0.0018189 | 0.0018191 | 0.0018191 | 0.97683 | -0.1631 | 0.97674 | -0.16373 | 0.67374
82 | 0.0059488 | 0.0014881 | -0.005948 | -0.0014879 | 7.3549e-07 | 1.0659e-07 | 0.0091043 | 0.0091044 | 0.0091044 | 0.97216 | -0.19849 | 0.97203 | -0.19939 | 3.372

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24068 | 0.06041

## res_load
| p_mw | q_mvar
0 | 0.00021971 | 5.5064e-05
1 | 0.00023621 | 5.92e-05
2 | 0.00020277 | 5.082e-05
3 | 0.00044447 | 0.00011139
4 | 0.0003548 | 8.8921e-05
5 | 0.00036165 | 9.0637e-05
6 | 0.00021935 | 5.4975e-05
7 | 0.00048087 | 0.00012052
8 | 0.00034886 | 8.7433e-05
9 | 0.00012755 | 3.1967e-05
10 | 0.00035649 | 8.9344e-05
11 | 5.9907e-05 | 1.5014e-05
12 | 0.00017017 | 4.2649e-05
13 | 0.00082677 | 0.00020721
14 | 0.0037979 | 0.00095185
15 | 0.012248 | 0.0030696
16 | 0.022092 | 0.0055368
17 | 0.030435 | 0.0076277
18 | 0.0036177 | 0.00090668
19 | 0.010148 | 0.0025433
20 | 0.017529 | 0.0043932
21 | 0.00018643 | 4.6723e-05
22 | 0.000291 | 7.2932e-05
23 | 0.007236 | 0.0018135
24 | 0.086038 | 0.021563
25 | 0.00048208 | 0.00012082
26 | 0.00022169 | 5.556e-05
27 | 0.00010736 | 2.6906e-05
28 | 0.00059441 | 0.00014897
29 | 0.00086445 | 0.00021665
30 | 0.00022586 | 5.6605e-05
31 | 0.0005168 | 0.00012952
32 | 0.00016705 | 4.1866e-05
33 | 0.00054527 | 0.00013666
34 | 0.00036183 | 9.0684e-05
35 | 0.00029932 | 7.5016e-05
36 | 0.00043091 | 0.000108
37 | 0.0019358 | 0.00048515
38 | 0.00037698 | 9.4479e-05
39 | 0.0005754 | 0.00014421
40 | 0.0015025 | 0.00037656
41 | 0.0003072 | 7.6992e-05
42 | 0.0017029 | 0.00042679
43 | 0.00020306 | 5.0892e-05
44 | 0.0094081 | 0.0023579
45 | 0.00015581 | 3.9051e-05
46 | 0.0017719 | 0.00044408
47 | 0.00059498 | 0.00014912
48 | 0.0010175 | 0.00025502
49 | 0.00013804 | 3.4595e-05
50 | 0.00043402 | 0.00010878
51 | 0.000455 | 0.00011403
52 | 0.0010298 | 0.00025809
53 | 0.00060292 | 0.00015111
54 | 0.00010239 | 2.5662e-05
55 | 0.00020897 | 5.2374e-05
56 | 0.0001639 | 4.1077e-05
57 | 0.00086051 | 0.00021566
58 | 0.0002416 | 6.0551e-05
59 | 0.00051726 | 0.00012964
60 | 0.0065092 | 0.0016313
61 | 0.00088776 | 0.00022249
62 | 0.0011941 | 0.00029926
63 | 0.00095594 | 0.00023958
64 | 0.00016859 | 4.2253e-05
65 | 0.000335 | 8.396e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1