## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1009-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1009-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1009-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1009-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1009-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1009-1_0_3_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1009-1_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1009-1_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1009-1_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1009-1_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1009-1_0_3_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_1009-1_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1009-1_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1009-1_0_3_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1009-1_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1009-1_0_3_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1009-1_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1009-1_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1009-1_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1009-1_0_3_node_28 | 0.4 | n |  | TRUE
20 | bus_LV_1009-1_0_3_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1009-1_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1009-1_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1009-1_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1009-1_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1009-1_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1009-1_0_3_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1009-1_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1009-1_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1009-1_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1009-1_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_1009-1_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1009-1_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1009-1_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1009-1_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1009-1_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1009-1_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1009-1_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_MV_2_0_node_59 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1009-1_0_3_load_0 | 0 | 0.0060039 | 0.0015047 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1009-1_0_3_load_1 | 1 | 0.0028658 | 0.00071823 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1009-1_0_3_load_2 | 2 | 0.0042248 | 0.0010588 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1009-1_0_3_load_38 | 10 | 0.0064753 | 0.0016229 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1009-1_0_3_load_7 | 11 | 0.027746 | 0.0069539 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1009-1_0_3_load_5 | 12 | 0.0013248 | 0.00033203 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1009-1_0_3_load_27 | 13 | 0.0014207 | 0.00035606 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1009-1_0_3_load_36 | 15 | 0.0020172 | 0.00050557 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1009-1_0_3_load_13 | 16 | 0.001163 | 0.00029147 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1009-1_0_3_load_9 | 17 | 0.010781 | 0.0027021 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1009-1_0_3_load_26 | 18 | 0.0076382 | 0.0019143 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1009-1_0_3_load_28 | 19 | 0.0020837 | 0.00052222 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1009-1_0_3_load_10 | 20 | 0.043961 | 0.011018 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1009-1_0_3_load_12 | 21 | 0.011661 | 0.0029226 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1009-1_0_3_load_21 | 24 | 0.026004 | 0.0065173 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1009-1_0_3_load_24 | 25 | 0.013103 | 0.003284 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1009-1_0_3_load_22 | 26 | 0.0099076 | 0.0024831 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1009-1_0_3_load_15 | 27 | 0.0015633 | 0.00039181 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1009-1_0_3_load_16 | 28 | 0.0047824 | 0.0011986 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1009-1_0_3_load_18 | 29 | 0.0017577 | 0.00044053 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1009-1_0_3_load_29 | 31 | 0.0023536 | 0.00058986 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1009-1_0_3_load_34 | 35 | 0.0037677 | 0.00094427 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1009-1_0_3_load_35 | 36 | 0.008242 | 0.0020656 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1009-1_0_3_load_37 | 37 | 0.00092818 | 0.00023262 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1009-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.050652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_1009-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.00047532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1009-1_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.064232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1009-1_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0089021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1009-1_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.005184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1009-1_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.061359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1009-1_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.015474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1009-1_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.11749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1009-1_0_3_line_8 | NAYY 4x150 SE | 6 | 11 | 0.035263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1009-1_0_3_line_9 | NAYY 4x150 SE | 6 | 12 | 0.019441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1009-1_0_3_line_10 | NAYY 4x150 SE | 7 | 13 | 0.046881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1009-1_0_3_line_11 | NAYY 4x150 SE | 8 | 9 | 0.005492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1009-1_0_3_line_12 | NAYY 4x150 SE | 8 | 27 | 0.031732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1009-1_0_3_line_13 | NAYY 4x150 SE | 9 | 10 | 0.077669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1009-1_0_3_line_14 | NAYY 4x150 SE | 10 | 30 | 0.13023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1009-1_0_3_line_15 | NAYY 4x150 SE | 11 | 14 | 0.018208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1009-1_0_3_line_16 | NAYY 4x150 SE | 11 | 15 | 0.02498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1009-1_0_3_line_17 | NAYY 4x150 SE | 13 | 19 | 0.00031461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1009-1_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.010215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1009-1_0_3_line_19 | NAYY 4x150 SE | 14 | 17 | 0.023678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1009-1_0_3_line_20 | NAYY 4x150 SE | 15 | 18 | 0.038494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1009-1_0_3_line_21 | NAYY 4x150 SE | 17 | 20 | 0.025031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1009-1_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.013913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1009-1_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.047792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1009-1_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.04569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1009-1_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.03055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1009-1_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.073088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1009-1_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.010503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1009-1_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0038056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1009-1_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0039768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1009-1_0_3_line_30 | NAYY 4x150 SE | 30 | 35 | 0.037109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1009-1_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.029949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1009-1_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.013899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1009-1_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.004372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1009-1_0_3_line_34 | NAYY 4x150 SE | 33 | 35 | 0.042334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1009-1_0_3_line_35 | NAYY 4x150 SE | 33 | 36 | 0.0057207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1009-1_0_3_line_36 | NAYY 4x150 SE | 34 | 37 | 0.083306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1009-1_0_3_trafo_21 | 0.25 MVA 20/0.4 kV | 38 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2652781.1642 | 1210257.0885 | 2652763.8549 | 1210264.2946 | 2652740.6702 | 1210271.6719 | 2652733.5382 | 1210274.2177
1 | 2652781.1642 | 1210257.0885 | 2652781.603 | 1210256.9058
2 | 2652673.0443 | 1210295.8114 | 2652733.5382 | 1210274.2177
3 | 2652789.8213 | 1210253.4844 | 2652781.603 | 1210256.9058
4 | 2652673.0443 | 1210295.8114 | 2652675.2372 | 1210300.5113
5 | 2652789.8213 | 1210253.4844 | 2652791.6184 | 1210257.3915 | 2652816.495 | 1210308.742
6 | 2652781.4465 | 1210262.0154 | 2652791.6184 | 1210257.3915 | 2652789.8213 | 1210253.4844
7 | 2652564.3224 | 1210340.1572 | 2652675.2372 | 1210300.5113
8 | 2652831.7249 | 1210340.5623 | 2652816.495 | 1210308.742
9 | 2652816.495 | 1210308.742 | 2652834.1078 | 1210300.5124
10 | 2652781.4465 | 1210262.0154 | 2652779.4091 | 1210262.9424 | 2652737.4144 | 1210278.0875
11 | 2652561.8195 | 1210335.2656 | 2652564.3224 | 1210340.1572
12 | 2652564.3224 | 1210340.1572 | 2652576.0064 | 1210369.6603
13 | 2652561.8195 | 1210335.2656 | 2652488.4634 | 1210360.7876
14 | 2652365.4667 | 1210403.5805 | 2652488.4634 | 1210360.7876
15 | 2652831.7249 | 1210340.5623 | 2652820.6767 | 1210345.4674 | 2652815.1352 | 1210348.1644
16 | 2652831.7249 | 1210340.5623 | 2652841.7735 | 1210363.4323
17 | 2652737.1184 | 1210278.1942 | 2652737.4144 | 1210278.0875
18 | 2652815.1352 | 1210348.1644 | 2652810.3398 | 1210339.1454
19 | 2652815.1352 | 1210348.1644 | 2652799.6299 | 1210355.187 | 2652793.615 | 1210358.0385
20 | 2652858.2665 | 1210398.2 | 2652848.4572 | 1210378.6441 | 2652841.7735 | 1210363.4323
21 | 2652793.615 | 1210358.0385 | 2652775.8715 | 1210366.4503 | 2652770.9981 | 1210368.7628
22 | 2652758.4273 | 1210374.7243 | 2652764.1411 | 1210372.0165 | 2652770.9981 | 1210368.7628
23 | 2652715.2433 | 1210395.1983 | 2652743.2754 | 1210381.9047 | 2652758.4273 | 1210374.7243
24 | 2652673.8483 | 1210414.789 | 2652710.3589 | 1210397.5121 | 2652715.2433 | 1210395.1983
25 | 2652715.2433 | 1210395.1983 | 2652713.5202 | 1210391.5254 | 2652702.265 | 1210367.5417
26 | 2652673.8483 | 1210414.789 | 2652673.6606 | 1210417.9781 | 2652673.9289 | 1210420.293 | 2652674.6114 | 1210423.0451 | 2652683.9029 | 1210438.0359 | 2652685.8281 | 1210440.3432 | 2652686.9349 | 1210441.5203 | 2652688.3321 | 1210442.511 | 2652689.9092 | 1210442.9363 | 2652691.3744 | 1210443.1049 | 2652693.8857 | 1210442.7268 | 2652718.2523 | 1210431.3908 | 2652720.3697 | 1210430.8647 | 2652722.3761 | 1210430.8602 | 2652724.0753 | 1210431.2199 | 2652726.0739 | 1210432.1047 | 2652726.1674 | 1210432.1862
27 | 2652697.8029 | 1210358.0334 | 2652702.265 | 1210367.5417
28 | 2652577.4076 | 1210373.1985 | 2652576.0064 | 1210369.6603
29 | 2652578.8719 | 1210376.896 | 2652577.4076 | 1210373.1985
30 | 2652365.4667 | 1210403.5805 | 2652346.2706 | 1210391.3049 | 2652332.5345 | 1210387.2438
31 | 2652283.8255 | 1210432.5265 | 2652282.7291 | 1210426.6912 | 2652290.082 | 1210416.7164 | 2652292.7093 | 1210410.9026 | 2652292.8597 | 1210405.6653
32 | 2652293.3406 | 1210391.7746 | 2652293.0375 | 1210399.4765 | 2652292.8597 | 1210405.6653
33 | 2652283.8255 | 1210432.5265 | 2652285.4467 | 1210436.5876
34 | 2652293.3406 | 1210391.7746 | 2652296.6624 | 1210387.3678 | 2652304.8811 | 1210384.4047 | 2652313.3169 | 1210383.5448 | 2652328.0173 | 1210385.9083 | 2652332.5345 | 1210387.2438
35 | 2652293.3406 | 1210391.7746 | 2652288.5111 | 1210388.7083
36 | 2652285.4467 | 1210436.5876 | 2652364.1787 | 1210409.3634

## bus_geodata
| x | y | coords
0 | 2652781.1642 | 1210257.0885
1 | 2652733.5382 | 1210274.2177
2 | 2652781.603 | 1210256.9058
3 | 2652673.0443 | 1210295.8114
4 | 2652789.8213 | 1210253.4844
5 | 2652675.2372 | 1210300.5113
6 | 2652816.495 | 1210308.742
7 | 2652781.4465 | 1210262.0154
8 | 2652564.3224 | 1210340.1572
9 | 2652561.8195 | 1210335.2656
10 | 2652488.4634 | 1210360.7876
11 | 2652831.7249 | 1210340.5623
12 | 2652834.1078 | 1210300.5124
13 | 2652737.4144 | 1210278.0875
14 | 2652815.1352 | 1210348.1644
15 | 2652841.7735 | 1210363.4323
16 | 2652810.3398 | 1210339.1454
17 | 2652793.615 | 1210358.0385
18 | 2652858.2665 | 1210398.2
19 | 2652737.1184 | 1210278.1943
20 | 2652770.9981 | 1210368.7628
21 | 2652758.4273 | 1210374.7243
22 | 2652715.2433 | 1210395.1983
23 | 2652673.8483 | 1210414.789
24 | 2652702.265 | 1210367.5417
25 | 2652726.1674 | 1210432.1862
26 | 2652697.8029 | 1210358.0334
27 | 2652576.0064 | 1210369.6603
28 | 2652577.4076 | 1210373.1985
29 | 2652578.8719 | 1210376.896
30 | 2652365.4667 | 1210403.5805
31 | 2652292.8597 | 1210405.6653
32 | 2652283.8255 | 1210432.5265
33 | 2652293.3406 | 1210391.7746
34 | 2652285.4467 | 1210436.5876
35 | 2652332.5345 | 1210387.2438
36 | 2652288.5111 | 1210388.7083
37 | 2652364.1787 | 1210409.3634
38 | 2652697.8029 | 1210358.0334

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98164 | -0.12877 | 0.0060039 | 0.0015047
1 | 0.98042 | -0.13739 | 0.0028658 | 0.00071823
2 | 0.98165 | -0.12867 | 0.0042248 | 0.0010588
3 | 0.97902 | -0.14739 | 0 | 0
4 | 0.98193 | -0.12669 | 0 | 0
5 | 0.97891 | -0.1482 | 0 | 0
6 | 0.98401 | -0.11193 | 0 | 0
7 | 0.98185 | -0.12725 | 0 | 0
8 | 0.97634 | -0.16656 | 0 | 0
9 | 0.97625 | -0.16719 | 0 | 0
10 | 0.97501 | -0.17607 | 0.0064753 | 0.0016229
11 | 0.98524 | -0.10323 | 0.027746 | 0.0069539
12 | 0.98398 | -0.11219 | 0.0013248 | 0.00033203
13 | 0.98161 | -0.12895 | 0.0014207 | 0.00035606
14 | 0.98637 | -0.095255 | 0 | 0
15 | 0.98489 | -0.10571 | 0.0020172 | 0.00050557
16 | 0.98635 | -0.095377 | 0.001163 | 0.00029147
17 | 0.98786 | -0.084766 | 0.010781 | 0.0027021
18 | 0.98447 | -0.10874 | 0.0076382 | 0.0019143
19 | 0.98161 | -0.12896 | 0.0020837 | 0.00052222
20 | 0.98962 | -0.072337 | 0.043961 | 0.011018
21 | 0.99105 | -0.062338 | 0.011661 | 0.0029226
22 | 0.99633 | -0.025405 | 0 | 0
23 | 0.99547 | -0.031434 | 0 | 0
24 | 1 | 0 | -0.17902 | -0.044971
25 | 0.9941 | -0.041095 | 0.013103 | 0.003284
26 | 0.99985 | -0.0010388 | 0.0099076 | 0.0024831
27 | 0.97596 | -0.16926 | 0.0015633 | 0.00039181
28 | 0.97592 | -0.16952 | 0.0047824 | 0.0011986
29 | 0.97591 | -0.16959 | 0.0017577 | 0.00044053
30 | 0.97208 | -0.19707 | 0 | 0
31 | 0.97047 | -0.20874 | 0.0023536 | 0.00058986
32 | 0.97043 | -0.20903 | 0 | 0
33 | 0.97053 | -0.20825 | 0 | 0
34 | 0.97042 | -0.20908 | 0 | 0
35 | 0.97125 | -0.20308 | 0.0037677 | 0.00094427
36 | 0.97047 | -0.20875 | 0.008242 | 0.0020656
37 | 0.97031 | -0.2099 | 0.00092818 | 0.00023262
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.032996 | 0.0082915 | -0.032956 | -0.0082776 | 3.9548e-05 | 1.3932e-05 | 0.050025 | 0.050025 | 0.050025 | 0.98164 | -0.12877 | 0.98042 | -0.13739 | 9.2639
1 | -0.039 | -0.0097962 | 0.039 | 0.0097964 | 5.1844e-07 | 1.8738e-07 | 0.059126 | 0.059126 | 0.059126 | 0.98164 | -0.12877 | 0.98165 | -0.12867 | 10.9492
2 | 0.030091 | 0.0075594 | -0.030049 | -0.0075449 | 4.181e-05 | 1.4463e-05 | 0.045676 | 0.045676 | 0.045676 | 0.98042 | -0.13739 | 0.97902 | -0.14739 | 8.4586
3 | -0.043225 | -0.010855 | 0.043237 | 0.01086 | 1.1927e-05 | 4.3621e-06 | 0.06553 | 0.06553 | 0.06553 | 0.98165 | -0.12867 | 0.98193 | -0.12669 | 12.1351
4 | 0.030049 | 0.0075449 | -0.030045 | -0.0075437 | 3.3744e-06 | 1.1675e-06 | 0.045676 | 0.045676 | 0.045676 | 0.97902 | -0.14739 | 0.97891 | -0.1482 | 8.4586
5 | -0.046742 | -0.011738 | 0.046838 | 0.011773 | 9.6074e-05 | 3.5396e-05 | 0.070842 | 0.070841 | 0.070842 | 0.98193 | -0.12669 | 0.98401 | -0.11193 | 13.1188
6 | 0.0035054 | 0.0008779 | -0.0035052 | -0.00087799 | 2.7246e-07 | -9.0932e-08 | 0.0053119 | 0.005312 | 0.005312 | 0.98193 | -0.12669 | 0.98185 | -0.12725 | 1.9674
7 | 0.030045 | 0.0075437 | -0.029969 | -0.0075173 | 7.6478e-05 | 2.6468e-05 | 0.045676 | 0.045677 | 0.045677 | 0.97891 | -0.1482 | 0.97634 | -0.16656 | 8.4588
8 | -0.048163 | -0.012105 | 0.048222 | 0.012126 | 5.838e-05 | 2.1557e-05 | 0.072844 | 0.072844 | 0.072844 | 0.98401 | -0.11193 | 0.98524 | -0.10323 | 13.4897
9 | 0.0013249 | 0.0003318 | -0.0013248 | -0.00033203 | 4.869e-08 | -2.2822e-07 | 0.0020034 | 0.0020035 | 0.0020035 | 0.98401 | -0.11193 | 0.98398 | -0.11219 | 0.74202
10 | 0.0035052 | 0.00087799 | -0.0035044 | -0.00087827 | 8.2549e-07 | -2.7528e-07 | 0.005312 | 0.0053122 | 0.0053122 | 0.98185 | -0.12725 | 0.98161 | -0.12895 | 1.9675
11 | 0.021862 | 0.0054856 | -0.02186 | -0.005485 | 1.9026e-06 | 5.9441e-07 | 0.033322 | 0.033322 | 0.033322 | 0.97634 | -0.16656 | 0.97625 | -0.16719 | 6.1707
12 | 0.0081068 | 0.0020317 | -0.0081038 | -0.0020309 | 3.0228e-06 | 7.6593e-07 | 0.012355 | 0.012356 | 0.012356 | 0.97634 | -0.16656 | 0.97596 | -0.16926 | 4.5761
13 | 0.02186 | 0.005485 | -0.021833 | -0.0054765 | 2.6907e-05 | 8.4092e-06 | 0.033322 | 0.033323 | 0.033323 | 0.97625 | -0.16719 | 0.97501 | -0.17607 | 6.1709
14 | 0.015358 | 0.0038537 | -0.015313 | -0.0038381 | 4.4651e-05 | 1.5554e-05 | 0.02344 | 0.023441 | 0.023441 | 0.97501 | -0.17607 | 0.97208 | -0.19707 | 8.6818
15 | -0.08563 | -0.021502 | 0.085725 | 0.021538 | 9.5038e-05 | 3.6089e-05 | 0.12934 | 0.12934 | 0.12934 | 0.98524 | -0.10323 | 0.98637 | -0.095255 | 23.9523
16 | 0.009662 | 0.0024216 | -0.0096587 | -0.0024206 | 3.3193e-06 | 9.5865e-07 | 0.014593 | 0.014593 | 0.014593 | 0.98524 | -0.10323 | 0.98489 | -0.10571 | 5.4047
17 | 0.0020837 | 0.00052221 | -0.0020837 | -0.00052222 | 1.9586e-09 | -3.2239e-09 | 0.0031586 | 0.0031586 | 0.0031586 | 0.98161 | -0.12895 | 0.98161 | -0.12896 | 1.1699
18 | 0.001163 | 0.00029135 | -0.001163 | -0.00029147 | 1.962e-08 | -1.2283e-07 | 0.0017545 | 0.0017545 | 0.0017545 | 0.98637 | -0.095255 | 0.98635 | -0.095377 | 0.64981
19 | -0.086888 | -0.021829 | 0.087015 | 0.021877 | 0.00012696 | 4.8227e-05 | 0.1311 | 0.1311 | 0.1311 | 0.98637 | -0.095255 | 0.98786 | -0.084766 | 24.2771
20 | 0.0076414 | 0.0019151 | -0.0076382 | -0.0019143 | 3.2016e-06 | 7.4172e-07 | 0.011545 | 0.011545 | 0.011545 | 0.98489 | -0.10571 | 0.98447 | -0.10874 | 4.276
21 | -0.097797 | -0.02458 | 0.097966 | 0.024644 | 0.00016953 | 6.4562e-05 | 0.14734 | 0.14734 | 0.14734 | 0.98786 | -0.084766 | 0.98962 | -0.072337 | 27.2845
22 | -0.14193 | -0.035662 | 0.14212 | 0.035737 | 0.00019774 | 7.5697e-05 | 0.21344 | 0.21344 | 0.21344 | 0.98962 | -0.072337 | 0.99105 | -0.062338 | 39.5252
23 | -0.15379 | -0.03866 | 0.15458 | 0.038965 | 0.00079528 | 0.00030464 | 0.23094 | 0.23094 | 0.23094 | 0.99105 | -0.062338 | 0.99633 | -0.025405 | 42.7676
24 | 0.013132 | 0.0032934 | -0.013121 | -0.0032898 | 1.0967e-05 | 3.6236e-06 | 0.019613 | 0.019613 | 0.019613 | 0.99633 | -0.025405 | 0.99547 | -0.031434 | 7.2641
25 | -0.16771 | -0.042258 | 0.16831 | 0.042487 | 0.00059839 | 0.00022935 | 0.25056 | 0.25056 | 0.25056 | 0.99633 | -0.025405 | 1 | 0 | 46.3995
26 | 0.013121 | 0.0032898 | -0.013103 | -0.003284 | 1.7544e-05 | 5.7989e-06 | 0.019613 | 0.019613 | 0.019613 | 0.99547 | -0.031434 | 0.9941 | -0.041095 | 7.2643
27 | 0.009909 | 0.0024835 | -0.0099076 | -0.0024831 | 1.4249e-06 | 4.1027e-07 | 0.014745 | 0.014745 | 0.014745 | 1 | 0 | 0.99985 | -0.0010388 | 5.4611
28 | 0.0065404 | 0.0016391 | -0.0065402 | -0.0016391 | 2.3614e-07 | 4.327e-08 | 0.009972 | 0.009972 | 0.009972 | 0.97596 | -0.16926 | 0.97592 | -0.16952 | 3.6933
29 | 0.0017577 | 0.00044049 | -0.0017577 | -0.00044053 | 1.7824e-08 | -4.2835e-08 | 0.0026801 | 0.0026801 | 0.0026801 | 0.97592 | -0.16952 | 0.97591 | -0.16959 | 0.99262
30 | 0.015313 | 0.0038381 | -0.015301 | -0.0038337 | 1.2724e-05 | 4.4342e-06 | 0.023441 | 0.023441 | 0.023441 | 0.97208 | -0.19707 | 0.97125 | -0.20308 | 8.6819
31 | 0.00092833 | 0.00023123 | -0.00092829 | -0.00023158 | 3.784e-08 | -3.5547e-07 | 0.0014229 | 0.001423 | 0.001423 | 0.97047 | -0.20874 | 0.97043 | -0.20903 | 0.52705
32 | -0.0032819 | -0.00082109 | 0.0032821 | 0.000821 | 2.1957e-07 | -8.7297e-08 | 0.0050316 | 0.0050315 | 0.0050316 | 0.97047 | -0.20874 | 0.97053 | -0.20825 | 1.8636
33 | 0.00092829 | 0.00023158 | -0.00092829 | -0.00023164 | 5.5245e-09 | -5.189e-08 | 0.001423 | 0.001423 | 0.001423 | 0.97043 | -0.20903 | 0.97042 | -0.20908 | 0.52705
34 | -0.011525 | -0.0028868 | 0.011533 | 0.0028894 | 8.247e-06 | 2.6484e-06 | 0.017669 | 0.017669 | 0.017669 | 0.97053 | -0.20825 | 0.97125 | -0.20308 | 6.5441
35 | 0.0082426 | 0.0020658 | -0.008242 | -0.0020656 | 5.701e-07 | 1.4858e-07 | 0.012637 | 0.012637 | 0.012637 | 0.97053 | -0.20825 | 0.97047 | -0.20875 | 4.6805
36 | 0.00092829 | 0.00023164 | -0.00092818 | -0.00023262 | 1.053e-07 | -9.886e-07 | 0.001423 | 0.0014234 | 0.0014234 | 0.97042 | -0.20908 | 0.97031 | -0.2099 | 0.52719

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20502 | 0.051488

## res_load
| p_mw | q_mvar
0 | 0.0060039 | 0.0015047
1 | 0.0028658 | 0.00071823
2 | 0.0042248 | 0.0010588
3 | 0.0064753 | 0.0016229
4 | 0.027746 | 0.0069539
5 | 0.0013248 | 0.00033203
6 | 0.0014207 | 0.00035606
7 | 0.0020172 | 0.00050557
8 | 0.001163 | 0.00029147
9 | 0.010781 | 0.0027021
10 | 0.0076382 | 0.0019143
11 | 0.0020837 | 0.00052222
12 | 0.043961 | 0.011018
13 | 0.011661 | 0.0029226
14 | 0.026004 | 0.0065173
15 | 0.013103 | 0.003284
16 | 0.0099076 | 0.0024831
17 | 0.0015633 | 0.00039181
18 | 0.0047824 | 0.0011986
19 | 0.0017577 | 0.00044053
20 | 0.0023536 | 0.00058986
21 | 0.0037677 | 0.00094427
22 | 0.008242 | 0.0020656
23 | 0.00092818 | 0.00023262

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1