## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1009-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1009-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1009-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1009-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1009-4_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1009-4_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1009-4_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1009-4_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1009-4_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1009-4_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1009-4_0_4_node_53 | 0.4 | n |  | TRUE
11 | bus_LV_1009-4_0_4_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_1009-4_0_4_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1009-4_0_4_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1009-4_0_4_node_44 | 0.4 | n |  | TRUE
15 | bus_LV_1009-4_0_4_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_1009-4_0_4_node_55 | 0.4 | n |  | TRUE
17 | bus_LV_1009-4_0_4_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_1009-4_0_4_node_60 | 0.4 | n |  | TRUE
19 | bus_LV_1009-4_0_4_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_1009-4_0_4_node_62 | 0.4 | n |  | TRUE
21 | bus_MV_2_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1009-4_0_4_load_0 | 0 | 0.012829 | 0.0032153 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1009-4_0_4_load_1 | 1 | 0.0048194 | 0.0012079 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1009-4_0_4_load_5 | 4 | 0.0059116 | 0.0014816 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1009-4_0_4_load_8 | 7 | 0.037172 | 0.0093163 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1009-4_0_4_load_4 | 8 | 0.013219 | 0.003313 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1009-4_0_4_load_53 | 10 | 0.003384 | 0.00084811 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1009-4_0_4_load_58 | 11 | 0.0046427 | 0.0011636 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1009-4_0_4_load_42 | 12 | 0.0018002 | 0.00045116 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1009-4_0_4_load_43 | 13 | 0.0094701 | 0.0023734 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1009-4_0_4_load_44 | 14 | 0.0011759 | 0.00029472 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1009-4_0_4_load_55 | 16 | 0.0066768 | 0.0016734 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1009-4_0_4_load_59 | 17 | 0.00016602 | 4.1609e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1009-4_0_4_load_61 | 19 | 0.00093882 | 0.00023529 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1009-4_0_4_load_62 | 20 | 0.02311 | 0.0057918 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1009-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.034271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1009-4_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.11611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1009-4_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.026257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1009-4_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.13978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1009-4_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.037479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1009-4_0_4_line_5 | NAYY 4x150 SE | 2 | 6 | 0.066195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1009-4_0_4_line_6 | NAYY 4x150 SE | 3 | 7 | 0.046865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1009-4_0_4_line_7 | NAYY 4x150 SE | 5 | 11 | 0.038557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1009-4_0_4_line_8 | NAYY 4x150 SE | 6 | 12 | 0.09323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1009-4_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.025001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1009-4_0_4_line_10 | NAYY 4x150 SE | 8 | 9 | 0.022385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1009-4_0_4_line_11 | NAYY 4x150 SE | 8 | 10 | 0.21799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1009-4_0_4_line_12 | NAYY 4x150 SE | 10 | 15 | 0.015663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1009-4_0_4_line_13 | NAYY 4x150 SE | 11 | 17 | 0.043546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1009-4_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0089258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1009-4_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.0096087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1009-4_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.028285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1009-4_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.066944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1009-4_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.038422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1009-4_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.17085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1009-4_0_4_trafo_2 | 0.25 MVA 20/0.4 kV | 21 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2653346.7335 | 1209900.0542 | 2653375.3818 | 1209881.2461
1 | 2653249.6756 | 1209963.7744 | 2653346.7335 | 1209900.0542
2 | 2653397.3315 | 1209866.8357 | 2653375.3818 | 1209881.2461
3 | 2653249.6756 | 1209963.7744 | 2653142.5229 | 1210031.293 | 2653131.704 | 1210038.7341
4 | 2653220.7587 | 1209975.3679 | 2653247.057 | 1209958.2589 | 2653249.6756 | 1209963.7744
5 | 2653209.3797 | 1209911.5731 | 2653225.2823 | 1209930.0591 | 2653235.8398 | 1209941.9492 | 2653240.6683 | 1209948.5184 | 2653242.6497 | 1209951.3377 | 2653243.6017 | 1209952.8248 | 2653247.057 | 1209958.2589 | 2653249.6756 | 1209963.7744
6 | 2653397.3315 | 1209866.8357 | 2653417.8397 | 1209908.9755
7 | 2653220.7587 | 1209975.3679 | 2653188.4375 | 1209996.3916
8 | 2653209.3797 | 1209911.5731 | 2653131.1133 | 1209962.2302
9 | 2653425.4976 | 1209932.3932 | 2653425.541 | 1209927.5463 | 2653422.9381 | 1209919.4515 | 2653417.8397 | 1209908.9755
10 | 2653425.4976 | 1209932.3932 | 2653423.1989 | 1209938.7097 | 2653419.6021 | 1209943.158 | 2653410.4621 | 1209947.071
11 | 2653410.4621 | 1209947.071 | 2653538.6652 | 1210123.3802
12 | 2653542.5961 | 1210138.5423 | 2653538.6652 | 1210123.3802
13 | 2653188.4375 | 1209996.3916 | 2653151.9343 | 1210020.1356
14 | 2653131.1133 | 1209962.2302 | 2653123.6201 | 1209967.0801
15 | 2653115.5536 | 1209972.3011 | 2653123.6201 | 1209967.0801
16 | 2653542.5961 | 1210138.5423 | 2653570.1366 | 1210132.0967
17 | 2653096.4509 | 1210057.5875 | 2653137.5837 | 1210029.4702 | 2653151.9343 | 1210020.1356
18 | 2653096.4509 | 1210057.5875 | 2653064.3376 | 1210078.6815
19 | 2653064.3376 | 1210078.6815 | 2653155.3495 | 1210223.2755

## bus_geodata
| x | y | coords
0 | 2653346.7335 | 1209900.0542
1 | 2653375.3818 | 1209881.2461
2 | 2653249.6756 | 1209963.7744
3 | 2653397.3315 | 1209866.8357
4 | 2653131.704 | 1210038.7341
5 | 2653220.7587 | 1209975.3679
6 | 2653209.3797 | 1209911.5731
7 | 2653417.8397 | 1209908.9755
8 | 2653410.4621 | 1209947.071
9 | 2653425.4976 | 1209932.3932
10 | 2653538.6652 | 1210123.3802
11 | 2653188.4375 | 1209996.3916
12 | 2653131.1133 | 1209962.2302
13 | 2653123.6201 | 1209967.0801
14 | 2653115.5536 | 1209972.3011
15 | 2653542.5961 | 1210138.5423
16 | 2653570.1366 | 1210132.0967
17 | 2653151.9343 | 1210020.1356
18 | 2653096.4509 | 1210057.5875
19 | 2653064.3376 | 1210078.6815
20 | 2653155.3495 | 1210223.2755
21 | 2653247.0571 | 1209958.2589

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98678 | -0.091765 | 0.012829 | 0.0032153
1 | 0.98352 | -0.11478 | 0.0048194 | 0.0012079
2 | 1 | 0 | -0.12819 | -0.032191
3 | 0.9812 | -0.13121 | 0 | 0
4 | 0.99882 | -0.0082663 | 0.0059116 | 0.0014816
5 | 0.99844 | -0.010825 | 0 | 0
6 | 0.99882 | -0.0082416 | 0 | 0
7 | 0.97706 | -0.16072 | 0.037172 | 0.0093163
8 | 0.97545 | -0.17228 | 0.013219 | 0.003313
9 | 0.97621 | -0.16681 | 0 | 0
10 | 0.97223 | -0.19539 | 0.003384 | 0.00084811
11 | 0.99683 | -0.021995 | 0.0046427 | 0.0011636
12 | 0.99716 | -0.019875 | 0.0018002 | 0.00045116
13 | 0.99703 | -0.020829 | 0.0094701 | 0.0023734
14 | 0.99701 | -0.020942 | 0.0011759 | 0.00029472
15 | 0.97208 | -0.1965 | 0 | 0
16 | 0.9718 | -0.19849 | 0.0066768 | 0.0016734
17 | 0.99531 | -0.032614 | 0.00016602 | 4.1609e-05
18 | 0.99298 | -0.048887 | 0 | 0
19 | 0.99165 | -0.058259 | 0.00093882 | 0.00023529
20 | 0.98594 | -0.098577 | 0.02311 | 0.0057918
21 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.065944 | 0.016612 | -0.065732 | -0.016531 | 0.00021159 | 8.0943e-05 | 0.09947 | 0.09947 | 0.09947 | 0.98678 | -0.091765 | 0.98352 | -0.11478 | 36.8407
1 | -0.078773 | -0.019827 | 0.079795 | 0.020219 | 0.0010228 | 0.00039187 | 0.11882 | 0.11881 | 0.11882 | 0.98678 | -0.091765 | 1 | 0 | 44.0056
2 | 0.060913 | 0.015323 | -0.060773 | -0.01527 | 0.00013922 | 5.3213e-05 | 0.092178 | 0.092178 | 0.092178 | 0.98352 | -0.11478 | 0.9812 | -0.13121 | 34.1402
3 | 0.0059183 | 0.0014823 | -0.0059116 | -0.0014816 | 6.7647e-06 | 7.7012e-07 | 0.0088062 | 0.0088069 | 0.0088069 | 1 | 0 | 0.99882 | -0.0082663 | 3.2618
4 | 0.029199 | 0.0073588 | -0.029155 | -0.0073423 | 4.418e-05 | 1.6501e-05 | 0.043463 | 0.043464 | 0.043464 | 1 | 0 | 0.99844 | -0.010825 | 16.0976
5 | 0.012482 | 0.0031307 | -0.012468 | -0.0031261 | 1.4251e-05 | 4.6137e-06 | 0.018574 | 0.018574 | 0.018574 | 1 | 0 | 0.99882 | -0.0082416 | 6.8794
6 | 0.060773 | 0.01527 | -0.060525 | -0.015175 | 0.00024848 | 9.4981e-05 | 0.092178 | 0.092179 | 0.092179 | 0.9812 | -0.13121 | 0.97706 | -0.16072 | 34.1402
7 | 0.029155 | 0.0073423 | -0.02911 | -0.0073253 | 4.5451e-05 | 1.6978e-05 | 0.043464 | 0.043464 | 0.043464 | 0.99844 | -0.010825 | 0.99683 | -0.021995 | 16.0977
8 | 0.012468 | 0.0031261 | -0.012448 | -0.0031196 | 2.0072e-05 | 6.5016e-06 | 0.018574 | 0.018575 | 0.018575 | 0.99882 | -0.0082416 | 0.99716 | -0.019875 | 6.8796
9 | 0.023353 | 0.0058586 | -0.023333 | -0.0058513 | 1.9735e-05 | 7.2774e-06 | 0.035567 | 0.035567 | 0.035567 | 0.97706 | -0.16072 | 0.97621 | -0.16681 | 13.1729
10 | -0.023315 | -0.0058448 | 0.023333 | 0.0058513 | 1.767e-05 | 6.5164e-06 | 0.035567 | 0.035567 | 0.035567 | 0.97545 | -0.17228 | 0.97621 | -0.16681 | 13.173
11 | 0.010096 | 0.0025317 | -0.010064 | -0.002522 | 3.2269e-05 | 9.6989e-06 | 0.015402 | 0.015403 | 0.015403 | 0.97545 | -0.17228 | 0.97223 | -0.19539 | 5.7046
12 | 0.0066797 | 0.0016739 | -0.0066786 | -0.0016737 | 1.0215e-06 | 1.9869e-07 | 0.010223 | 0.010223 | 0.010223 | 0.97223 | -0.19539 | 0.97208 | -0.1965 | 3.7864
13 | 0.024467 | 0.0061617 | -0.024431 | -0.0061483 | 3.6267e-05 | 1.3382e-05 | 0.036533 | 0.036534 | 0.036534 | 0.99683 | -0.021995 | 0.99531 | -0.032614 | 13.5309
14 | 0.010647 | 0.0026684 | -0.010646 | -0.002668 | 1.4061e-06 | 4.2437e-07 | 0.015889 | 0.015889 | 0.015889 | 0.99716 | -0.019875 | 0.99703 | -0.020829 | 5.8847
15 | 0.001176 | 0.0002946 | -0.0011759 | -0.00029472 | 1.8468e-08 | -1.1821e-07 | 0.001755 | 0.0017551 | 0.0017551 | 0.99703 | -0.020829 | 0.99701 | -0.020942 | 0.65002
16 | 0.0066786 | 0.0016737 | -0.0066768 | -0.0016734 | 1.8447e-06 | 3.5896e-07 | 0.010223 | 0.010223 | 0.010223 | 0.97208 | -0.1965 | 0.9718 | -0.19849 | 3.7865
17 | 0.024265 | 0.0061067 | -0.02421 | -0.0060864 | 5.5e-05 | 2.0286e-05 | 0.036285 | 0.036286 | 0.036286 | 0.99531 | -0.032614 | 0.99298 | -0.048887 | 13.4391
18 | 0.02421 | 0.0060864 | -0.024178 | -0.0060748 | 3.1567e-05 | 1.1645e-05 | 0.036286 | 0.036286 | 0.036286 | 0.99298 | -0.048887 | 0.99165 | -0.058259 | 13.4392
19 | 0.023239 | 0.0058395 | -0.02311 | -0.0057918 | 0.00012969 | 4.7688e-05 | 0.034877 | 0.034878 | 0.034878 | 0.99165 | -0.058259 | 0.98594 | -0.098577 | 12.9177

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12819 | 0.032191

## res_load
| p_mw | q_mvar
0 | 0.012829 | 0.0032153
1 | 0.0048194 | 0.0012079
2 | 0.0059116 | 0.0014816
3 | 0.037172 | 0.0093163
4 | 0.013219 | 0.003313
5 | 0.003384 | 0.00084811
6 | 0.0046427 | 0.0011636
7 | 0.0018002 | 0.00045116
8 | 0.0094701 | 0.0023734
9 | 0.0011759 | 0.00029472
10 | 0.0066768 | 0.0016734
11 | 0.00016602 | 4.1609e-05
12 | 0.00093882 | 0.00023529
13 | 0.02311 | 0.0057918

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1