## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-16_1_4_node_51 | 0.4 | n |  | TRUE
1 | bus_LV_1010-16_1_4_node_138 | 0.4 | n |  | TRUE
2 | bus_LV_1010-16_1_4_node_163 | 0.4 | n |  | TRUE
3 | bus_LV_1010-16_1_4_node_49 | 0.4 | n |  | TRUE
4 | bus_LV_1010-16_1_4_node_52 | 0.4 | n |  | TRUE
5 | bus_LV_1010-16_1_4_node_155 | 0.4 | n |  | TRUE
6 | bus_LV_1010-16_1_4_node_156 | 0.4 | n |  | TRUE
7 | bus_LV_1010-16_1_4_node_131 | 0.4 | n |  | TRUE
8 | bus_LV_1010-16_1_4_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_1010-16_1_4_node_132 | 0.4 | n |  | TRUE
10 | bus_LV_1010-16_1_4_node_122 | 0.4 | n |  | TRUE
11 | bus_LV_1010-16_1_4_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_1010-16_1_4_node_102 | 0.4 | n |  | TRUE
13 | bus_LV_1010-16_1_4_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_1010-16_1_4_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_1010-16_1_4_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_1010-16_1_4_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_1010-16_1_4_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_1010-16_1_4_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_1010-16_1_4_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_1010-16_1_4_node_115 | 0.4 | n |  | TRUE
21 | bus_LV_1010-16_1_4_node_172 | 0.4 | n |  | TRUE
22 | bus_LV_1010-16_1_4_node_170 | 0.4 | n |  | TRUE
23 | bus_LV_1010-16_1_4_node_84 | 0.4 | n |  | TRUE
24 | bus_LV_1010-16_1_4_node_82 | 0.4 | n |  | TRUE
25 | bus_LV_1010-16_1_4_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_1010-16_1_4_node_113 | 0.4 | n |  | TRUE
27 | bus_LV_1010-16_1_4_node_97 | 0.4 | n |  | TRUE
28 | bus_LV_1010-16_1_4_node_161 | 0.4 | n |  | TRUE
29 | bus_LV_1010-16_1_4_node_86 | 0.4 | n |  | TRUE
30 | bus_LV_1010-16_1_4_node_160 | 0.4 | n |  | TRUE
31 | bus_LV_1010-16_1_4_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_1010-16_1_4_node_159 | 0.4 | n |  | TRUE
33 | bus_LV_1010-16_1_4_node_111 | 0.4 | n |  | TRUE
34 | bus_LV_1010-16_1_4_node_162 | 0.4 | n |  | TRUE
35 | bus_LV_1010-16_1_4_node_192 | 0.4 | n |  | TRUE
36 | bus_LV_1010-16_1_4_node_109 | 0.4 | n |  | TRUE
37 | bus_LV_1010-16_1_4_node_110 | 0.4 | n |  | TRUE
38 | bus_LV_1010-16_1_4_node_87 | 0.4 | n |  | TRUE
39 | bus_LV_1010-16_1_4_node_55 | 0.4 | n |  | TRUE
40 | bus_LV_1010-16_1_4_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_1010-16_1_4_node_57 | 0.4 | n |  | TRUE
42 | bus_LV_1010-16_1_4_node_58 | 0.4 | n |  | TRUE
43 | bus_LV_1010-16_1_4_node_59 | 0.4 | n |  | TRUE
44 | bus_LV_1010-16_1_4_node_127 | 0.4 | n |  | TRUE
45 | bus_LV_1010-16_1_4_node_81 | 0.4 | n |  | TRUE
46 | bus_LV_1010-16_1_4_node_60 | 0.4 | n |  | TRUE
47 | bus_LV_1010-16_1_4_node_62 | 0.4 | n |  | TRUE
48 | bus_LV_1010-16_1_4_node_63 | 0.4 | n |  | TRUE
49 | bus_LV_1010-16_1_4_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_1010-16_1_4_node_65 | 0.4 | n |  | TRUE
51 | bus_LV_1010-16_1_4_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_1010-16_1_4_node_168 | 0.4 | n |  | TRUE
53 | bus_LV_1010-16_1_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_1010-16_1_4_node_166 | 0.4 | n |  | TRUE
55 | bus_LV_1010-16_1_4_node_146 | 0.4 | n |  | TRUE
56 | bus_LV_1010-16_1_4_node_145 | 0.4 | n |  | TRUE
57 | bus_LV_1010-16_1_4_node_173 | 0.4 | n |  | TRUE
58 | bus_LV_1010-16_1_4_node_66 | 0.4 | n |  | TRUE
59 | bus_LV_1010-16_1_4_node_153 | 0.4 | n |  | TRUE
60 | bus_LV_1010-16_1_4_node_150 | 0.4 | n |  | TRUE
61 | bus_LV_1010-16_1_4_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_1010-16_1_4_node_124 | 0.4 | n |  | TRUE
63 | bus_LV_1010-16_1_4_node_139 | 0.4 | n |  | TRUE
64 | bus_LV_1010-16_1_4_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_1010-16_1_4_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_1010-16_1_4_node_69 | 0.4 | n |  | TRUE
67 | bus_LV_1010-16_1_4_node_137 | 0.4 | n |  | TRUE
68 | bus_LV_1010-16_1_4_node_171 | 0.4 | n |  | TRUE
69 | bus_LV_1010-16_1_4_node_142 | 0.4 | n |  | TRUE
70 | bus_LV_1010-16_1_4_node_128 | 0.4 | n |  | TRUE
71 | bus_LV_1010-16_1_4_node_130 | 0.4 | n |  | TRUE
72 | bus_LV_1010-16_1_4_node_140 | 0.4 | n |  | TRUE
73 | bus_LV_1010-16_1_4_node_79 | 0.4 | n |  | TRUE
74 | bus_LV_1010-16_1_4_node_133 | 0.4 | n |  | TRUE
75 | bus_LV_1010-16_1_4_node_148 | 0.4 | n |  | TRUE
76 | bus_LV_1010-16_1_4_node_154 | 0.4 | n |  | TRUE
77 | bus_LV_1010-16_1_4_node_167 | 0.4 | n |  | TRUE
78 | bus_LV_1010-16_1_4_node_144 | 0.4 | n |  | TRUE
79 | bus_LV_1010-16_1_4_node_164 | 0.4 | n |  | TRUE
80 | bus_LV_1010-16_1_4_node_143 | 0.4 | n |  | TRUE
81 | bus_LV_1010-16_1_4_node_152 | 0.4 | n |  | TRUE
82 | bus_LV_1010-16_1_4_node_151 | 0.4 | n |  | TRUE
83 | bus_LV_1010-16_1_4_node_157 | 0.4 | n |  | TRUE
84 | bus_LV_1010-16_1_4_node_125 | 0.4 | n |  | TRUE
85 | bus_LV_1010-16_1_4_node_126 | 0.4 | n |  | TRUE
86 | bus_LV_1010-16_1_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_1010-16_1_4_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_1010-16_1_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_1010-16_1_4_node_107 | 0.4 | n |  | TRUE
90 | bus_LV_1010-16_1_4_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_1010-16_1_4_node_95 | 0.4 | n |  | TRUE
92 | bus_LV_1010-16_1_4_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_1010-16_1_4_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_1010-16_1_4_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_1010-16_1_4_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_1010-16_1_4_node_120 | 0.4 | n |  | TRUE
97 | bus_LV_1010-16_1_4_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_1010-16_1_4_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_1010-16_1_4_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_1010-16_1_4_node_106 | 0.4 | n |  | TRUE
101 | bus_LV_1010-16_1_4_node_149 | 0.4 | n |  | TRUE
102 | bus_LV_1010-16_1_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_1010-16_1_4_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_1010-16_1_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_1010-16_1_4_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_1010-16_1_4_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_1010-16_1_4_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_1010-16_1_4_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_1010-16_1_4_node_92 | 0.4 | n |  | TRUE
110 | bus_LV_1010-16_1_4_node_119 | 0.4 | n |  | TRUE
111 | bus_LV_1010-16_1_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_1010-16_1_4_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_1010-16_1_4_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_1010-16_1_4_node_121 | 0.4 | n |  | TRUE
115 | bus_LV_1010-16_1_4_node_104 | 0.4 | n |  | TRUE
116 | bus_LV_1010-16_1_4_node_147 | 0.4 | n |  | TRUE
117 | bus_LV_1010-16_1_4_node_134 | 0.4 | n |  | TRUE
118 | bus_LV_1010-16_1_4_node_135 | 0.4 | n |  | TRUE
119 | bus_LV_1010-16_1_4_node_158 | 0.4 | n |  | TRUE
120 | bus_LV_1010-16_1_4_node_129 | 0.4 | n |  | TRUE
121 | bus_LV_1010-16_1_4_node_141 | 0.4 | n |  | TRUE
122 | bus_LV_1010-16_1_4_node_136 | 0.4 | n |  | TRUE
123 | bus_LV_1010-16_1_4_node_165 | 0.4 | n |  | TRUE
124 | bus_LV_1010-16_1_4_node_169 | 0.4 | n |  | TRUE
125 | bus_MV_126_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-16_1_4_load_138 | 1 | 0.0054565 | 0.0013675 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-16_1_4_load_163 | 2 | 0.0036464 | 0.00091387 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-16_1_4_load_156 | 6 | 0.0031682 | 0.00079404 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-16_1_4_load_131 | 7 | 0.0030372 | 0.00076118 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-16_1_4_load_132 | 9 | 0.002576 | 0.00064561 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-16_1_4_load_122 | 10 | 0.0032567 | 0.00081621 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-16_1_4_load_76 | 11 | 0.0069135 | 0.0017327 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-16_1_4_load_48 | 14 | 0.0010933 | 0.00027401 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-16_1_4_load_45 | 15 | 0.00063707 | 0.00015966 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-16_1_4_load_54 | 17 | 0.00069107 | 0.0001732 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-16_1_4_load_75 | 18 | 0.0018807 | 0.00047135 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-16_1_4_load_74 | 19 | 0.001524 | 0.00038196 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-16_1_4_load_172 | 21 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-16_1_4_load_170 | 22 | 0.0044783 | 0.0011224 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-16_1_4_load_84 | 23 | 0.0020585 | 0.0005159 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-16_1_4_load_82 | 24 | 0.0017777 | 0.00044552 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-16_1_4_load_97 | 27 | 0.0020746 | 0.00051993 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-16_1_4_load_161 | 28 | 0.0013974 | 0.00035022 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-16_1_4_load_86 | 29 | 0.00049105 | 0.00012307 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-16_1_4_load_160 | 30 | 0.0010138 | 0.00025408 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-16_1_4_load_101 | 31 | 0.0033091 | 0.00082933 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1010-16_1_4_load_159 | 32 | 0.0018586 | 0.00046582 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1010-16_1_4_load_162 | 34 | 0.0033305 | 0.0008347 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1010-16_1_4_load_192 | 35 | 0.0012608 | 0.00031599 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1010-16_1_4_load_109 | 36 | 0.0061554 | 0.0015427 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1010-16_1_4_load_87 | 38 | 0.00046666 | 0.00011696 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1010-16_1_4_load_55 | 39 | 8.8643e-05 | 2.2216e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1010-16_1_4_load_56 | 40 | 0.00016378 | 4.1047e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1010-16_1_4_load_127 | 44 | 9.9278e-05 | 2.4881e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1010-16_1_4_load_81 | 45 | 0.00012391 | 3.1054e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1010-16_1_4_load_168 | 52 | 0.001958 | 0.00049073 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1010-16_1_4_load_166 | 54 | 0.0023316 | 0.00058436 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1010-16_1_4_load_146 | 55 | 0.0041752 | 0.0010464 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1010-16_1_4_load_145 | 56 | 0.0039852 | 0.00099878 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1010-16_1_4_load_173 | 57 | 0.00163 | 0.00040852 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1010-16_1_4_load_153 | 59 | 0.00014634 | 3.6676e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1010-16_1_4_load_150 | 60 | 0.0004325 | 0.0001084 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1010-16_1_4_load_139 | 63 | 0.0029612 | 0.00074214 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1010-16_1_4_load_123 | 65 | 0.0024418 | 0.00061198 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1010-16_1_4_load_171 | 68 | 0.0068137 | 0.0017077 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1010-16_1_4_load_142 | 69 | 0.0096736 | 0.0024244 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1010-16_1_4_load_130 | 71 | 0.00025783 | 6.4618e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1010-16_1_4_load_140 | 72 | 0.00022554 | 5.6526e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1010-16_1_4_load_79 | 73 | 3.3972e-05 | 8.5142e-06 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1010-16_1_4_load_148 | 75 | 0.0031833 | 0.0007978 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1010-16_1_4_load_154 | 76 | 0.0030744 | 0.00077052 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1010-16_1_4_load_167 | 77 | 0.0021325 | 0.00053445 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1010-16_1_4_load_164 | 79 | 0.0010721 | 0.0002687 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1010-16_1_4_load_143 | 80 | 0.020238 | 0.0050721 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1010-16_1_4_load_152 | 81 | 0.00020038 | 5.0221e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1010-16_1_4_load_151 | 82 | 0.00018334 | 4.595e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1010-16_1_4_load_157 | 83 | 0.0018848 | 0.00047238 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1010-16_1_4_load_125 | 84 | 0.00039132 | 9.8074e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1010-16_1_4_load_126 | 85 | 0.0018358 | 0.00046008 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1010-16_1_4_load_71 | 86 | 0.00090179 | 0.00022601 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1010-16_1_4_load_72 | 87 | 0.00030201 | 7.5691e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1010-16_1_4_load_108 | 90 | 0.00038646 | 9.6856e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1010-16_1_4_load_95 | 91 | 0.00097918 | 0.0002454 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1010-16_1_4_load_77 | 92 | 0.00010185 | 2.5527e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1010-16_1_4_load_78 | 93 | 5.2518e-05 | 1.3162e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1010-16_1_4_load_80 | 94 | 0.00014728 | 3.6912e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1010-16_1_4_load_116 | 95 | 0.00014325 | 3.5901e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1010-16_1_4_load_120 | 96 | 0.00058291 | 0.00014609 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1010-16_1_4_load_83 | 97 | 0.0018989 | 0.0004759 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1010-16_1_4_load_106 | 100 | 0.0026662 | 0.0006682 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1010-16_1_4_load_149 | 101 | 0.0019003 | 0.00047625 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1010-16_1_4_load_94 | 104 | 0.00091895 | 0.00023031 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1010-16_1_4_load_88 | 105 | 0.00053927 | 0.00013515 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1010-16_1_4_load_89 | 106 | 0.00083707 | 0.00020979 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1010-16_1_4_load_90 | 107 | 0.00016944 | 4.2465e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1010-16_1_4_load_91 | 108 | 0.00025211 | 6.3184e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1010-16_1_4_load_92 | 109 | 0.00014402 | 3.6095e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1010-16_1_4_load_119 | 110 | 0.00014183 | 3.5547e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1010-16_1_4_load_100 | 112 | 0.00086277 | 0.00021623 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1010-16_1_4_load_96 | 113 | 0.0016784 | 0.00042066 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1010-16_1_4_load_121 | 114 | 0.006754 | 0.0016927 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1010-16_1_4_load_104 | 115 | 0.0043992 | 0.0011025 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1010-16_1_4_load_147 | 116 | 0.0011729 | 0.00029396 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1010-16_1_4_load_134 | 117 | 0.0052644 | 0.0013194 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1010-16_1_4_load_135 | 118 | 0.0039796 | 0.00099739 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1010-16_1_4_load_158 | 119 | 0.0017078 | 0.00042802 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1010-16_1_4_load_129 | 120 | 6.2134e-05 | 1.5572e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1010-16_1_4_load_141 | 121 | 0.00024257 | 6.0793e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1010-16_1_4_load_165 | 123 | 0.0028142 | 0.0007053 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1010-16_1_4_load_169 | 124 | 0.00088811 | 0.00022258 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 46 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-16_1_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1010-16_1_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.011266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1010-16_1_4_line_2 | NAYY 4x150 SE | 0 | 3 | 0.007433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1010-16_1_4_line_3 | NAYY 4x150 SE | 1 | 33 | 0.025427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1010-16_1_4_line_4 | NAYY 4x150 SE | 2 | 34 | 0.023305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-16_1_4_line_5 | NAYY 4x150 SE | 3 | 11 | 0.054797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1010-16_1_4_line_6 | NAYY 4x150 SE | 3 | 12 | 0.011681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1010-16_1_4_line_7 | NAYY 4x150 SE | 4 | 5 | 0.019733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1010-16_1_4_line_8 | NAYY 4x150 SE | 4 | 6 | 0.014836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1010-16_1_4_line_9 | NAYY 4x150 SE | 4 | 7 | 0.023721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1010-16_1_4_line_10 | NAYY 4x150 SE | 5 | 35 | 0.019688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1010-16_1_4_line_11 | NAYY 4x150 SE | 6 | 34 | 0.03494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1010-16_1_4_line_12 | NAYY 4x150 SE | 7 | 8 | 0.012157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-16_1_4_line_13 | NAYY 4x150 SE | 8 | 9 | 0.040867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1010-16_1_4_line_14 | NAYY 4x150 SE | 8 | 10 | 0.01823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1010-16_1_4_line_15 | NAYY 4x150 SE | 9 | 32 | 0.022506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1010-16_1_4_line_16 | NAYY 4x150 SE | 11 | 19 | 0.03797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1010-16_1_4_line_17 | NAYY 4x150 SE | 12 | 31 | 0.033414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1010-16_1_4_line_18 | NAYY 4x150 SE | 13 | 14 | 0.02908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1010-16_1_4_line_19 | NAYY 4x150 SE | 13 | 15 | 0.031799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1010-16_1_4_line_20 | NAYY 4x150 SE | 14 | 28 | 0.024686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1010-16_1_4_line_21 | NAYY 4x150 SE | 15 | 16 | 0.013324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-16_1_4_line_22 | NAYY 4x150 SE | 16 | 17 | 0.047031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-16_1_4_line_23 | NAYY 4x150 SE | 17 | 29 | 0.0069579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-16_1_4_line_24 | NAYY 4x150 SE | 18 | 19 | 0.041471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1010-16_1_4_line_25 | NAYY 4x150 SE | 20 | 21 | 0.01622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-16_1_4_line_26 | NAYY 4x150 SE | 20 | 22 | 0.022379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1010-16_1_4_line_27 | NAYY 4x150 SE | 22 | 26 | 0.017387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1010-16_1_4_line_28 | NAYY 4x150 SE | 23 | 24 | 0.02016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1010-16_1_4_line_29 | NAYY 4x150 SE | 24 | 97 | 0.010195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1010-16_1_4_line_30 | NAYY 4x150 SE | 25 | 26 | 0.020584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1010-16_1_4_line_31 | NAYY 4x150 SE | 25 | 27 | 0.019207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1010-16_1_4_line_32 | NAYY 4x150 SE | 26 | 79 | 0.023192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1010-16_1_4_line_33 | NAYY 4x150 SE | 27 | 113 | 0.073337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1010-16_1_4_line_34 | NAYY 4x150 SE | 28 | 30 | 0.003016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1010-16_1_4_line_35 | NAYY 4x150 SE | 29 | 38 | 0.029093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1010-16_1_4_line_36 | NAYY 4x150 SE | 30 | 32 | 0.018669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1010-16_1_4_line_37 | NAYY 4x150 SE | 31 | 102 | 0.016897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1010-16_1_4_line_38 | NAYY 4x150 SE | 33 | 117 | 0.010351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1010-16_1_4_line_39 | NAYY 4x150 SE | 33 | 37 | 0.002384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1010-16_1_4_line_40 | NAYY 4x150 SE | 33 | 67 | 0.022215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1010-16_1_4_line_41 | NAYY 4x150 SE | 36 | 37 | 0.013683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1010-16_1_4_line_42 | NAYY 4x150 SE | 38 | 103 | 0.025691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1010-16_1_4_line_43 | NAYY 4x150 SE | 39 | 40 | 0.034413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1010-16_1_4_line_44 | NAYY 4x150 SE | 39 | 41 | 0.013921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1010-16_1_4_line_45 | NAYY 4x150 SE | 41 | 42 | 0.14347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1010-16_1_4_line_46 | NAYY 4x150 SE | 41 | 43 | 0.076297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1010-16_1_4_line_47 | NAYY 4x150 SE | 42 | 44 | 0.028752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1010-16_1_4_line_48 | NAYY 4x150 SE | 43 | 45 | 0.013926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1010-16_1_4_line_49 | NAYY 4x150 SE | 44 | 70 | 0.011111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1010-16_1_4_line_50 | NAYY 4x150 SE | 45 | 73 | 0.027867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1010-16_1_4_line_51 | NAYY 4x150 SE | 46 | 47 | 0.13584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_1010-16_1_4_line_52 | NAYY 4x150 SE | 46 | 48 | 0.015056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1010-16_1_4_line_53 | NAYY 4x150 SE | 47 | 53 | 0.095032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1010-16_1_4_line_54 | NAYY 4x150 SE | 47 | 54 | 0.053099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1010-16_1_4_line_55 | NAYY 4x150 SE | 48 | 55 | 0.020814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1010-16_1_4_line_56 | NAYY 4x150 SE | 48 | 56 | 0.012375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_1010-16_1_4_line_57 | NAYY 4x150 SE | 49 | 50 | 0.0080095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1010-16_1_4_line_58 | NAYY 4x150 SE | 49 | 51 | 0.014964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1010-16_1_4_line_59 | NAYY 4x150 SE | 49 | 52 | 0.0053828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1010-16_1_4_line_60 | NAYY 4x150 SE | 50 | 57 | 0.022534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1010-16_1_4_line_61 | NAYY 4x150 SE | 51 | 54 | 0.013577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1010-16_1_4_line_62 | NAYY 4x150 SE | 52 | 77 | 0.026402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1010-16_1_4_line_63 | NAYY 4x150 SE | 53 | 69 | 0.034377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1010-16_1_4_line_64 | NAYY 4x150 SE | 56 | 67 | 0.0077282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
65 | LV_1010-16_1_4_line_65 | NAYY 4x150 SE | 57 | 81 | 0.04137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1010-16_1_4_line_66 | NAYY 4x150 SE | 58 | 59 | 0.040219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1010-16_1_4_line_67 | NAYY 4x150 SE | 58 | 60 | 0.012055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1010-16_1_4_line_68 | NAYY 4x150 SE | 60 | 82 | 0.029426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1010-16_1_4_line_69 | NAYY 4x150 SE | 61 | 62 | 0.017637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1010-16_1_4_line_70 | NAYY 4x150 SE | 61 | 63 | 0.0027634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1010-16_1_4_line_71 | NAYY 4x150 SE | 62 | 83 | 0.010787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1010-16_1_4_line_72 | NAYY 4x150 SE | 62 | 64 | 0.037406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1010-16_1_4_line_73 | NAYY 4x150 SE | 64 | 65 | 0.089823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1010-16_1_4_line_74 | NAYY 4x150 SE | 66 | 67 | 0.004512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1010-16_1_4_line_75 | NAYY 4x150 SE | 66 | 68 | 0.012287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1010-16_1_4_line_76 | NAYY 4x150 SE | 69 | 80 | 0.031734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1010-16_1_4_line_77 | NAYY 4x150 SE | 70 | 120 | 0.018211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1010-16_1_4_line_78 | NAYY 4x150 SE | 71 | 72 | 0.028956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1010-16_1_4_line_79 | NAYY 4x150 SE | 72 | 121 | 0.017772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1010-16_1_4_line_80 | NAYY 4x150 SE | 73 | 92 | 0.011261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1010-16_1_4_line_81 | NAYY 4x150 SE | 74 | 75 | 0.0084909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1010-16_1_4_line_82 | NAYY 4x150 SE | 74 | 76 | 0.03412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1010-16_1_4_line_83 | NAYY 4x150 SE | 75 | 116 | 0.0043442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1010-16_1_4_line_84 | NAYY 4x150 SE | 77 | 124 | 0.011312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1010-16_1_4_line_85 | NAYY 4x150 SE | 78 | 79 | 0.019014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1010-16_1_4_line_86 | NAYY 4x150 SE | 78 | 80 | 0.036239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1010-16_1_4_line_87 | NAYY 4x150 SE | 81 | 82 | 0.0050248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1010-16_1_4_line_88 | NAYY 4x150 SE | 83 | 119 | 0.0091065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1010-16_1_4_line_89 | NAYY 4x150 SE | 84 | 85 | 0.00039711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1010-16_1_4_line_90 | NAYY 4x150 SE | 85 | 90 | 0.009514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1010-16_1_4_line_91 | NAYY 4x150 SE | 86 | 87 | 0.044724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1010-16_1_4_line_92 | NAYY 4x150 SE | 87 | 88 | 0.043329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1010-16_1_4_line_93 | NAYY 4x150 SE | 88 | 89 | 0.0048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1010-16_1_4_line_94 | NAYY 4x150 SE | 88 | 90 | 0.017435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1010-16_1_4_line_95 | NAYY 4x150 SE | 89 | 91 | 0.015221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1010-16_1_4_line_96 | NAYY 4x150 SE | 91 | 103 | 0.010058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1010-16_1_4_line_97 | NAYY 4x150 SE | 92 | 93 | 0.018006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1010-16_1_4_line_98 | NAYY 4x150 SE | 93 | 94 | 0.025587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1010-16_1_4_line_99 | NAYY 4x150 SE | 94 | 95 | 0.017925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1010-16_1_4_line_100 | NAYY 4x150 SE | 95 | 96 | 0.00085434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1010-16_1_4_line_101 | NAYY 4x150 SE | 96 | 109 | 0.005232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1010-16_1_4_line_102 | NAYY 4x150 SE | 97 | 98 | 0.0073906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1010-16_1_4_line_103 | NAYY 4x150 SE | 98 | 99 | 0.001779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1010-16_1_4_line_104 | NAYY 4x150 SE | 98 | 100 | 0.03239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1010-16_1_4_line_105 | NAYY 4x150 SE | 99 | 101 | 0.016592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1010-16_1_4_line_106 | NAYY 4x150 SE | 99 | 102 | 0.00693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1010-16_1_4_line_107 | NAYY 4x150 SE | 101 | 116 | 0.012531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1010-16_1_4_line_108 | NAYY 4x150 SE | 102 | 115 | 0.0083973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1010-16_1_4_line_109 | NAYY 4x150 SE | 103 | 104 | 0.018097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1010-16_1_4_line_110 | NAYY 4x150 SE | 105 | 106 | 0.0039048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1010-16_1_4_line_111 | NAYY 4x150 SE | 105 | 107 | 0.046602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1010-16_1_4_line_112 | NAYY 4x150 SE | 106 | 108 | 0.026393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1010-16_1_4_line_113 | NAYY 4x150 SE | 107 | 109 | 0.01429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1010-16_1_4_line_114 | NAYY 4x150 SE | 108 | 110 | 0.094154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1010-16_1_4_line_115 | NAYY 4x150 SE | 108 | 111 | 0.12688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1010-16_1_4_line_116 | NAYY 4x150 SE | 111 | 112 | 0.020896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1010-16_1_4_line_117 | NAYY 4x150 SE | 111 | 113 | 0.018201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1010-16_1_4_line_118 | NAYY 4x150 SE | 112 | 114 | 0.040621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1010-16_1_4_line_119 | NAYY 4x150 SE | 117 | 118 | 0.0089096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1010-16_1_4_line_120 | NAYY 4x150 SE | 118 | 122 | 0.012105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1010-16_1_4_line_121 | NAYY 4x150 SE | 119 | 122 | 0.014585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1010-16_1_4_line_122 | NAYY 4x150 SE | 121 | 124 | 0.012506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1010-16_1_4_line_123 | NAYY 4x150 SE | 122 | 123 | 0.022562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-16_1_4_trafo_60 | 0.25 MVA 20/0.4 kV | 125 | 46 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2635149.9351 | 1189263.0454 | 2635157.0305 | 1189275.5827 | 2635162.761 | 1189285.9863
1 | 2635149.9351 | 1189263.0454 | 2635144.13 | 1189253.3905
2 | 2635149.9351 | 1189263.0454 | 2635153.1872 | 1189261.208 | 2635156.4086 | 1189259.3925
3 | 2635175.0129 | 1189308.2168 | 2635172.1543 | 1189304.0978 | 2635168.9609 | 1189297.2421 | 2635162.761 | 1189285.9863
4 | 2635131.3102 | 1189233.9328 | 2635134.9363 | 1189239.1891 | 2635143.0997 | 1189251.677 | 2635144.13 | 1189253.3905
5 | 2635156.4086 | 1189259.3925 | 2635151.7582 | 1189251.2831 | 2635144.6405 | 1189239.9353 | 2635134.4684 | 1189225.3345 | 2635128.358 | 1189216.4828 | 2635126.3666 | 1189213.6011
6 | 2635162.2215 | 1189269.5321 | 2635159.8814 | 1189265.4273 | 2635156.4086 | 1189259.3925
7 | 2635102.7088 | 1189193.1978 | 2635093.3591 | 1189198.3236 | 2635086.3218 | 1189201.8621 | 2635085.1078 | 1189202.0996
8 | 2635102.7088 | 1189193.1978 | 2635107.5662 | 1189199.8409 | 2635111.3923 | 1189205.2266
9 | 2635102.7088 | 1189193.1978 | 2635099.0167 | 1189188.1401 | 2635089.0973 | 1189173.7724
10 | 2635065.7866 | 1189200.0076 | 2635075.0173 | 1189202.1739 | 2635080.0075 | 1189203.0702 | 2635085.1078 | 1189202.0996
11 | 2635111.3923 | 1189205.2266 | 2635115.0926 | 1189210.4352 | 2635117.4748 | 1189213.8843 | 2635126.9127 | 1189227.5581 | 2635131.3102 | 1189233.9328
12 | 2635082.1518 | 1189163.795 | 2635084.837 | 1189167.6016 | 2635089.0973 | 1189173.7724
13 | 2635082.1518 | 1189163.795 | 2635073.5666 | 1189151.6493 | 2635058.1752 | 1189130.7025
14 | 2635082.1518 | 1189163.795 | 2635068.5203 | 1189172.0641 | 2635066.4816 | 1189173.0998
15 | 2635045.1646 | 1189112.3391 | 2635056.527 | 1189128.4594 | 2635058.1752 | 1189130.7025
16 | 2635104.6246 | 1189182.4734 | 2635110.9038 | 1189191.2225 | 2635120.2662 | 1189204.7735 | 2635126.3666 | 1189213.6011
17 | 2635162.2215 | 1189269.5321 | 2635167.6864 | 1189268.8082 | 2635174.7003 | 1189269.2385 | 2635195.354 | 1189272.2626
18 | 2634999.4654 | 1189052.4518 | 2635004.5235 | 1189057.4285 | 2635013.9765 | 1189068.5897 | 2635018.2664 | 1189074.5671
19 | 2634999.4654 | 1189052.4518 | 2634990.5997 | 1189056.9469 | 2634978.0632 | 1189063.1438 | 2634973.7543 | 1189065.7089 | 2634970.9422 | 1189066.2263
20 | 2635032.6224 | 1189094.6497 | 2635022.9261 | 1189081.0598 | 2635018.2664 | 1189074.5671
21 | 2634957.7318 | 1189066.7716 | 2634965.2031 | 1189067.2821 | 2634970.9422 | 1189066.2263
22 | 2634957.7318 | 1189066.7716 | 2634961.8897 | 1189082.2375 | 2634967.8337 | 1189097.4581 | 2634973.706 | 1189107.9647 | 2634974.7892 | 1189110.3718
23 | 2634974.7892 | 1189110.3718 | 2634977.6444 | 1189116.7169
24 | 2635104.6246 | 1189182.4734 | 2635090.7206 | 1189163.1003 | 2635080.5277 | 1189148.7224
25 | 2635386.7645 | 1189483.513 | 2635397.9283 | 1189495.3075
26 | 2635397.9283 | 1189495.3075 | 2635382.2292 | 1189511.256
27 | 2635370.0319 | 1189523.647 | 2635382.2292 | 1189511.256
28 | 2635230.7641 | 1189262.7253 | 2635246.3501 | 1189249.9388
29 | 2635230.7641 | 1189262.7253 | 2635222.8819 | 1189269.1917
30 | 2635370.0319 | 1189523.647 | 2635372.9737 | 1189527.8555 | 2635381.2926 | 1189535.8311 | 2635384.3819 | 1189538.2951
31 | 2635384.3819 | 1189538.2951 | 2635398.4553 | 1189551.3657
32 | 2635370.0319 | 1189523.647 | 2635347.3013 | 1189528.2486
33 | 2635450.9897 | 1189602.5062 | 2635425.8466 | 1189576.8052 | 2635398.4553 | 1189551.3657
34 | 2635032.6224 | 1189094.6497 | 2635034.3741 | 1189097.1048
35 | 2634989.5831 | 1189143.2479 | 2634977.6444 | 1189116.7169
36 | 2635034.3741 | 1189097.1048 | 2635038.7289 | 1189103.2085 | 2635045.1646 | 1189112.3391
37 | 2635210.1141 | 1189278.9738 | 2635208.1611 | 1189276.4832 | 2635202.78 | 1189273.35 | 2635195.354 | 1189272.2626
38 | 2635175.0129 | 1189308.2168 | 2635172.2061 | 1189309.5678 | 2635165.054 | 1189310.6676
39 | 2635177.1621 | 1189307.1733 | 2635175.0129 | 1189308.2168
40 | 2635175.0129 | 1189308.2168 | 2635189.833 | 1189324.8016
41 | 2635177.1621 | 1189307.1733 | 2635172.8097 | 1189298.9767 | 2635170.9009 | 1189295.0101
42 | 2634992.0436 | 1189167.537 | 2634994.7722 | 1189154.7794 | 2634989.5831 | 1189143.2479
43 | 2635145.019 | 1189883.9509 | 2635177.2311 | 1189871.8415
44 | 2635190.5875 | 1189868.899 | 2635185.4638 | 1189868.7466 | 2635177.2311 | 1189871.8415
45 | 2635190.5875 | 1189868.899 | 2635185.5628 | 1189920.7086 | 2635184.6513 | 1189939.58 | 2635184.8966 | 1189956.246 | 2635186.1988 | 1189970.8282 | 2635188.9311 | 1189988.6094 | 2635192.462 | 1190005.4392 | 2635198.2895 | 1190003.8837
46 | 2635190.5875 | 1189868.899 | 2635197.9806 | 1189798.171 | 2635203.1485 | 1189798.5793
47 | 2635198.2895 | 1190003.8837 | 2635214.7713 | 1189999.5003 | 2635226.1197 | 1189996.6655
48 | 2635203.1485 | 1189798.5793 | 2635204.8099 | 1189798.767 | 2635216.9836 | 1189800.1718
49 | 2635237.2153 | 1189996.6084 | 2635231.8484 | 1189996.3434 | 2635226.1197 | 1189996.6655
50 | 2635244.7585 | 1189802.0701 | 2635230.1868 | 1189801.6954 | 2635216.9836 | 1189800.1718
51 | 2635201.9314 | 1189350.2752 | 2635208.4861 | 1189441.8075 | 2635212.1327 | 1189485.7303
52 | 2635193.3482 | 1189344.3772 | 2635197.4157 | 1189343.9231 | 2635197.8105 | 1189350.7291 | 2635201.9314 | 1189350.2752
53 | 2635212.1327 | 1189485.7303 | 2635208.4861 | 1189441.8075 | 2635225.8633 | 1189441.0536 | 2635233.3347 | 1189442.7651 | 2635251.9284 | 1189460.7952
54 | 2635212.1327 | 1189485.7303 | 2635215.9577 | 1189534.3122 | 2635216.3942 | 1189538.657
55 | 2635193.3482 | 1189344.3772 | 2635176.6963 | 1189346.2472 | 2635172.6565 | 1189345.8677
56 | 2635193.3482 | 1189344.3772 | 2635192.6394 | 1189333.9119 | 2635192.2366 | 1189332.0701
57 | 2635211.071 | 1189567.746 | 2635214.9089 | 1189567.4239 | 2635219.052 | 1189567.0703
58 | 2635217.7516 | 1189552.1657 | 2635219.052 | 1189567.0703
59 | 2635219.052 | 1189567.0703 | 2635219.5205 | 1189572.4327
60 | 2635211.071 | 1189567.746 | 2635211.7434 | 1189580.5013 | 2635210.8756 | 1189590.2236
61 | 2635217.7516 | 1189552.1657 | 2635216.3942 | 1189538.657
62 | 2635221.1121 | 1189598.7768 | 2635220.674 | 1189585.6343 | 2635219.5205 | 1189572.4327
63 | 2635251.9284 | 1189460.7952 | 2635258.5511 | 1189465.4478 | 2635278.7866 | 1189482.2206
64 | 2635189.833 | 1189324.8016 | 2635191.1911 | 1189327.2887 | 2635192.2366 | 1189332.0701
65 | 2635210.8756 | 1189590.2236 | 2635210.1515 | 1189598.3348 | 2635210.7529 | 1189605.0086 | 2635212.5493 | 1189614.6577 | 2635212.3109 | 1189627.9857 | 2635211.9774 | 1189631.3497
66 | 2635207.3901 | 1189677.628 | 2635201.4077 | 1189676.948 | 2635191.3746 | 1189676.4667 | 2635187.3255 | 1189677.7102 | 2635185.984 | 1189680.1926 | 2635184.7745 | 1189697.2456
67 | 2635207.3901 | 1189677.628 | 2635208.5792 | 1189665.6321
68 | 2635211.4818 | 1189636.35 | 2635208.5792 | 1189665.6321
69 | 2635112.4647 | 1189330.9179 | 2635109.8289 | 1189313.482
70 | 2635112.4647 | 1189330.9179 | 2635112.8761 | 1189333.6505
71 | 2635109.8289 | 1189313.482 | 2635113.0262 | 1189313.1783 | 2635120.601 | 1189313.2634
72 | 2635073.1759 | 1189321.3272 | 2635074.2448 | 1189321.1222 | 2635083.7024 | 1189319.6879 | 2635091.7739 | 1189317.9231 | 2635109.8289 | 1189313.482
73 | 2635073.1759 | 1189321.3272 | 2635069.0816 | 1189322.4261 | 2635064.3983 | 1189325.1446 | 2635056.5303 | 1189333.8366 | 2635032.6028 | 1189357.8763 | 2635030.0867 | 1189368.2116 | 2635030.1641 | 1189375.8495 | 2635026.1912 | 1189380.9846 | 2635019.533 | 1189386.2596 | 2635018.4712 | 1189386.9462
74 | 2635193.932 | 1189322.8913 | 2635189.833 | 1189324.8016
75 | 2635193.932 | 1189322.8913 | 2635199.4305 | 1189320.3222 | 2635199.9183 | 1189326.5212
76 | 2635278.7866 | 1189482.2206 | 2635279.1104 | 1189482.489 | 2635301.7046 | 1189504.1688
77 | 2635237.2153 | 1189996.6084 | 2635241.8944 | 1189995.8244 | 2635255.111 | 1189992.9895
78 | 2635217.0316 | 1189669.1161 | 2635219.9479 | 1189640.3071
79 | 2635221.0827 | 1189622.5849 | 2635220.8795 | 1189631.1044 | 2635219.9479 | 1189640.3071
80 | 2635244.7585 | 1189802.0701 | 2635248.6844 | 1189802.1711 | 2635255.7398 | 1189800.1681
81 | 2635237.0932 | 1189310.705 | 2635236.0103 | 1189304.2173 | 2635234.922 | 1189302.6435
82 | 2635237.0932 | 1189310.705 | 2635257.3366 | 1189311.5467 | 2635266.6375 | 1189313.4357 | 2635270.6934 | 1189315.0585
83 | 2635232.4512 | 1189299.0704 | 2635234.922 | 1189302.6435
84 | 2635221.1121 | 1189598.7768 | 2635221.426 | 1189608.1953 | 2635221.381 | 1189610.0825
85 | 2635328.5787 | 1189528.3273 | 2635332.1183 | 1189529.4376 | 2635336.4715 | 1189529.6745 | 2635342.392 | 1189529.2425 | 2635347.3013 | 1189528.2486
86 | 2635328.5787 | 1189528.3273 | 2635323.7006 | 1189525.2746 | 2635301.7046 | 1189504.1688
87 | 2635211.4818 | 1189636.35 | 2635211.9774 | 1189631.3497
88 | 2635120.601 | 1189313.2634 | 2635129.5822 | 1189313.3643 | 2635129.7069 | 1189313.3685
89 | 2635010.3394 | 1189213.0736 | 2635010.5153 | 1189213.4296
90 | 2635010.3394 | 1189213.0736 | 2635009.0745 | 1189210.5151 | 2635007.2072 | 1189204.1223
91 | 2634997.6152 | 1189267.0851 | 2634997.6402 | 1189264.3885 | 2634990.0579 | 1189242.4435 | 2634987.3601 | 1189223.8289 | 2634987.3601 | 1189223.8289
92 | 2635004.849 | 1189187.089 | 2634993.1487 | 1189197.7042 | 2634987.8081 | 1189207.1892 | 2634987.3601 | 1189223.8289
93 | 2635009.2156 | 1189185.0689 | 2635004.849 | 1189187.089
94 | 2635004.849 | 1189187.089 | 2635004.4687 | 1189194.7464 | 2635007.2072 | 1189204.1223
95 | 2635009.2156 | 1189185.0689 | 2634997.1742 | 1189175.7587
96 | 2634992.0436 | 1189167.537 | 2634994.2207 | 1189173.4752 | 2634997.1742 | 1189175.7587
97 | 2635255.7398 | 1189800.1681 | 2635272.8148 | 1189795.3205 | 2635273.0275 | 1189795.1774
98 | 2635294.2483 | 1189780.8843 | 2635294.1833 | 1189780.9496 | 2635273.0275 | 1189795.1774
99 | 2635294.2483 | 1189780.8843 | 2635306.8903 | 1189768.1774
100 | 2635307.4929 | 1189767.5718 | 2635306.8903 | 1189768.1774
101 | 2635311.183 | 1189763.8627 | 2635311.183 | 1189763.8627 | 2635307.4929 | 1189767.5718
102 | 2635217.1681 | 1189273.8792 | 2635222.8819 | 1189269.1917
103 | 2635215.8872 | 1189275.1168 | 2635217.1681 | 1189273.8792
104 | 2635217.1681 | 1189273.8792 | 2635213.8521 | 1189264.5436 | 2635216.0825 | 1189242.1719
105 | 2635215.8872 | 1189275.1168 | 2635225.3241 | 1189288.7638
106 | 2635215.8872 | 1189275.1168 | 2635210.1141 | 1189278.9738
107 | 2635225.3241 | 1189288.7638 | 2635232.4512 | 1189299.0704
108 | 2635210.1141 | 1189278.9738 | 2635203.9876 | 1189284.7166
109 | 2634992.0436 | 1189167.537 | 2634975.7307 | 1189159.6042
110 | 2635342.8819 | 1189712.923 | 2635346.0987 | 1189710.7095
111 | 2635342.8819 | 1189712.923 | 2635337.7568 | 1189716.4494 | 2635325.3986 | 1189732.6741 | 2635317.1096 | 1189750.8598
112 | 2635367.8415 | 1189695.749 | 2635346.0987 | 1189710.7095
113 | 2635311.183 | 1189763.8627 | 2635317.1096 | 1189750.8598
114 | 2635367.8415 | 1189695.749 | 2635374.4596 | 1189701.1354 | 2635379.7415 | 1189704.2015 | 2635405.359 | 1189714.236 | 2635412.6095 | 1189718.4033 | 2635416.3041 | 1189721.6602 | 2635439.2621 | 1189744.2302 | 2635444.0891 | 1189748.6111
115 | 2635463.7178 | 1189615.5166 | 2635462.8092 | 1189620.8475 | 2635461.5714 | 1189623.8306 | 2635459.8006 | 1189626.6661 | 2635455.8044 | 1189630.5557 | 2635401.3797 | 1189672.679 | 2635367.8415 | 1189695.749
116 | 2635463.7178 | 1189615.5166 | 2635479.0025 | 1189611.3159 | 2635483.9868 | 1189610.5368
117 | 2635463.7178 | 1189615.5166 | 2635450.9897 | 1189602.5062
118 | 2635483.9868 | 1189610.5368 | 2635505.4515 | 1189607.1814 | 2635515.7922 | 1189604.6635 | 2635523.6637 | 1189602.184
119 | 2635165.054 | 1189310.6676 | 2635156.2479 | 1189312.0219
120 | 2635144.2832 | 1189313.8619 | 2635156.2479 | 1189312.0219
121 | 2635144.2832 | 1189313.8619 | 2635129.7069 | 1189313.3685
122 | 2635221.0827 | 1189622.5849 | 2635221.381 | 1189610.0825
123 | 2635144.2832 | 1189313.8619 | 2635145.735 | 1189331.5799 | 2635146.5894 | 1189334.1418 | 2635148.4293 | 1189335.1198 | 2635148.4293 | 1189335.1198

## bus_geodata
| x | y | coords
0 | 2635149.9351 | 1189263.0454
1 | 2635162.761 | 1189285.9863
2 | 2635144.13 | 1189253.3905
3 | 2635156.4086 | 1189259.3925
4 | 2635102.7088 | 1189193.1978
5 | 2635085.1078 | 1189202.0996
6 | 2635111.3923 | 1189205.2266
7 | 2635089.0973 | 1189173.7724
8 | 2635082.1518 | 1189163.795
9 | 2635058.1752 | 1189130.7025
10 | 2635066.4816 | 1189173.0998
11 | 2635126.3666 | 1189213.6011
12 | 2635162.2215 | 1189269.5321
13 | 2634999.4654 | 1189052.4518
14 | 2635018.2664 | 1189074.5671
15 | 2634970.9422 | 1189066.2263
16 | 2634957.7318 | 1189066.7716
17 | 2634974.7892 | 1189110.3718
18 | 2635080.5277 | 1189148.7224
19 | 2635104.6246 | 1189182.4734
20 | 2635397.9283 | 1189495.3075
21 | 2635386.7645 | 1189483.513
22 | 2635382.2292 | 1189511.256
23 | 2635246.3501 | 1189249.9388
24 | 2635230.7641 | 1189262.7253
25 | 2635384.3819 | 1189538.2951
26 | 2635370.0319 | 1189523.647
27 | 2635398.4553 | 1189551.3657
28 | 2635032.6224 | 1189094.6497
29 | 2634977.6444 | 1189116.7169
30 | 2635034.3741 | 1189097.1048
31 | 2635195.354 | 1189272.2626
32 | 2635045.1646 | 1189112.3391
33 | 2635175.0129 | 1189308.2168
34 | 2635131.3102 | 1189233.9328
35 | 2635065.7866 | 1189200.0076
36 | 2635170.9009 | 1189295.0101
37 | 2635177.1621 | 1189307.1733
38 | 2634989.5831 | 1189143.2479
39 | 2635177.2311 | 1189871.8415
40 | 2635145.019 | 1189883.9509
41 | 2635190.5875 | 1189868.899
42 | 2635198.2895 | 1190003.8837
43 | 2635203.1485 | 1189798.5793
44 | 2635226.1197 | 1189996.6655
45 | 2635216.9836 | 1189800.1718
46 | 2635201.9314 | 1189350.2752
47 | 2635212.1327 | 1189485.7303
48 | 2635193.3482 | 1189344.3772
49 | 2635219.052 | 1189567.0703
50 | 2635211.071 | 1189567.746
51 | 2635217.7516 | 1189552.1657
52 | 2635219.5205 | 1189572.4327
53 | 2635251.9284 | 1189460.7952
54 | 2635216.3942 | 1189538.657
55 | 2635172.6565 | 1189345.8677
56 | 2635192.2366 | 1189332.0701
57 | 2635210.8756 | 1189590.2236
58 | 2635207.3901 | 1189677.628
59 | 2635184.7745 | 1189697.2456
60 | 2635208.5792 | 1189665.6321
61 | 2635112.4647 | 1189330.9179
62 | 2635109.8289 | 1189313.482
63 | 2635112.8761 | 1189333.6505
64 | 2635073.1759 | 1189321.3272
65 | 2635018.4712 | 1189386.9462
66 | 2635193.932 | 1189322.8913
67 | 2635189.833 | 1189324.8016
68 | 2635199.9183 | 1189326.5212
69 | 2635278.7866 | 1189482.2206
70 | 2635237.2153 | 1189996.6084
71 | 2635217.0316 | 1189669.1161
72 | 2635219.9479 | 1189640.3071
73 | 2635244.7585 | 1189802.0701
74 | 2635237.0932 | 1189310.705
75 | 2635234.922 | 1189302.6435
76 | 2635270.6934 | 1189315.0585
77 | 2635221.1121 | 1189598.7768
78 | 2635328.5787 | 1189528.3273
79 | 2635347.3013 | 1189528.2486
80 | 2635301.7046 | 1189504.1688
81 | 2635211.9774 | 1189631.3497
82 | 2635211.4818 | 1189636.35
83 | 2635120.601 | 1189313.2634
84 | 2635010.5153 | 1189213.4296
85 | 2635010.3393 | 1189213.0736
86 | 2634997.6152 | 1189267.0851
87 | 2634987.3601 | 1189223.8289
88 | 2635004.849 | 1189187.089
89 | 2635009.2156 | 1189185.0689
90 | 2635007.2072 | 1189204.1223
91 | 2634997.1742 | 1189175.7587
92 | 2635255.7398 | 1189800.1681
93 | 2635273.0275 | 1189795.1774
94 | 2635294.2483 | 1189780.8843
95 | 2635306.8903 | 1189768.1774
96 | 2635307.4929 | 1189767.5718
97 | 2635222.8819 | 1189269.1917
98 | 2635217.1681 | 1189273.8792
99 | 2635215.8872 | 1189275.1168
100 | 2635216.0825 | 1189242.1719
101 | 2635225.3241 | 1189288.7638
102 | 2635210.1141 | 1189278.9738
103 | 2634992.0436 | 1189167.537
104 | 2634975.7307 | 1189159.6042
105 | 2635342.8819 | 1189712.923
106 | 2635346.0987 | 1189710.7095
107 | 2635317.1097 | 1189750.8598
108 | 2635367.8415 | 1189695.749
109 | 2635311.183 | 1189763.8627
110 | 2635444.0891 | 1189748.6111
111 | 2635463.7178 | 1189615.5166
112 | 2635483.9868 | 1189610.5368
113 | 2635450.9897 | 1189602.5062
114 | 2635523.6637 | 1189602.184
115 | 2635203.9876 | 1189284.7166
116 | 2635232.4512 | 1189299.0704
117 | 2635165.054 | 1189310.6676
118 | 2635156.2479 | 1189312.0219
119 | 2635129.7069 | 1189313.3685
120 | 2635255.111 | 1189992.9895
121 | 2635221.0827 | 1189622.5849
122 | 2635144.2832 | 1189313.8619
123 | 2635148.4293 | 1189335.1198
124 | 2635221.381 | 1189610.0825
125 | 2635197.8105 | 1189350.7291

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98845 | -0.080825 | 0 | 0
1 | 0.99109 | -0.062217 | 0.0054565 | 0.0013675
2 | 0.9879 | -0.084705 | 0.0036464 | 0.00091387
3 | 0.98806 | -0.083544 | 0 | 0
4 | 0.98503 | -0.10505 | 0 | 0
5 | 0.98499 | -0.1053 | 0 | 0
6 | 0.98554 | -0.10145 | 0.0031682 | 0.00079404
7 | 0.98426 | -0.11049 | 0.0030372 | 0.00076118
8 | 0.98393 | -0.1129 | 0 | 0
9 | 0.98298 | -0.11964 | 0.002576 | 0.00064561
10 | 0.98384 | -0.11351 | 0.0032567 | 0.00081621
11 | 0.98725 | -0.089335 | 0.0069135 | 0.0017327
12 | 0.98764 | -0.086586 | 0 | 0
13 | 0.98152 | -0.13006 | 0 | 0
14 | 0.98186 | -0.12764 | 0.0010933 | 0.00027401
15 | 0.98115 | -0.13271 | 0.00063707 | 0.00015966
16 | 0.98101 | -0.13373 | 0 | 0
17 | 0.9805 | -0.13733 | 0.00069107 | 0.0001732
18 | 0.98695 | -0.091461 | 0.0018807 | 0.00047135
19 | 0.98706 | -0.090661 | 0.001524 | 0.00038196
20 | 0.97931 | -0.14545 | 0 | 0
21 | 0.97927 | -0.14573 | 0.0016707 | 0.00041871
22 | 0.97936 | -0.14506 | 0.0044783 | 0.0011224
23 | 0.98549 | -0.10182 | 0.0020585 | 0.0005159
24 | 0.98555 | -0.1014 | 0.0017777 | 0.00044552
25 | 0.97907 | -0.14719 | 0 | 0
26 | 0.97952 | -0.14394 | 0 | 0
27 | 0.97865 | -0.15021 | 0.0020746 | 0.00051993
28 | 0.98218 | -0.12531 | 0.0013974 | 0.00035022
29 | 0.98044 | -0.13782 | 0.00049105 | 0.00012307
30 | 0.98223 | -0.12498 | 0.0010138 | 0.00025408
31 | 0.98641 | -0.0953 | 0.0033091 | 0.00082933
32 | 0.98254 | -0.12275 | 0.0018586 | 0.00046582
33 | 0.99384 | -0.042906 | 0 | 0
34 | 0.98689 | -0.091875 | 0.0033305 | 0.0008347
35 | 0.98496 | -0.10556 | 0.0012608 | 0.00031599
36 | 0.9937 | -0.043905 | 0.0061554 | 0.0015427
37 | 0.99382 | -0.043054 | 0 | 0
38 | 0.98017 | -0.13969 | 0.00046666 | 0.00011696
39 | 0.9758 | -0.1709 | 8.8643e-05 | 2.2216e-05
40 | 0.97579 | -0.17096 | 0.00016378 | 4.1047e-05
41 | 0.9758 | -0.17086 | 0 | 0
42 | 0.97577 | -0.17113 | 0 | 0
43 | 0.97585 | -0.17051 | 0 | 0
44 | 0.97576 | -0.17118 | 9.9278e-05 | 2.4881e-05
45 | 0.97586 | -0.17045 | 0.00012391 | 3.1054e-05
46 | 1 | 0 | -0.18303 | -0.045949
47 | 0.99381 | -0.042956 | 0 | 0
48 | 0.99873 | -0.0088148 | 0 | 0
49 | 0.99266 | -0.051085 | 0 | 0
50 | 0.99263 | -0.051297 | 0 | 0
51 | 0.99284 | -0.049824 | 0 | 0
52 | 0.99262 | -0.051397 | 0.001958 | 0.00049073
53 | 0.9866 | -0.093545 | 0 | 0
54 | 0.993 | -0.04868 | 0.0023316 | 0.00058436
55 | 0.99861 | -0.0096846 | 0.0041752 | 0.0010464
56 | 0.99772 | -0.015817 | 0.0039852 | 0.00099878
57 | 0.99255 | -0.051892 | 0.00163 | 0.00040852
58 | 0.99246 | -0.052532 | 0 | 0
59 | 0.99245 | -0.052592 | 0.00014634 | 3.6676e-05
60 | 0.99246 | -0.052513 | 0.0004325 | 0.0001084
61 | 0.99268 | -0.051109 | 0 | 0
62 | 0.99276 | -0.05058 | 0 | 0
63 | 0.99267 | -0.051192 | 0.0029612 | 0.00074214
64 | 0.99262 | -0.051509 | 0 | 0
65 | 0.99231 | -0.053735 | 0.0024418 | 0.00061198
66 | 0.99707 | -0.020351 | 0 | 0
67 | 0.99712 | -0.020043 | 0 | 0
68 | 0.99695 | -0.021192 | 0.0068137 | 0.0017077
69 | 0.98399 | -0.11203 | 0.0096736 | 0.0024244
70 | 0.97576 | -0.17118 | 0 | 0
71 | 0.99241 | -0.052843 | 0.00025783 | 6.4618e-05
72 | 0.99242 | -0.052767 | 0.00022554 | 5.6526e-05
73 | 0.97588 | -0.17028 | 3.3972e-05 | 8.5142e-06
74 | 0.98525 | -0.1035 | 0 | 0
75 | 0.98529 | -0.10323 | 0.0031833 | 0.0007978
76 | 0.9851 | -0.10458 | 0.0030744 | 0.00077052
77 | 0.99247 | -0.052401 | 0.0021325 | 0.00053445
78 | 0.98085 | -0.13439 | 0 | 0
79 | 0.98024 | -0.13881 | 0.0010721 | 0.0002687
80 | 0.98203 | -0.12599 | 0.020238 | 0.0050721
81 | 0.99249 | -0.0523 | 0.00020038 | 5.0221e-05
82 | 0.99248 | -0.052339 | 0.00018334 | 4.595e-05
83 | 0.99284 | -0.049988 | 0.0018848 | 0.00047238
84 | 0.97968 | -0.14322 | 0.00039132 | 9.8074e-05
85 | 0.97968 | -0.14322 | 0.0018358 | 0.00046008
86 | 0.97964 | -0.14349 | 0.00090179 | 0.00022601
87 | 0.9797 | -0.14307 | 0.00030201 | 7.5691e-05
88 | 0.97978 | -0.14252 | 0 | 0
89 | 0.97981 | -0.14233 | 0 | 0
90 | 0.97971 | -0.14299 | 0.00038646 | 9.6856e-05
91 | 0.97989 | -0.14172 | 0.00097918 | 0.0002454
92 | 0.97589 | -0.17021 | 0.00010185 | 2.5527e-05
93 | 0.9759 | -0.17008 | 5.2518e-05 | 1.3162e-05
94 | 0.97593 | -0.16987 | 0.00014728 | 3.6912e-05
95 | 0.97595 | -0.1697 | 0.00014325 | 3.5901e-05
96 | 0.97596 | -0.16969 | 0.00058291 | 0.00014609
97 | 0.9856 | -0.10099 | 0.0018989 | 0.0004759
98 | 0.98567 | -0.10056 | 0 | 0
99 | 0.98569 | -0.1004 | 0 | 0
100 | 0.98554 | -0.10145 | 0.0026662 | 0.0006682
101 | 0.98546 | -0.102 | 0.0019003 | 0.00047625
102 | 0.98587 | -0.099141 | 0 | 0
103 | 0.97996 | -0.14122 | 0 | 0
104 | 0.97994 | -0.14139 | 0.00091895 | 0.00023031
105 | 0.97613 | -0.16838 | 0.00053927 | 0.00013515
106 | 0.97615 | -0.16827 | 0.00083707 | 0.00020979
107 | 0.976 | -0.16933 | 0.00016944 | 4.2465e-05
108 | 0.97627 | -0.16735 | 0.00025211 | 6.3184e-05
109 | 0.97597 | -0.1696 | 0.00014402 | 3.6095e-05
110 | 0.97626 | -0.16749 | 0.00014183 | 3.5547e-05
111 | 0.97696 | -0.16237 | 0 | 0
112 | 0.97672 | -0.16404 | 0.00086277 | 0.00021623
113 | 0.97726 | -0.16021 | 0.0016784 | 0.00042066
114 | 0.97632 | -0.16691 | 0.006754 | 0.0016927
115 | 0.98581 | -0.09952 | 0.0043992 | 0.0011025
116 | 0.98533 | -0.10295 | 0.0011729 | 0.00029396
117 | 0.99353 | -0.045111 | 0.0052644 | 0.0013194
118 | 0.99333 | -0.046535 | 0.0039796 | 0.00099739
119 | 0.99293 | -0.049315 | 0.0017078 | 0.00042802
120 | 0.97576 | -0.17119 | 6.2134e-05 | 1.5572e-05
121 | 0.99243 | -0.05268 | 0.00024257 | 6.0793e-05
122 | 0.99312 | -0.047984 | 0 | 0
123 | 0.99303 | -0.048627 | 0.0028142 | 0.0007053
124 | 0.99245 | -0.052587 | 0.00088811 | 0.00022258
125 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.069644 | -0.017475 | 0.069825 | 0.017544 | 0.0001803 | 6.9009e-05 | 0.10485 | 0.10485 | 0.10485 | 0.98845 | -0.080825 | 0.99109 | -0.062217 | 38.8334
1 | 0.033802 | 0.0084851 | -0.033783 | -0.0084782 | 1.8206e-05 | 6.8579e-06 | 0.05089 | 0.05089 | 0.05089 | 0.98845 | -0.080825 | 0.9879 | -0.084705 | 18.8481
2 | 0.035843 | 0.0089897 | -0.035829 | -0.0089846 | 1.3505e-05 | 5.099e-06 | 0.05396 | 0.05396 | 0.05396 | 0.98845 | -0.080825 | 0.98806 | -0.083544 | 19.9853
3 | -0.075281 | -0.018911 | 0.075484 | 0.018989 | 0.00020275 | 7.7653e-05 | 0.11304 | 0.11304 | 0.11304 | 0.99109 | -0.062217 | 0.99384 | -0.042906 | 41.8675
4 | 0.030137 | 0.0075643 | -0.030107 | -0.0075531 | 2.997e-05 | 1.1229e-05 | 0.045398 | 0.045398 | 0.045398 | 0.9879 | -0.084705 | 0.98689 | -0.091875 | 16.814
5 | 0.010327 | 0.0025878 | -0.010319 | -0.0025853 | 8.271e-06 | 2.4799e-06 | 0.015553 | 0.015553 | 0.015553 | 0.98806 | -0.083544 | 0.98725 | -0.089335 | 5.7603
6 | 0.025502 | 0.0063968 | -0.025491 | -0.0063928 | 1.0752e-05 | 3.9859e-06 | 0.038408 | 0.038408 | 0.038408 | 0.98806 | -0.083544 | 0.98764 | -0.086586 | 14.225
7 | 0.0012609 | 0.00031552 | -0.0012608 | -0.00031575 | 4.4667e-08 | -2.34e-07 | 0.0019046 | 0.0019047 | 0.0019047 | 0.98503 | -0.10505 | 0.98499 | -0.1053 | 0.70543
8 | -0.023561 | -0.0059068 | 0.023573 | 0.0059112 | 1.1728e-05 | 4.3218e-06 | 0.035593 | 0.035593 | 0.035593 | 0.98503 | -0.10505 | 0.98554 | -0.10145 | 13.1825
9 | 0.0223 | 0.0055913 | -0.022283 | -0.0055852 | 1.6799e-05 | 6.1593e-06 | 0.033688 | 0.033688 | 0.033688 | 0.98503 | -0.10505 | 0.98426 | -0.11049 | 12.4771
10 | 0.0012608 | 0.00031575 | -0.0012608 | -0.00031599 | 4.457e-08 | -2.3345e-07 | 0.0019047 | 0.0019047 | 0.0019047 | 0.98499 | -0.1053 | 0.98496 | -0.10556 | 0.70546
11 | -0.026741 | -0.0067052 | 0.026777 | 0.0067184 | 3.5543e-05 | 1.3225e-05 | 0.040376 | 0.040376 | 0.040376 | 0.98554 | -0.10145 | 0.98689 | -0.091875 | 14.9542
12 | 0.019246 | 0.004824 | -0.01924 | -0.0048217 | 6.4224e-06 | 2.3157e-06 | 0.029097 | 0.029097 | 0.029097 | 0.98426 | -0.11049 | 0.98393 | -0.1129 | 10.7766
13 | 0.015983 | 0.0040056 | -0.015968 | -0.0040004 | 1.4899e-05 | 5.2118e-06 | 0.024171 | 0.024171 | 0.024171 | 0.98393 | -0.1129 | 0.98298 | -0.11964 | 8.9523
14 | 0.003257 | 0.00081609 | -0.0032567 | -0.00081621 | 2.7599e-07 | -1.2537e-07 | 0.0049256 | 0.0049257 | 0.0049257 | 0.98393 | -0.1129 | 0.98384 | -0.11351 | 1.8243
15 | 0.013392 | 0.0033548 | -0.013386 | -0.0033528 | 5.7712e-06 | 1.9345e-06 | 0.020272 | 0.020272 | 0.020272 | 0.98298 | -0.11964 | 0.98254 | -0.12275 | 7.5081
16 | 0.0034056 | 0.00085262 | -0.003405 | -0.00085286 | 6.2422e-07 | -2.4535e-07 | 0.0051327 | 0.0051329 | 0.0051329 | 0.98725 | -0.089335 | 0.98706 | -0.090661 | 1.9011
17 | 0.025491 | 0.0063928 | -0.02546 | -0.0063814 | 3.0757e-05 | 1.1403e-05 | 0.038408 | 0.038408 | 0.038408 | 0.98764 | -0.086586 | 0.98641 | -0.0953 | 14.2251
18 | -0.0080134 | -0.002006 | 0.008016 | 0.0020066 | 2.6777e-06 | 6.6221e-07 | 0.012148 | 0.012148 | 0.012148 | 0.98152 | -0.13006 | 0.98186 | -0.12764 | 4.4991
19 | 0.0080134 | 0.002006 | -0.0080104 | -0.0020052 | 2.9281e-06 | 7.2444e-07 | 0.012148 | 0.012148 | 0.012148 | 0.98152 | -0.13006 | 0.98115 | -0.13271 | 4.4992
20 | -0.0091093 | -0.0022806 | 0.0091123 | 0.0022814 | 2.9354e-06 | 8.1669e-07 | 0.013804 | 0.013804 | 0.013804 | 0.98186 | -0.12764 | 0.98218 | -0.12531 | 5.1128
21 | 0.0073734 | 0.0018456 | -0.0073723 | -0.0018453 | 1.0395e-06 | 2.3157e-07 | 0.011182 | 0.011182 | 0.011182 | 0.98115 | -0.13271 | 0.98101 | -0.13373 | 4.1414
22 | 0.0073723 | 0.0018453 | -0.0073687 | -0.0018445 | 3.6694e-06 | 8.1781e-07 | 0.011182 | 0.011182 | 0.011182 | 0.98101 | -0.13373 | 0.9805 | -0.13733 | 4.1414
23 | 0.0066776 | 0.0016713 | -0.0066771 | -0.0016712 | 4.4581e-07 | 8.3715e-08 | 0.010133 | 0.010133 | 0.010133 | 0.9805 | -0.13733 | 0.98044 | -0.13782 | 3.753
24 | -0.0018807 | -0.00047135 | 0.0018809 | 0.0004709 | 2.0805e-07 | -4.5e-07 | 0.0028355 | 0.0028354 | 0.0028355 | 0.98695 | -0.091461 | 0.98706 | -0.090661 | 1.0502
25 | 0.0016708 | 0.00041854 | -0.0016707 | -0.00041871 | 6.5227e-08 | -1.7899e-07 | 0.0025386 | 0.0025386 | 0.0025386 | 0.97931 | -0.14545 | 0.97927 | -0.14573 | 0.94024
26 | -0.0016708 | -0.00041854 | 0.0016708 | 0.00041829 | 8.9988e-08 | -2.4698e-07 | 0.0025386 | 0.0025385 | 0.0025386 | 0.97931 | -0.14545 | 0.97936 | -0.14506 | 0.94021
27 | -0.0061491 | -0.0015407 | 0.0061501 | 0.0015408 | 9.4699e-07 | 1.454e-07 | 0.0093426 | 0.0093426 | 0.0093426 | 0.97936 | -0.14506 | 0.97952 | -0.14394 | 3.4602
28 | -0.0020585 | -0.0005159 | 0.0020586 | 0.00051569 | 1.2152e-07 | -2.1014e-07 | 0.0031081 | 0.003108 | 0.0031081 | 0.98549 | -0.10182 | 0.98555 | -0.1014 | 1.1512
29 | -0.0038362 | -0.00096121 | 0.0038365 | 0.00096116 | 2.1342e-07 | -4.7838e-08 | 0.005792 | 0.005792 | 0.005792 | 0.98555 | -0.1014 | 0.9856 | -0.10099 | 2.1452
30 | -0.015088 | -0.0037746 | 0.015095 | 0.0037769 | 6.7529e-06 | 2.3383e-06 | 0.022929 | 0.022929 | 0.022929 | 0.97907 | -0.14719 | 0.97952 | -0.14394 | 8.4923
31 | 0.015088 | 0.0037746 | -0.015082 | -0.0037724 | 6.3012e-06 | 2.1821e-06 | 0.022929 | 0.022929 | 0.022929 | 0.97907 | -0.14719 | 0.97865 | -0.15021 | 8.4924
32 | -0.021245 | -0.0053177 | 0.02126 | 0.0053232 | 1.5072e-05 | 5.5047e-06 | 0.032272 | 0.032272 | 0.032272 | 0.97952 | -0.14394 | 0.98024 | -0.13881 | 11.9525
33 | 0.013008 | 0.0032525 | -0.01299 | -0.0032465 | 1.7896e-05 | 5.9628e-06 | 0.019775 | 0.019775 | 0.019775 | 0.97865 | -0.15021 | 0.97726 | -0.16021 | 7.3242
34 | -0.01051 | -0.0026317 | 0.01051 | 0.0026318 | 4.7706e-07 | 1.4531e-07 | 0.015921 | 0.015921 | 0.015921 | 0.98218 | -0.12531 | 0.98223 | -0.12498 | 5.8968
35 | 0.0061861 | 0.0015482 | -0.0061845 | -0.0015479 | 1.6e-06 | 2.4859e-07 | 0.0093879 | 0.009388 | 0.009388 | 0.98044 | -0.13782 | 0.98017 | -0.13969 | 3.477
36 | -0.011524 | -0.0028859 | 0.011527 | 0.002887 | 3.5501e-06 | 1.1291e-06 | 0.017457 | 0.017457 | 0.017457 | 0.98223 | -0.12498 | 0.98254 | -0.12275 | 6.4656
37 | 0.022151 | 0.0055521 | -0.02214 | -0.0055477 | 1.1774e-05 | 4.3127e-06 | 0.033416 | 0.033416 | 0.033416 | 0.98641 | -0.0953 | 0.98587 | -0.099141 | 12.3763
38 | 0.02107 | 0.0052798 | -0.021064 | -0.0052774 | 6.4281e-06 | 2.3382e-06 | 0.031547 | 0.031547 | 0.031547 | 0.99384 | -0.042906 | 0.99353 | -0.045111 | 11.6839
39 | 0.0061563 | 0.0015428 | -0.0061562 | -0.0015428 | 1.2639e-07 | 1.7719e-08 | 0.0092174 | 0.0092174 | 0.0092174 | 0.99384 | -0.042906 | 0.99382 | -0.043054 | 3.4139
40 | -0.10271 | -0.025812 | 0.10304 | 0.025937 | 0.00032793 | 0.00012584 | 0.15381 | 0.15381 | 0.15381 | 0.99384 | -0.042906 | 0.99712 | -0.020043 | 56.9652
41 | -0.0061554 | -0.0015427 | 0.0061562 | 0.0015428 | 7.2539e-07 | 1.0172e-07 | 0.0092175 | 0.0092174 | 0.0092175 | 0.9937 | -0.043905 | 0.99382 | -0.043054 | 3.4139
42 | 0.0057178 | 0.001431 | -0.0057166 | -0.0014308 | 1.2078e-06 | 1.4077e-07 | 0.0086796 | 0.0086797 | 0.0086797 | 0.98017 | -0.13969 | 0.97996 | -0.14122 | 3.2147
43 | 0.00016378 | 4.0618e-05 | -0.00016378 | -4.1047e-05 | 1.3386e-09 | -4.2937e-07 | 0.0002496 | 0.00024975 | 0.00024975 | 0.9758 | -0.1709 | 0.97579 | -0.17096 | 0.092501
44 | -0.00025242 | -6.2834e-05 | 0.00025242 | 6.266e-05 | 1.2859e-09 | -1.7341e-07 | 0.00038477 | 0.00038471 | 0.00038477 | 0.9758 | -0.1709 | 0.9758 | -0.17086 | 0.14251
45 | 0.00016142 | 3.7939e-05 | -0.00016141 | -3.9729e-05 | 5.3992e-09 | -1.7901e-06 | 0.00024527 | 0.00024589 | 0.00024589 | 0.9758 | -0.17086 | 0.97577 | -0.17113 | 0.091071
46 | -0.00041384 | -0.0001006 | 0.00041386 | 9.9653e-05 | 1.8885e-08 | -9.4589e-07 | 0.00062997 | 0.00062964 | 0.00062997 | 0.9758 | -0.17086 | 0.97585 | -0.17051 | 0.23332
47 | 0.00016141 | 3.9729e-05 | -0.00016141 | -4.0088e-05 | 1.0853e-09 | -3.5872e-07 | 0.00024589 | 0.00024602 | 0.00024602 | 0.97577 | -0.17113 | 0.97576 | -0.17118 | 0.091118
48 | -0.00041386 | -9.9653e-05 | 0.00041387 | 9.948e-05 | 3.4448e-09 | -1.7266e-07 | 0.00062964 | 0.00062958 | 0.00062964 | 0.97585 | -0.17051 | 0.97586 | -0.17045 | 0.2332
49 | 6.2134e-05 | 1.5206e-05 | -6.2134e-05 | -1.5345e-05 | 6.2111e-11 | -1.3877e-07 | 9.4623e-05 | 9.4672e-05 | 9.4672e-05 | 0.97576 | -0.17118 | 0.97576 | -0.17118 | 0.035064
50 | -0.00053777 | -0.00013053 | 0.00053779 | 0.00013019 | 1.1648e-08 | -3.4369e-07 | 0.00081851 | 0.00081839 | 0.00081851 | 0.97586 | -0.17045 | 0.97588 | -0.17028 | 0.30315
51 | 0.063897 | 0.016136 | -0.063514 | -0.015992 | 0.00038349 | 0.00014395 | 0.095123 | 0.095124 | 0.095124 | 1 | 0 | 0.99381 | -0.042956 | 17.6155
52 | 0.11834 | 0.029813 | -0.11819 | -0.029758 | 0.00014574 | 5.566e-05 | 0.17614 | 0.17614 | 0.17614 | 1 | 0 | 0.99873 | -0.0088148 | 32.6186
53 | 0.052872 | 0.013327 | -0.052501 | -0.013186 | 0.0003719 | 0.00014181 | 0.079192 | 0.079192 | 0.079192 | 0.99381 | -0.042956 | 0.9866 | -0.093545 | 29.3305
54 | 0.010641 | 0.0026641 | -0.010633 | -0.0026616 | 8.4102e-06 | 2.5472e-06 | 0.015932 | 0.015932 | 0.015932 | 0.99381 | -0.042956 | 0.993 | -0.04868 | 5.9008
55 | 0.0041757 | 0.0010463 | -0.0041752 | -0.0010464 | 5.0272e-07 | -7.8985e-08 | 0.0062214 | 0.0062215 | 0.0062215 | 0.99873 | -0.0088148 | 0.99861 | -0.0096846 | 2.3043
56 | 0.11401 | 0.028711 | -0.1139 | -0.028669 | 0.00011147 | 4.2551e-05 | 0.16992 | 0.16992 | 0.16992 | 0.99873 | -0.0088148 | 0.99772 | -0.015817 | 31.4665
57 | 0.0025929 | 0.00064785 | -0.0025929 | -0.00064793 | 7.5481e-08 | -7.4508e-08 | 0.0038862 | 0.0038862 | 0.0038862 | 0.99266 | -0.051085 | 0.99263 | -0.051297 | 1.4393
58 | -0.0082983 | -0.0020765 | 0.0082998 | 0.0020769 | 1.4446e-06 | 3.6214e-07 | 0.012438 | 0.012438 | 0.012438 | 0.99266 | -0.051085 | 0.99284 | -0.049824 | 4.6068
59 | 0.0057054 | 0.0014287 | -0.0057052 | -0.0014287 | 2.4566e-07 | 2.4903e-08 | 0.0085521 | 0.0085521 | 0.0085521 | 0.99266 | -0.051085 | 0.99262 | -0.051397 | 3.1674
60 | 0.0025929 | 0.00064793 | -0.0025927 | -0.00064814 | 2.1237e-07 | -2.0958e-07 | 0.0038862 | 0.0038863 | 0.0038863 | 0.99263 | -0.051297 | 0.99255 | -0.051892 | 1.4394
61 | -0.0082998 | -0.0020769 | 0.0083011 | 0.0020772 | 1.3107e-06 | 3.285e-07 | 0.012438 | 0.012438 | 0.012438 | 0.99284 | -0.049824 | 0.993 | -0.04868 | 4.6067
62 | 0.0037471 | 0.00093794 | -0.0037466 | -0.00093808 | 5.1977e-07 | -1.4132e-07 | 0.0056168 | 0.005617 | 0.005617 | 0.99262 | -0.051397 | 0.99247 | -0.052401 | 2.0804
63 | 0.052501 | 0.013186 | -0.052366 | -0.013134 | 0.00013453 | 5.1304e-05 | 0.079192 | 0.079193 | 0.079193 | 0.9866 | -0.093545 | 0.98399 | -0.11203 | 29.3306
64 | 0.10992 | 0.02767 | -0.10985 | -0.027645 | 6.4832e-05 | 2.4734e-05 | 0.16398 | 0.16398 | 0.16398 | 0.99772 | -0.015817 | 0.99712 | -0.020043 | 30.3659
65 | 0.00096264 | 0.00023961 | -0.00096259 | -0.00024013 | 5.373e-08 | -5.1399e-07 | 0.0014426 | 0.0014428 | 0.0014428 | 0.99255 | -0.051892 | 0.99249 | -0.0523 | 0.53437
66 | 0.00014634 | 3.6156e-05 | -0.00014634 | -3.6676e-05 | 1.2072e-09 | -5.1924e-07 | 0.00021923 | 0.00021941 | 0.00021941 | 0.99246 | -0.052532 | 0.99245 | -0.052592 | 0.081263
67 | -0.00014634 | -3.6156e-05 | 0.00014634 | 3.6001e-05 | 3.6142e-10 | -1.5563e-07 | 0.00021923 | 0.00021917 | 0.00021923 | 0.99246 | -0.052532 | 0.99246 | -0.052513 | 0.081195
68 | -0.00057884 | -0.0001444 | 0.00057885 | 0.00014402 | 1.382e-08 | -3.7494e-07 | 0.00086763 | 0.0008675 | 0.00086763 | 0.99246 | -0.052513 | 0.99248 | -0.052339 | 0.32134
69 | -0.0029612 | -0.00074212 | 0.0029614 | 0.00074197 | 2.1684e-07 | -1.4463e-07 | 0.0044388 | 0.0044387 | 0.0044388 | 0.99268 | -0.051109 | 0.99276 | -0.05058 | 1.644
70 | 0.0029612 | 0.00074212 | -0.0029612 | -0.00074214 | 3.3975e-08 | -2.2657e-08 | 0.0044388 | 0.0044388 | 0.0044388 | 0.99268 | -0.051109 | 0.99267 | -0.051192 | 1.644
71 | -0.0054043 | -0.0013527 | 0.0054048 | 0.0013527 | 4.416e-07 | 3.0359e-08 | 0.0080998 | 0.0080997 | 0.0080998 | 0.99276 | -0.05058 | 0.99284 | -0.049988 | 2.9999
72 | 0.0024429 | 0.00061074 | -0.0024426 | -0.0006111 | 3.1286e-07 | -3.6326e-07 | 0.003661 | 0.0036612 | 0.0036612 | 0.99276 | -0.05058 | 0.99262 | -0.051509 | 1.356
73 | 0.0024426 | 0.0006111 | -0.0024418 | -0.00061198 | 7.514e-07 | -8.7173e-07 | 0.0036612 | 0.0036616 | 0.0036616 | 0.99262 | -0.051509 | 0.99231 | -0.053735 | 1.3562
74 | -0.0068145 | -0.0017078 | 0.0068148 | 0.0017079 | 2.9119e-07 | 5.3146e-08 | 0.01017 | 0.01017 | 0.01017 | 0.99707 | -0.020351 | 0.99712 | -0.020043 | 3.7666
75 | 0.0068145 | 0.0017078 | -0.0068137 | -0.0017077 | 7.9299e-07 | 1.4476e-07 | 0.01017 | 0.01017 | 0.01017 | 0.99707 | -0.020351 | 0.99695 | -0.021192 | 3.7666
76 | 0.042692 | 0.01071 | -0.04261 | -0.010679 | 8.2544e-05 | 3.1346e-05 | 0.064564 | 0.064564 | 0.064564 | 0.98399 | -0.11203 | 0.98203 | -0.12599 | 23.9127
77 | 6.2134e-05 | 1.5345e-05 | -6.2134e-05 | -1.5572e-05 | 1.0195e-10 | -2.2743e-07 | 9.4672e-05 | 9.4754e-05 | 9.4754e-05 | 0.97576 | -0.17118 | 0.97576 | -0.17119 | 0.035094
78 | -0.00025783 | -6.4618e-05 | 0.00025783 | 6.4245e-05 | 2.6994e-09 | -3.7311e-07 | 0.00038659 | 0.00038645 | 0.00038659 | 0.99241 | -0.052843 | 0.99242 | -0.052767 | 0.14318
79 | -0.00048337 | -0.00012077 | 0.00048338 | 0.00012054 | 5.8222e-09 | -2.2739e-07 | 0.00072462 | 0.00072454 | 0.00072462 | 0.99242 | -0.052767 | 0.99243 | -0.05268 | 0.26838
80 | -0.00057176 | -0.00013871 | 0.00057176 | 0.00013857 | 5.3208e-09 | -1.3865e-07 | 0.00087019 | 0.00087014 | 0.00087019 | 0.97588 | -0.17028 | 0.97589 | -0.17021 | 0.32229
81 | -0.0030749 | -0.00077027 | 0.003075 | 0.0007702 | 1.1426e-07 | -6.4191e-08 | 0.0046438 | 0.0046438 | 0.0046438 | 0.98525 | -0.1035 | 0.98529 | -0.10323 | 1.7199
82 | 0.0030749 | 0.00077027 | -0.0030744 | -0.00077052 | 4.5916e-07 | -2.5786e-07 | 0.0046438 | 0.004644 | 0.004644 | 0.98525 | -0.1035 | 0.9851 | -0.10458 | 1.72
83 | -0.0062583 | -0.001568 | 0.0062585 | 0.001568 | 2.4215e-07 | 3.7802e-08 | 0.0094513 | 0.0094513 | 0.0094513 | 0.98529 | -0.10323 | 0.98533 | -0.10295 | 3.5005
84 | 0.0016141 | 0.00040363 | -0.0016141 | -0.00040376 | 4.1328e-08 | -1.3027e-07 | 0.0024197 | 0.0024198 | 0.0024198 | 0.99247 | -0.052401 | 0.99245 | -0.052587 | 0.89621
85 | 0.022346 | 0.0055969 | -0.022332 | -0.0055919 | 1.3635e-05 | 5.0043e-06 | 0.033899 | 0.033899 | 0.033899 | 0.98085 | -0.13439 | 0.98024 | -0.13881 | 12.5552
86 | -0.022346 | -0.0055969 | 0.022372 | 0.0056065 | 2.5985e-05 | 9.5364e-06 | 0.033899 | 0.033899 | 0.033899 | 0.98085 | -0.13439 | 0.98203 | -0.12599 | 12.5552
87 | 0.0007622 | 0.00018991 | -0.0007622 | -0.00018997 | 4.0918e-09 | -6.3361e-08 | 0.0011424 | 0.0011424 | 0.0011424 | 0.99249 | -0.0523 | 0.99248 | -0.052339 | 0.4231
88 | -0.0072896 | -0.0018251 | 0.0072903 | 0.0018253 | 6.7818e-07 | 1.4306e-07 | 0.010925 | 0.010925 | 0.010925 | 0.99284 | -0.049988 | 0.99293 | -0.049315 | 4.0462
89 | -0.00039132 | -9.8074e-05 | 0.00039132 | 9.8069e-05 | 8.7514e-11 | -4.9666e-09 | 0.00059436 | 0.00059436 | 0.00059436 | 0.97968 | -0.14322 | 0.97968 | -0.14322 | 0.22013
90 | -0.0022271 | -0.00055815 | 0.0022271 | 0.00055806 | 6.793e-08 | -9.3674e-08 | 0.0033827 | 0.0033826 | 0.0033827 | 0.97968 | -0.14322 | 0.97971 | -0.14299 | 1.2528
91 | -0.00090179 | -0.00022601 | 0.00090184 | 0.00022547 | 5.2354e-08 | -5.43e-07 | 0.0013698 | 0.0013696 | 0.0013698 | 0.97964 | -0.14349 | 0.9797 | -0.14307 | 0.50732
92 | -0.0012039 | -0.00030116 | 0.0012039 | 0.00030065 | 9.0365e-08 | -5.1089e-07 | 0.0018283 | 0.0018281 | 0.0018283 | 0.9797 | -0.14307 | 0.97978 | -0.14252 | 0.67714
93 | -0.0038177 | -0.00095541 | 0.0038178 | 0.00095539 | 1.0067e-07 | -2.1732e-08 | 0.0057976 | 0.0057976 | 0.0057976 | 0.97978 | -0.14252 | 0.97981 | -0.14233 | 2.1473
94 | 0.0026138 | 0.00065476 | -0.0026136 | -0.00065492 | 1.7143e-07 | -1.5362e-07 | 0.0039695 | 0.0039696 | 0.0039696 | 0.97978 | -0.14252 | 0.97971 | -0.14299 | 1.4702
95 | -0.0038178 | -0.00095539 | 0.0038181 | 0.00095532 | 3.1923e-07 | -6.8938e-08 | 0.0057976 | 0.0057975 | 0.0057976 | 0.97981 | -0.14233 | 0.97989 | -0.14172 | 2.1472
96 | -0.0047973 | -0.0012007 | 0.0047977 | 0.0012007 | 3.3303e-07 | 1.3796e-09 | 0.0072844 | 0.0072844 | 0.0072844 | 0.97989 | -0.14172 | 0.97996 | -0.14122 | 2.6979
97 | -0.00067362 | -0.00016409 | 0.00067363 | 0.00016387 | 1.1814e-08 | -2.2043e-07 | 0.0010254 | 0.0010254 | 0.0010254 | 0.97589 | -0.17021 | 0.9759 | -0.17008 | 0.37979
98 | -0.00072615 | -0.00017704 | 0.00072617 | 0.00017672 | 1.9509e-08 | -3.1221e-07 | 0.0011054 | 0.0011053 | 0.0011054 | 0.9759 | -0.17008 | 0.97593 | -0.16987 | 0.40942
99 | -0.00087345 | -0.00021364 | 0.00087347 | 0.00021342 | 1.978e-08 | -2.1637e-07 | 0.0013299 | 0.0013298 | 0.0013299 | 0.97593 | -0.16987 | 0.97595 | -0.1697 | 0.49255
100 | -0.0010167 | -0.00024932 | 0.0010167 | 0.00024931 | 1.2778e-09 | -1.0184e-08 | 0.0015482 | 0.0015482 | 0.0015482 | 0.97595 | -0.1697 | 0.97596 | -0.16969 | 0.57341
101 | -0.0015996 | -0.0003954 | 0.0015996 | 0.00039534 | 1.9388e-08 | -5.7923e-08 | 0.0024369 | 0.0024369 | 0.0024369 | 0.97596 | -0.16969 | 0.97597 | -0.1696 | 0.90257
102 | -0.0057353 | -0.0014371 | 0.0057357 | 0.0014371 | 3.4576e-07 | 3.8791e-08 | 0.0086588 | 0.0086588 | 0.0086588 | 0.9856 | -0.10099 | 0.98567 | -0.10056 | 3.207
103 | -0.0084022 | -0.002105 | 0.0084023 | 0.0021051 | 1.786e-07 | 4.6017e-08 | 0.012684 | 0.012684 | 0.012684 | 0.98567 | -0.10056 | 0.98569 | -0.1004 | 4.6978
104 | 0.0026665 | 0.00066792 | -0.0026662 | -0.0006682 | 3.275e-07 | -2.8682e-07 | 0.0040254 | 0.0040255 | 0.0040255 | 0.98567 | -0.10056 | 0.98554 | -0.10145 | 1.4909
105 | 0.0093347 | 0.0023391 | -0.0093327 | -0.0023385 | 2.056e-06 | 5.7932e-07 | 0.014092 | 0.014092 | 0.014092 | 0.98569 | -0.1004 | 0.98546 | -0.102 | 5.2192
106 | -0.017737 | -0.0044441 | 0.01774 | 0.0044452 | 3.1003e-06 | 1.1041e-06 | 0.026776 | 0.026776 | 0.026776 | 0.98569 | -0.1004 | 0.98587 | -0.099141 | 9.917
107 | 0.0074324 | 0.0018622 | -0.0074314 | -0.001862 | 9.848e-07 | 2.1914e-07 | 0.011223 | 0.011223 | 0.011223 | 0.98546 | -0.102 | 0.98533 | -0.10295 | 4.1565
108 | 0.0043994 | 0.0011025 | -0.0043992 | -0.0011025 | 2.3104e-07 | -1.8205e-08 | 0.0066402 | 0.0066403 | 0.0066403 | 0.98587 | -0.099141 | 0.98581 | -0.09952 | 2.4594
109 | 0.00091897 | 0.00023009 | -0.00091895 | -0.00023031 | 2.1987e-08 | -2.1954e-07 | 0.0013953 | 0.0013954 | 0.0013954 | 0.97996 | -0.14122 | 0.97994 | -0.14139 | 0.51682
110 | -0.0024527 | -0.00060842 | 0.0024527 | 0.00060838 | 3.402e-08 | -3.5728e-08 | 0.0037366 | 0.0037366 | 0.0037366 | 0.97613 | -0.16838 | 0.97615 | -0.16827 | 1.3839
111 | 0.0019134 | 0.00047326 | -0.0019132 | -0.00047375 | 2.4704e-07 | -4.8746e-07 | 0.0029146 | 0.0029148 | 0.0029148 | 0.97613 | -0.16838 | 0.976 | -0.16933 | 1.0795
112 | -0.0032898 | -0.00081817 | 0.0032902 | 0.000818 | 4.1379e-07 | -1.7082e-07 | 0.0050126 | 0.0050125 | 0.0050126 | 0.97615 | -0.16827 | 0.97627 | -0.16735 | 1.8565
113 | 0.0017437 | 0.00043128 | -0.0017437 | -0.00043144 | 6.2925e-08 | -1.5438e-07 | 0.0026564 | 0.0026565 | 0.0026565 | 0.976 | -0.16933 | 0.97597 | -0.1696 | 0.98389
114 | 0.00014184 | 3.437e-05 | -0.00014183 | -3.5547e-05 | 2.7405e-09 | -1.1762e-06 | 0.00021577 | 0.00021618 | 0.00021618 | 0.97627 | -0.16735 | 0.97626 | -0.16749 | 0.080068
115 | -0.0036841 | -0.00091555 | 0.0036866 | 0.00091492 | 2.4938e-06 | -6.2852e-07 | 0.0056125 | 0.0056119 | 0.0056125 | 0.97627 | -0.16735 | 0.97696 | -0.16237 | 2.0787
116 | 0.0076212 | 0.0019099 | -0.0076194 | -0.0019095 | 1.757e-06 | 4.1416e-07 | 0.011608 | 0.011608 | 0.011608 | 0.97696 | -0.16237 | 0.97672 | -0.16404 | 4.2992
117 | -0.011308 | -0.0028248 | 0.011311 | 0.0028259 | 3.3677e-06 | 1.0673e-06 | 0.01722 | 0.01722 | 0.01722 | 0.97696 | -0.16237 | 0.97726 | -0.16021 | 6.3777
118 | 0.0067566 | 0.0016932 | -0.006754 | -0.0016927 | 2.6858e-06 | 5.248e-07 | 0.010294 | 0.010294 | 0.010294 | 0.97672 | -0.16404 | 0.97632 | -0.16691 | 3.8125
119 | 0.015799 | 0.0039581 | -0.015796 | -0.003957 | 3.1128e-06 | 1.0819e-06 | 0.023662 | 0.023662 | 0.023662 | 0.99353 | -0.045111 | 0.99333 | -0.046535 | 8.7637
120 | 0.011817 | 0.0029596 | -0.011814 | -0.0029588 | 2.3667e-06 | 7.5359e-07 | 0.017701 | 0.017701 | 0.017701 | 0.99333 | -0.046535 | 0.99312 | -0.047984 | 6.5558
121 | -0.0089981 | -0.0022533 | 0.0089997 | 0.0022537 | 1.6547e-06 | 4.4773e-07 | 0.013484 | 0.013484 | 0.013484 | 0.99293 | -0.049315 | 0.99312 | -0.047984 | 4.994
122 | -0.00072594 | -0.00018134 | 0.00072595 | 0.00018118 | 9.2411e-09 | -1.5804e-07 | 0.0010882 | 0.0010882 | 0.0010882 | 0.99243 | -0.05268 | 0.99245 | -0.052587 | 0.40305
123 | 0.0028144 | 0.0007051 | -0.0028142 | -0.0007053 | 2.5034e-07 | -1.9562e-07 | 0.0042168 | 0.0042169 | 0.0042169 | 0.99312 | -0.047984 | 0.99303 | -0.048627 | 1.5618

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18303 | 0.045949

## res_load
| p_mw | q_mvar
0 | 0.0054565 | 0.0013675
1 | 0.0036464 | 0.00091387
2 | 0.0031682 | 0.00079404
3 | 0.0030372 | 0.00076118
4 | 0.002576 | 0.00064561
5 | 0.0032567 | 0.00081621
6 | 0.0069135 | 0.0017327
7 | 0.0010933 | 0.00027401
8 | 0.00063707 | 0.00015966
9 | 0.00069107 | 0.0001732
10 | 0.0018807 | 0.00047135
11 | 0.001524 | 0.00038196
12 | 0.0016707 | 0.00041871
13 | 0.0044783 | 0.0011224
14 | 0.0020585 | 0.0005159
15 | 0.0017777 | 0.00044552
16 | 0.0020746 | 0.00051993
17 | 0.0013974 | 0.00035022
18 | 0.00049105 | 0.00012307
19 | 0.0010138 | 0.00025408
20 | 0.0033091 | 0.00082933
21 | 0.0018586 | 0.00046582
22 | 0.0033305 | 0.0008347
23 | 0.0012608 | 0.00031599
24 | 0.0061554 | 0.0015427
25 | 0.00046666 | 0.00011696
26 | 8.8643e-05 | 2.2216e-05
27 | 0.00016378 | 4.1047e-05
28 | 9.9278e-05 | 2.4881e-05
29 | 0.00012391 | 3.1054e-05
30 | 0.001958 | 0.00049073
31 | 0.0023316 | 0.00058436
32 | 0.0041752 | 0.0010464
33 | 0.0039852 | 0.00099878
34 | 0.00163 | 0.00040852
35 | 0.00014634 | 3.6676e-05
36 | 0.0004325 | 0.0001084
37 | 0.0029612 | 0.00074214
38 | 0.0024418 | 0.00061198
39 | 0.0068137 | 0.0017077
40 | 0.0096736 | 0.0024244
41 | 0.00025783 | 6.4618e-05
42 | 0.00022554 | 5.6526e-05
43 | 3.3972e-05 | 8.5142e-06
44 | 0.0031833 | 0.0007978
45 | 0.0030744 | 0.00077052
46 | 0.0021325 | 0.00053445
47 | 0.0010721 | 0.0002687
48 | 0.020238 | 0.0050721
49 | 0.00020038 | 5.0221e-05
50 | 0.00018334 | 4.595e-05
51 | 0.0018848 | 0.00047238
52 | 0.00039132 | 9.8074e-05
53 | 0.0018358 | 0.00046008
54 | 0.00090179 | 0.00022601
55 | 0.00030201 | 7.5691e-05
56 | 0.00038646 | 9.6856e-05
57 | 0.00097918 | 0.0002454
58 | 0.00010185 | 2.5527e-05
59 | 5.2518e-05 | 1.3162e-05
60 | 0.00014728 | 3.6912e-05
61 | 0.00014325 | 3.5901e-05
62 | 0.00058291 | 0.00014609
63 | 0.0018989 | 0.0004759
64 | 0.0026662 | 0.0006682
65 | 0.0019003 | 0.00047625
66 | 0.00091895 | 0.00023031
67 | 0.00053927 | 0.00013515
68 | 0.00083707 | 0.00020979
69 | 0.00016944 | 4.2465e-05
70 | 0.00025211 | 6.3184e-05
71 | 0.00014402 | 3.6095e-05
72 | 0.00014183 | 3.5547e-05
73 | 0.00086277 | 0.00021623
74 | 0.0016784 | 0.00042066
75 | 0.006754 | 0.0016927
76 | 0.0043992 | 0.0011025
77 | 0.0011729 | 0.00029396
78 | 0.0052644 | 0.0013194
79 | 0.0039796 | 0.00099739
80 | 0.0017078 | 0.00042802
81 | 6.2134e-05 | 1.5572e-05
82 | 0.00024257 | 6.0793e-05
83 | 0.0028142 | 0.0007053
84 | 0.00088811 | 0.00022258

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1