## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-17_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1010-17_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1010-17_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1010-17_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1010-17_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1010-17_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1010-17_0_3_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1010-17_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1010-17_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1010-17_0_3_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_1010-17_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1010-17_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1010-17_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1010-17_0_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1010-17_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1010-17_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1010-17_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1010-17_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1010-17_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1010-17_0_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1010-17_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1010-17_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1010-17_0_3_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1010-17_0_3_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1010-17_0_3_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_1010-17_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1010-17_0_3_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1010-17_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1010-17_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1010-17_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_MV_126_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-17_0_3_load_0 | 0 | 0.0042401 | 0.0010627 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-17_0_3_load_1 | 1 | 0.013158 | 0.0032978 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-17_0_3_load_4 | 4 | 0.0071336 | 0.0017878 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-17_0_3_load_17 | 6 | 0.023243 | 0.0058252 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-17_0_3_load_30 | 8 | 0.0036812 | 0.0009226 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-17_0_3_load_24 | 9 | 0.0026191 | 0.0006564 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-17_0_3_load_19 | 11 | 0.015524 | 0.0038907 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-17_0_3_load_20 | 12 | 0.0042999 | 0.0010776 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-17_0_3_load_18 | 13 | 0.0035308 | 0.00088491 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-17_0_3_load_15 | 17 | 0.0015867 | 0.00039767 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-17_0_3_load_26 | 19 | 0.039739 | 0.0099596 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-17_0_3_load_28 | 20 | 0.002486 | 0.00062304 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-17_0_3_load_22 | 21 | 0.0010831 | 0.00027146 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-17_0_3_load_33 | 22 | 0.0017562 | 0.00044014 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-17_0_3_load_31 | 23 | 0.004323 | 0.0010834 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-17_0_3_load_34 | 24 | 0.026529 | 0.0066489 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-17_0_3_load_16 | 25 | 0.0014252 | 0.00035718 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-17_0_3_load_32 | 26 | 0.030001 | 0.007519 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-17_0_3_load_27 | 27 | 0.023902 | 0.0059904 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-17_0_3_load_21 | 28 | 0.003009 | 0.00075413 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-17_0_3_load_23 | 29 | 0.0066877 | 0.0016761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-17_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1010-17_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.019114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1010-17_0_3_line_2 | NAYY 4x150 SE | 2 | 6 | 0.015862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1010-17_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.013607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1010-17_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-17_0_3_line_5 | NAYY 4x150 SE | 4 | 7 | 0.058738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1010-17_0_3_line_6 | NAYY 4x150 SE | 5 | 8 | 0.031734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1010-17_0_3_line_7 | NAYY 4x150 SE | 6 | 15 | 0.028212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1010-17_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.061439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1010-17_0_3_line_9 | NAYY 4x150 SE | 8 | 20 | 0.015937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1010-17_0_3_line_10 | NAYY 4x150 SE | 9 | 21 | 0.011959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1010-17_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.077892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1010-17_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.015052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-17_0_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.025931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1010-17_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.025113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1010-17_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.0084442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1010-17_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.017296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1010-17_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.010495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1010-17_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.11039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1010-17_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.017755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1010-17_0_3_line_20 | NAYY 4x150 SE | 17 | 25 | 0.021726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1010-17_0_3_line_21 | NAYY 4x150 SE | 18 | 26 | 0.0099699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-17_0_3_line_22 | NAYY 4x150 SE | 18 | 24 | 0.02411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-17_0_3_line_23 | NAYY 4x150 SE | 19 | 27 | 0.034253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-17_0_3_line_24 | NAYY 4x150 SE | 20 | 27 | 0.025533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1010-17_0_3_line_25 | NAYY 4x150 SE | 21 | 28 | 0.013876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-17_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.029926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1010-17_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.032807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1010-17_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.0070399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-17_0_3_trafo_26 | 0.25 MVA 20/0.4 kV | 30 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2635205.1937 | 1189395.8304 | 2635207.1209 | 1189422.7428
1 | 2635208.4861 | 1189441.8075 | 2635207.1209 | 1189422.7428
2 | 2635208.4861 | 1189441.8075 | 2635209.7984 | 1189457.6146
3 | 2635201.9314 | 1189350.2752 | 2635210.3814 | 1189348.9909 | 2635215.1434 | 1189347.2806
4 | 2635193.3482 | 1189344.3772 | 2635197.4157 | 1189343.9231 | 2635197.8105 | 1189350.7291 | 2635201.9314 | 1189350.2752
5 | 2635237.0932 | 1189310.705 | 2635244.9794 | 1189336.5653 | 2635215.1434 | 1189347.2806
6 | 2635193.3482 | 1189344.3772 | 2635195.6343 | 1189376.0285
7 | 2635212.1327 | 1189485.7303 | 2635209.7984 | 1189457.6146
8 | 2635237.0932 | 1189310.705 | 2635257.3366 | 1189311.5467 | 2635266.6375 | 1189313.4357 | 2635274.9004 | 1189316.7417 | 2635280.0945 | 1189320.5521 | 2635284.5573 | 1189326.7928 | 2635289.3405 | 1189334.028
9 | 2635195.6343 | 1189376.0285 | 2635196.7825 | 1189391.9246
10 | 2635295.9356 | 1189344.004 | 2635289.3405 | 1189334.028
11 | 2635207.0197 | 1189526.5333 | 2635183.0112 | 1189529.3272 | 2635172.5119 | 1189531.5779 | 2635164.8954 | 1189533.8233 | 2635152.9076 | 1189538.9336 | 2635134.8133 | 1189547.5766 | 2635133.0577 | 1189548.4454
12 | 2635207.0197 | 1189526.5333 | 2635205.7846 | 1189511.5323
13 | 2635207.0197 | 1189526.5333 | 2635209.5566 | 1189552.3402
14 | 2635203.724 | 1189486.5035 | 2635205.7846 | 1189511.5323
15 | 2635203.724 | 1189486.5035 | 2635208.3785 | 1189486.0751 | 2635212.1327 | 1189485.7303
16 | 2635203.724 | 1189486.5035 | 2635202.3686 | 1189469.2641
17 | 2635212.1327 | 1189485.7303 | 2635212.9564 | 1189496.1934
18 | 2635122.0187 | 1189434.0183 | 2635125.0256 | 1189462.2733 | 2635127.6536 | 1189468.0029 | 2635131.8318 | 1189470.7733 | 2635143.2427 | 1189471.7407 | 2635180.5013 | 1189471.0367 | 2635202.3686 | 1189469.2641
19 | 2635202.3686 | 1189469.2641 | 2635201.0895 | 1189451.555
20 | 2635212.9564 | 1189496.1934 | 2635214.6617 | 1189517.8519
21 | 2635122.0187 | 1189434.0183 | 2635121.3243 | 1189424.0726
22 | 2635122.0187 | 1189434.0183 | 2635097.9092 | 1189434.1596
23 | 2635198.6219 | 1189417.3912 | 2635201.0895 | 1189451.555
24 | 2635198.6219 | 1189417.3912 | 2635196.7825 | 1189391.9246
25 | 2635303.5881 | 1189355.5794 | 2635295.9356 | 1189344.004
26 | 2635119.0393 | 1189391.3448 | 2635117.9662 | 1189375.9744 | 2635103.5308 | 1189374.4223
27 | 2635119.0393 | 1189391.3448 | 2635121.3243 | 1189424.0726
28 | 2635307.4705 | 1189361.452 | 2635303.5881 | 1189355.5794

## bus_geodata
| x | y | coords
0 | 2635205.1937 | 1189395.8304
1 | 2635207.1209 | 1189422.7428
2 | 2635208.4861 | 1189441.8075
3 | 2635201.9314 | 1189350.2752
4 | 2635215.1434 | 1189347.2806
5 | 2635193.3482 | 1189344.3772
6 | 2635209.7984 | 1189457.6146
7 | 2635237.0932 | 1189310.705
8 | 2635195.6343 | 1189376.0285
9 | 2635289.3405 | 1189334.028
10 | 2635207.0197 | 1189526.5333
11 | 2635133.0577 | 1189548.4454
12 | 2635205.7846 | 1189511.5323
13 | 2635209.5566 | 1189552.3402
14 | 2635203.724 | 1189486.5035
15 | 2635212.1327 | 1189485.7303
16 | 2635202.3686 | 1189469.2641
17 | 2635212.9564 | 1189496.1934
18 | 2635122.0187 | 1189434.0183
19 | 2635201.0895 | 1189451.555
20 | 2635196.7825 | 1189391.9246
21 | 2635295.9356 | 1189344.004
22 | 2635103.5308 | 1189374.4223
23 | 2635119.0393 | 1189391.3448
24 | 2635097.9092 | 1189434.1596
25 | 2635214.6617 | 1189517.8519
26 | 2635121.3243 | 1189424.0726
27 | 2635198.6219 | 1189417.3912
28 | 2635303.5881 | 1189355.5794
29 | 2635307.4705 | 1189361.452
30 | 2635202.3686 | 1189469.2641

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99347 | -0.045701 | 0.0042401 | 0.0010627
1 | 0.99364 | -0.044544 | 0.013158 | 0.0032978
2 | 0.99412 | -0.041183 | 0 | 0
3 | 0.99461 | -0.037772 | 0 | 0
4 | 0.9942 | -0.040594 | 0.0071336 | 0.0017878
5 | 0.99505 | -0.034652 | 0 | 0
6 | 0.99451 | -0.038397 | 0.023243 | 0.0058252
7 | 0.99307 | -0.048557 | 0 | 0
8 | 0.99599 | -0.028085 | 0.0036812 | 0.0009226
9 | 0.99189 | -0.056902 | 0.0026191 | 0.0006564
10 | 0.99543 | -0.031927 | 0 | 0
11 | 0.9937 | -0.044131 | 0.015524 | 0.0038907
12 | 0.99584 | -0.029038 | 0.0042999 | 0.0010776
13 | 0.9953 | -0.03285 | 0.0035308 | 0.00088491
14 | 0.99668 | -0.023137 | 0 | 0
15 | 0.99616 | -0.026844 | 0 | 0
16 | 0.99834 | -0.011508 | 0 | 0
17 | 0.99611 | -0.027162 | 0.0015867 | 0.00039767
18 | 0.98837 | -0.081429 | 0 | 0
19 | 1 | 0 | -0.18238 | -0.045681
20 | 0.99654 | -0.024201 | 0.002486 | 0.00062304
21 | 0.9917 | -0.05821 | 0.0010831 | 0.00027146
22 | 0.98749 | -0.087686 | 0.0017562 | 0.00044014
23 | 0.98756 | -0.087148 | 0.004323 | 0.0010834
24 | 0.98745 | -0.08797 | 0.026529 | 0.0066489
25 | 0.99607 | -0.027474 | 0.0014252 | 0.00035718
26 | 0.98785 | -0.085106 | 0.030001 | 0.007519
27 | 0.99752 | -0.01735 | 0.023902 | 0.0059904
28 | 0.99151 | -0.059576 | 0.003009 | 0.00075413
29 | 0.99144 | -0.060054 | 0.0066877 | 0.0016761
30 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042401 | -0.0010627 | 0.0042408 | 0.0010626 | 6.7903e-07 | -8.8262e-08 | 0.0063508 | 0.0063506 | 0.0063508 | 0.99347 | -0.045701 | 0.99364 | -0.044544 | 2.3521
1 | -0.017399 | -0.0043604 | 0.017407 | 0.0043632 | 8.0972e-06 | 2.8666e-06 | 0.026056 | 0.026056 | 0.026056 | 0.99364 | -0.044544 | 0.99412 | -0.041183 | 9.6503
2 | -0.017407 | -0.0043632 | 0.017414 | 0.0043656 | 6.7195e-06 | 2.3787e-06 | 0.026056 | 0.026056 | 0.026056 | 0.99412 | -0.041183 | 0.99451 | -0.038397 | 9.6503
3 | 0.020575 | 0.0051602 | -0.020567 | -0.0051572 | 8.0459e-06 | 2.9181e-06 | 0.030783 | 0.030783 | 0.030783 | 0.99461 | -0.037772 | 0.9942 | -0.040594 | 11.4013
4 | -0.020575 | -0.0051602 | 0.020584 | 0.0051634 | 8.9028e-06 | 3.2287e-06 | 0.030783 | 0.030783 | 0.030783 | 0.99461 | -0.037772 | 0.99505 | -0.034652 | 11.4012
5 | 0.013433 | 0.0033694 | -0.013419 | -0.0033644 | 1.4818e-05 | 4.9384e-06 | 0.020107 | 0.020107 | 0.020107 | 0.9942 | -0.040594 | 0.99307 | -0.048557 | 7.447
6 | -0.020584 | -0.0051634 | 0.020603 | 0.0051702 | 1.8764e-05 | 6.8045e-06 | 0.030783 | 0.030783 | 0.030783 | 0.99505 | -0.034652 | 0.99599 | -0.028085 | 11.4012
7 | -0.040657 | -0.010191 | 0.040722 | 0.010216 | 6.5147e-05 | 2.469e-05 | 0.060833 | 0.060832 | 0.060833 | 0.99451 | -0.038397 | 0.99616 | -0.026844 | 22.5306
8 | 0.013419 | 0.0033644 | -0.013403 | -0.0033593 | 1.55e-05 | 5.1675e-06 | 0.020107 | 0.020107 | 0.020107 | 0.99307 | -0.048557 | 0.99189 | -0.056902 | 7.4471
9 | -0.024284 | -0.0060928 | 0.024297 | 0.0060976 | 1.3092e-05 | 4.8279e-06 | 0.036283 | 0.036283 | 0.036283 | 0.99599 | -0.028085 | 0.99654 | -0.024201 | 13.4381
10 | 0.010784 | 0.0027029 | -0.010782 | -0.0027023 | 1.9531e-06 | 5.9688e-07 | 0.016178 | 0.016178 | 0.016178 | 0.99189 | -0.056902 | 0.9917 | -0.05821 | 5.9919
11 | 0.015551 | 0.0038998 | -0.015524 | -0.0038907 | 2.6266e-05 | 9.0916e-06 | 0.023247 | 0.023247 | 0.023247 | 0.99543 | -0.031927 | 0.9937 | -0.044131 | 8.61
12 | -0.019082 | -0.0047846 | 0.019089 | 0.0047873 | 7.6423e-06 | 2.7436e-06 | 0.028525 | 0.028525 | 0.028525 | 0.99543 | -0.031927 | 0.99584 | -0.029038 | 10.5649
13 | 0.0035313 | 0.00088475 | -0.0035308 | -0.00088491 | 4.5088e-07 | -1.6364e-07 | 0.0052786 | 0.0052787 | 0.0052787 | 0.99543 | -0.031927 | 0.9953 | -0.03285 | 1.9551
14 | -0.023389 | -0.005865 | 0.023408 | 0.005872 | 1.9142e-05 | 7.0353e-06 | 0.03495 | 0.03495 | 0.03495 | 0.99584 | -0.029038 | 0.99668 | -0.023137 | 12.9445
15 | 0.043757 | 0.010979 | -0.043734 | -0.01097 | 2.249e-05 | 8.54e-06 | 0.065332 | 0.065332 | 0.065332 | 0.99668 | -0.023137 | 0.99616 | -0.026844 | 24.1969
16 | -0.067165 | -0.016851 | 0.067274 | 0.016892 | 0.00010854 | 4.1519e-05 | 0.10028 | 0.10028 | 0.10028 | 0.99668 | -0.023137 | 0.99834 | -0.011508 | 37.1413
17 | 0.0030121 | 0.00075451 | -0.003012 | -0.00075459 | 1.3258e-07 | -8.5639e-08 | 0.0044992 | 0.0044993 | 0.0044993 | 0.99616 | -0.026844 | 0.99611 | -0.027162 | 1.6664
18 | 0.063267 | 0.015942 | -0.062654 | -0.015707 | 0.0006129 | 0.0002343 | 0.094328 | 0.094329 | 0.094329 | 0.99834 | -0.011508 | 0.98837 | -0.081429 | 34.9366
19 | -0.13054 | -0.032834 | 0.13075 | 0.032914 | 0.0002098 | 8.0228e-05 | 0.19461 | 0.19461 | 0.19461 | 0.99834 | -0.011508 | 1 | 0 | 36.0389
20 | 0.0014252 | 0.00035692 | -0.0014252 | -0.00035718 | 6.1449e-08 | -2.5916e-07 | 0.002129 | 0.0021291 | 0.0021291 | 0.99611 | -0.027162 | 0.99607 | -0.027474 | 0.78854
21 | 0.036101 | 0.0090494 | -0.036082 | -0.0090425 | 1.8378e-05 | 6.9406e-06 | 0.054351 | 0.054351 | 0.054351 | 0.98837 | -0.081429 | 0.98785 | -0.085106 | 20.13
22 | 0.026553 | 0.0066578 | -0.026529 | -0.0066489 | 2.4045e-05 | 8.9393e-06 | 0.039978 | 0.039978 | 0.039978 | 0.98837 | -0.081429 | 0.98745 | -0.08797 | 14.8067
23 | 0.050833 | 0.012767 | -0.05071 | -0.012721 | 0.00012232 | 4.6598e-05 | 0.07565 | 0.07565 | 0.07565 | 1 | 0 | 0.99752 | -0.01735 | 28.0184
24 | -0.026783 | -0.0067206 | 0.026808 | 0.0067301 | 2.5485e-05 | 9.4691e-06 | 0.039995 | 0.039995 | 0.039995 | 0.99654 | -0.024201 | 0.99752 | -0.01735 | 14.8129
25 | 0.009699 | 0.0024308 | -0.0096971 | -0.0024303 | 1.8338e-06 | 5.2632e-07 | 0.014553 | 0.014553 | 0.014553 | 0.9917 | -0.05821 | 0.99151 | -0.059576 | 5.39
26 | -0.0017562 | -0.00044014 | 0.0017563 | 0.00043981 | 1.3077e-07 | -3.3258e-07 | 0.0026463 | 0.0026462 | 0.0026463 | 0.98749 | -0.087686 | 0.98756 | -0.087148 | 0.98012
27 | -0.0060793 | -0.0015232 | 0.006081 | 0.0015235 | 1.7176e-06 | 2.4073e-07 | 0.0091599 | 0.0091597 | 0.0091599 | 0.98756 | -0.087148 | 0.98785 | -0.085106 | 3.3925
28 | 0.0066881 | 0.0016762 | -0.0066877 | -0.0016761 | 4.4257e-07 | 7.9428e-08 | 0.010037 | 0.010037 | 0.010037 | 0.99151 | -0.059576 | 0.99144 | -0.060054 | 3.7175

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22212 | 0.055641

## res_load
| p_mw | q_mvar
0 | 0.0042401 | 0.0010627
1 | 0.013158 | 0.0032978
2 | 0.0071336 | 0.0017878
3 | 0.023243 | 0.0058252
4 | 0.0036812 | 0.0009226
5 | 0.0026191 | 0.0006564
6 | 0.015524 | 0.0038907
7 | 0.0042999 | 0.0010776
8 | 0.0035308 | 0.00088491
9 | 0.0015867 | 0.00039767
10 | 0.039739 | 0.0099596
11 | 0.002486 | 0.00062304
12 | 0.0010831 | 0.00027146
13 | 0.0017562 | 0.00044014
14 | 0.004323 | 0.0010834
15 | 0.026529 | 0.0066489
16 | 0.0014252 | 0.00035718
17 | 0.030001 | 0.007519
18 | 0.023902 | 0.0059904
19 | 0.003009 | 0.00075413
20 | 0.0066877 | 0.0016761

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1